## Power Operations Bulletin # 505

ERCOT has posted/revised the NODAL Real Time Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.4	Alarm Processing and Acknowledgment

Procedure Purpose: To monitor and acknowledge system alarms.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-1 R6, R8 | IRO-003-2 R2 | IRO-005-2 R1.1, R1.2 | TOP-002-2 R8 |
|  | TOP-006-1 R2, R5 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: |
| Categories | Tab 1: 345 KV Transmission Equipment Status Tab 2: 138 KV Transmission Equipment Status Tab 3: Generator Breaker, AVR, CAPS, REACTOR and SPS Status Tab 4: RLC alerts Tab 5: Transmission Line Overloads - Voltage Violations - Critical Alarms Tab 6: QKNET alarms Tab 7: ICCP status Tab 8: All other alarms |
| 1 | Monitor the Alarm Summary Display pages 3, 6 and 7 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as System conditions warrant. |
| 3 | Coordinate with the Transmission Operator to clear the alarms approximately every 2 to 3 hours or as needed. |

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.3.2(2) | 6.5.7.6.2.2 | 6.5.9.1(1)(b) | 8.2 (2)(b)(vii) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6, R7, R8 | BAL-005-0.b R8 | BAL-007 (Field Trial) | EOP-002-2.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 600 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -600 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, - Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) |
| Base Point Deviation | IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations > +/- 0.10 Hz | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz; THEN: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) - If unit trip, name of unit that tripped - Approximate MW on the unit when trip occurred - Actual Frequency and amount of RRS deployed - Approximate ERCOT load. |
| ### Response to High Frequency |  |
| BAAL Sheet | Open realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| Monitor | IF: - Frequency is above 60.05 Hz and continuing to climb or exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - CHECK if “Generation To Be Dispatched” (GTBD) is adequate to serve the predicted load, - Manually run SCED. |
| 10 MINUTES | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points (GEN-LDL), - Enter operator manual offset into “DSI Generation Requirement Manual Adjustment” to lower generation (the operator manual offset will continue to be deployed until removed), - Manually run SCED. |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points (GEN-LDL), - Re-adjust “DSI Generation Requirement Manual Adjustment” if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED, - Log the event and notify Shift Engineer to send an event notification to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| Stable | IF: - An operator manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Open realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.90 Hz - Load Resource providing RRS – 59.7 Hz |
| Monitor/ Deploy | IF: - Frequency is below 59.95 Hz and continuing to drop or is below 59.95 > 5 minutes, AND - Regulation Up service remains and is deploying; THEN: - CHECK if “Generation To Be Dispatched” (GTBD) is adequate to serve the predicted load, - Manually run SCED. IF: - Out of Up Regulation; THEN: - Select the Activate Manual Responsive Reserve, - Enter the Manual RRS Desired MW level, - Select Commit. |
| 10 Minutes | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter operator manual offset into “DSI Generation Requirement Manual Adjustment” to increase generation (the operator manual offset will continue to be deployed until removed), - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Notify the Shift Supervisor of the need to possibly commit additional Resources: - Resource Operator will issue a VDI for intra-hour - Notify RUC Operator for the next HRUC run. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust “DSI Generation Requirement Manual Adjustment” if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED, - Log the event and notify Shift Engineer to send notification of the event to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust DSI Generation Requirement Manual Adjustment if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points, - Re-adjusted “DSI Generation Requirement Manual Adjustment” if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED. |
| Stable | IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An operator manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Austin) |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source - Contact the Help Desk, - Notify the other Control Room Operators that SCED results could be skewed due to incorrect Frequency telemetry. |

## 3.2	Automatic Generation Control (AGC) Failure

Procedure Purpose:  To ensure that frequency is maintained in the event of an AGC failure.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Failure Indication/ Issues | IF: - The EMS frequency control is not functioning as indicated by: - AGC is SUSPENDED or PAUSED OR - “Last AGC Cycle” time on Generation Area Status display is not updating OR - AGC operation adversely impacts the reliability of the Interconnection, OR - SCED and EMS are not functioning, AND - The problem cannot be resolved quickly; THEN: - Verify the status of RLC - If RLC is also failed, proceed using the AGC and RLC Failure procedure. - If RLC is still functioning properly, continue - Determine which QSE has ample Capacity to place on Constant Frequency Control. (REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data), - Direct that QSE to go on “Constant Frequency”, by issuing an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into ‘Monitor” mode, - Using the Hotline, notify all QSEs that ERCOT is having AGC issues and has placed a QSE on constant frequency, Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to AGC issues and has placed a QSE on Constant Frequency. All remaining Resources should continue to follow their SCED Base Points. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” - Notify the Transmission Operator to make the same Hotline call to the TOs, - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| QSE Control Issues | IF: - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Coordinate with another QSE that has ample Capacity and place them on Constant Frequency Control. (Remember to take the first QSE off Constant Frequency). |
| QSE Capacity Issues | IF: - The QSE on Constant Frequency notifies ERCOT of Capacity issue; THEN: - Determine available Capacity for SCED and enter an operator manual offset OR - Issue electronic VDI(s) as needed, to Commit/Decommit additional generation to maintain Grid Reliability. - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level |
| AGC Issues Resolved | WHEN: - ERCOT AGC Control is functioning properly; THEN: - Direct QSE to come off “Constant Frequency” by ending the electronic VDI, - Place ERCOT AGC back into “ON” mode - Using the Hotline, notify all QSEs that ERCOT has resolved the computer issues and is back to normal operation, Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Emergency Notice due to AGC issues and has returned to normal operations. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” - Notify the Transmission Operator to make the same Hotline call to the TOs, - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| Log | Log all actions taken. |

## 3.4	AGC and RLC Failure

Procedure Purpose:  To ensure that Frequency is maintained in the event that AGC and RLC fail simultaneously.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: Decmeber 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Failure Indications | AGC: - AGC is SUSPENDED or PAUSED - “Last AGC CYCLE” time on the Generation Area Status page is not updating - AGC Operation adversely impacts the Reliability of the Interconnection - SCED and EMS are not functioning - Problem cannot be resolved quickly RLC: - Process Status: RLC Down will be displayed in RED in the upper right hand corner of the RLC display - RLC (PI Alarm) will be flashing RED. |
| AGC/RLC Issues | IF: - AGC and RLC fail simultaneously; THEN: - Determine which QSE has ample Capacity to place on Constant Frequency Control (REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data), - Direct the selected QSE to go on “Constant Frequency” by issuing an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into “Monitor” mode, - Using the Hotline, notify all QSEs that ERCOT is having AGC and RLC issues and has placed a QSE on Constant Frequency, Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to an issue with AGC and SCED. ERCOT has placed a QSE on Constant Frequency. Please hold your current output until instructed by ERCOT. ERCOT will be issuing unit specific deployments to individual QSEs as needed to maintain Frequency. [QSE] please repeat this back to me. That is correct, thank you.” - Notify the Transmission Operator to issue their Hotline notification - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| QSE Control Issues | IF: - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Determine which QSE has the most available Capacity, - Issue a unit specific instructions to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |
| System Wide Capacity Issue | IF: - There is no longer any available Capacity to issue fleet deployments; THEN: - Issue electronic VDI(s) as needed, to Commit/Decommit additional Generation to maintain Grid Reliability - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level - . |
| AGC/RLC Issues Resolved | WHEN: - AGC and RLC is restored; THEN: - Direct QSE to come off ‘constant frequency’ by ending electronic VDI, - Place ERCOT AGC back into “ON” mode - Cancel VDI(s) for additional generation, if issued - Remove the Emergency Base Point flag - Cancel the Emergency Notice. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is cancelling the Emergency Notice. All QSE’s please follow SCED Base Points. [QSE] please repeat this back to me. That is correct, thank you.” - Notify Transmission Operator to issue their Hotline notification - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| Log | Log all actions taken. |

## 3.5	Potential DCS Event

Procedure Purpose:  To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.4.2(2)(a)(ii) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6.2 | EOP-001-0 R5 | EOP-002-2.1 R5, 6.1 |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC Recovery Criteria | Restore System Frequency to the following limit within 15 minutes: - Scheduled Frequency if it was greater than or equal to scheduled Frequency prior to the disturbance, OR - Its pre-disturbance value if it was less than scheduled frequency prior to the disturbance. ERCOT ISO shall fully restore the minimum Contingency Reserve requirement of the ERCOT Region’s Largest Single Contingency (1354 MW) as soon as practical. Within 90 minutes, ERCOT ISO will restore Responsive Reserves to 2300 MW or greater. This 90 minute Restoration period begins at the end of the Disturbance Recovery period. |
| NOTE | When an automatic request for RRS from Generation Resources is sent to the QSE’s for Frequency at or below 59.91 Hz, the QSE’s have 60 seconds to update their RRS schedule to provide the additional capacity for SCED to dispatch. If the schedules are not updated by the time SCED executes, it may be necessary to execute a manual SCED run. It may be necessary to manually run SCED several times. |
| NOTE | The steps below will need to happen quickly, let phones ring, or if available, another desk will take the calls. |
| 1 | IF: - ERCOT experiences a Low Frequency Disturbance due to: - A loss of Generation, equal to or greater than 1083 MW (consisting of a single generator or the total of multiple generators within 1 minute), OR - There is NO indication of a Generation loss and the magnitude of the event is determined to be greater than 1000 MW; DETERMIME: - Magnitude of the event by using the “Raw ACE” tag, Analyze the change in this tag after a minimum of 30 seconds to avoid the initial overshoot. Example: If the “Raw ACE” pre-disturbance value is +150 MW, and post disturbance ( 30 seconds) value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. THEN: - It can be assumed that a potential NERC Reportable DCS Event has occurred, - Immediately check to ensure that SCED sees that the unit(s) correct telemetry (HSL of zero or Resource Status of “off”), Contact the QSE(s) if telemetry needs to be changed. - If SCED does not automatically execute within 60 seconds of the event, manually execute a SCED run. - Proceed to step 3 if necessary. |
| 2 | IF: - Unit telemetry is incorrect, AND/OR, - Frequency did not drop below 59.7 Hz; THEN: - Enter an operator manual offset for amount of MW needed or if SCED Up room for next 5 minutes is less than needed, enter that value (the operator manual offset will continue to be deployed until removed). |
| 3 | Until we get defect of sending 0 at the top of each hour when obligations go away and NPRR of having to make a hotline call at the top of each hour, deploy both group 1 and 2 together. IF: - (HASL-GEN) is less than 1150 MW; THEN: - Instruct the Resource Operator to deploy both Group 1 and 2 (work-around) of un-deployed Load Resources. |
| 4 | WHEN: - Notified by the Resource Operator that both Group 1 and 2 Load Resources have been deployed, THEN: - Notify QSEs, utilizing the Hotline, that ERCOT is issuing an Emergency Notice and to follow their XML instruction to deploy Load Resources. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice and has deployed both Group 1 and 2 Load Resources. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | If Load Resources are deployed it may become necessary to periodically execute SCED manually to control Frequency. |
| 5 | If Load Resources are deployed, instruct the Transmission Operator to notify the TOs. |
| 6 | Skip this step for now, as a workaround the auto deployment at the hour boundary will be disabled until sometime after post-go-live. Obligations change from hour to hour, IF: - Notified by the Resource Operator that additional Load Resources were deployed at the top of the hour, THEN: - Make another Hotline call Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT has issued an electronic directive to all QSEs to deploy both Group 1 and 2 Load Resources supplying Responsive Reserve. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 7 | WHEN: - System frequency has been restored; THEN: - Instruct the Resource Operator to send an XML message to recall Load Resources, - Ensure the SCED operator manual offset has been removed (if one was used), - Make Hotline call to QSEs to end Emergency Notice and recall Load Resources. |
| 8 | WHEN: - Notified by the Resource Operator that both Group 1 and 2 Load Resources have been recalled; THEN: - Notify QSEs, utilizing the Hotline, that ERCOT is cancelling the Emergency Notice and to follow their XML instruction to restore Load Resources. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is ending the Emergency Notice and has recalled all Load Resources. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| PRC Below 2300 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Implement EEA (see specific procedure). |
| Log | Make log entry. |

## 3.6	Monitor Capacity Reserves and Respond to Capacity Issues

Procedure Purpose:  To ensure the required amount of Operating Reserves are available to meet the Load Forecast.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4 | IRO-005-2 R1.4, R1.5, R4 |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Day-Ahead process, the Adjustment Period process, and the Real-Time process must be utilized before ordering Resources to specific output levels with Emergency Base Point instructions. |
| NOTE | If intra-hour capacity is needed, coordinate with the Resource Operator to deploy Non-Spin. |
| Capacity Shortage | MONITOR: - The Generation Area Status Page. IF: - (HDL-GEN) ≤ 200 MW during normal ramps, OR - (HDL-GEN) ≤ 500 MW during high load ramp/peak load hours; THEN: - Coordinate with the Resource Operator to deploy Non-Spin, - Notify the RUC Operator of the possibility of needing to commit additional Resources for the next hour. |
| Capacity Surplus | MONITOR: - The Generation Area Status Page IF: - (GEN-LDL) ≤ 200 MW; THEN: - Consult with RUC Operator to ensure HRUC is seeing the situation and is decommitting Resources, - If needed, issue VDI(s) to Resource(s) to help alleviate the surplus - Choose “DECOMMIT” as the Instruction Type from Resource level - . |
| Log | Log all actions taken as necessary. |

## 4.2	Managing SCED Failures

Procedure Purpose:  To make sure Generation is dispatched to match system load in the event that the SCED system application has failed or SCED results are unable to maintain Adequate Regulation or System Frequency.

| Protocol Reference | 6.5.9(1) | 6.5.9.2 | 6.5.9.1(2) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| System Failure |  |
| NOTE | If EMS is also not functioning, see “Loss of Frequency Control Procedure”. |
| 1 | IF: - Any module of the SCED Workflow Controller fails; THEN: - Make an attempt to manually run the SCED process. |
| 2 | IF: - SCED still fails after attempting a manual run; THEN: - Contact the Help Desk, - Determine if West – North (IROL) constraint is active, if so use script in step 3, - Initiate the Emergency Notice Hotline call, AND - Instruct the Resource Desk Operator to post a message on MIS Secure utilizing Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice due to the failure of SCED. ERCOT will be issuing Emergency Base Points as needed until this issue has been resolved. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Script to use if West – North IROL constraint was active when SCED failed: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice due to the failure of SCED. ERCOT is requesting all QSEs with curtailed WGRs to set their HSL=to their current output. ERCOT will be issuing Emergency Base Points as needed until this issue has been resolved. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | Once the Emergency Notice has been issued, issue Emergency Base Points as needed to maintain regulation and frequency. (see Section 5.8 in the Desktop Guide) |
| 5 | IF: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, AND - Communicate the restoration to Control Room staff, - Initiate Hotline call to cancel the Emergency Notice, - Instruct the Resource Operator to cancel the message on MIS Secure utilizing Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. SCED is now functional and ERCOT is canceling the Emergency Notice. Please follow your base points. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log all actions taken and any issues with the Market Participants. |
| Failure to Maintain Regulation |  |
| CAUTION | - When using the “DSI Generation Requirement Manual Adjustment”, the operator manual offset will continue to be deployed until removed after SCED completes its sequence. - Before entering an operator manual offset, be sure there is enough capacity for SCED (HDL-GEN). |
| 1 | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes> DSI Generation Requirement Manual Adjustment IF: - It has been determined to use the “DSI Generation Requirement Manual Adjustment”, (the operator manual offset will continue to be deployed until removed); THEN: - Calculate the operator manual offset MW amount that would be required to recall the Regulation Service, AND - Make adjustments as necessary until the problem is corrected. - Notify the Shift Supervisor and Shift Engineer. |
| 2 | IF: - SCED is solving with a valid solution; THEN: - Change the operator manual offset MW to zero, AND - Communicate the restoration to the appropriate Control Room staff |
| Log | Log all actions taken and any issues with the Market Participants. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| ### Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA. When a media appeal for voluntary energy conservation is enacted, TOs should be notified via Hotline call (see 2b for typical script). - Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore Reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Select the activate EEA flag in EMS, - Using the Hotline, notify all QSEs to implement EEA 1. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is implementing EEA 1, QSEs are to do the following: - Report when online available capacity is at risk due to adverse circumstance, - Immediately and continually update COPs to reflect all resource delays and limitations should they occur, - Notify ERCOT of all available uncommitted units within the expected time frame of the emergency, - QSE’s are not to take units off-line while ERCOT is in emergency operations unless it is due to a forced outage, - Suspend any Resource testing, - ERCOT is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2A |  |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Typical Script: “This is ERCOT Operator [first and last name]; this is a courtesy call to inform you that ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. |
| 1 | Until we get defect of sending 0 at the top of each hour when obligations go away and NPRR of having to make a hotline call at the top of each hour, deploy both group 1 and 2 together. IF: - Physical Responsive Capability falls below 1750 MW; THEN: - Once the Resource Desk has completed the deployment of the Load Resources (deployments must be made before the Hotline call) providing RRS as follows: - Less than 1750 MW, deploy Group 1. - As system conditions require, deploy remaining load resources. - Less than 1400 MW deploy both Groups 1 and 2 simultaneously. - Using the Hotline, notify all QSEs to implement EEA 2A and any measures associated with EEA 1, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], ERCOT is implementing EEA 2A and has deployed both Group 1 and 2 Load Resources. Also: - Implement all measures associated with EEA 1, if not already implemented. - Do not take units off-line while ERCOT is in Emergency Operations unless it is due to a forced outage. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2B |  |
| 1 | Deploy all EILS as a single block. IF: - No EILS exists; THEN: Skip EEA 2B and proceed to EEA 3 if needed. |
| 2 | IF: - Unable to maintain system frequency at 60.00Hz AND Load Resources providing RRS have been deployed and EILS have been procured; THEN: - Using the Hotline, notify all QSEs to implement EEA 2B and any measures associated with EEA 1 and 2A, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], ERCOT is implementing EEA 2B. ERCOT is issuing Verbal Dispatch Instruction to deploy contracted EILS Resources in the current time period until further notice. Implement all measures associated with EEA 1 and 2A, if not already implemented. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain System Frequency at 59.80 Hz; THEN: - Using the Hotline, notify all QSEs to implement EEA 3 and any measures associated with EEA 1, 2A, and 2B, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], ERCOT is implementing EEA 3, [MW Amount] of firm load is being shed. Implement all measures associated with EEA 1, 2A, and 2B if not already implemented. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |