## Power Operations Bulletin # 507

ERCOT has posted/revised the NODAL Resource Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Compliance Monitoring

Procedure Purpose: To monitor QSE performance

| Protocol Reference | 3.9.1(7) & (8) | 6.3.2(2) | 6.4.2.5 (2) | 6.4.2.5(3)(b) |
| --- | --- | --- | --- | --- |
|  | 6.4.8.1(1) | 6.5.7.5(2) | 6.5.9(3) | 8.1.1.3(3) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### Monitor Resource Status for Discrepancies |  |  |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instructions under normal conditions and Emergency Conditions. During Emergency Conditions, ERCOT may verbally request QSEs to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |  |
| Monitor COP | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>COP Monitor Periodically: - Review the COP changes utilizing the Date/Time of Submission column as a reference; IF: - A QSE has changed a resource status code, resource parameter, or ancillary service on a specific resource; THEN: - Review the change in the COP Monitor, AND - Notify the QSE representing the resource if the change is unacceptable to ERCOT. |  |
| Telemetered Status | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>Consistency Checks IF: - Discrepancy is identified between a COP and telemetered Resource Status; THEN: - Call the QSE representing Resource to determine the correct resource status and have them make the necessary correction. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Area Status>Nodal Operational Status>Resource Limit Data>Unit Tab WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) |  |
| ON TEST | - If the ONTEST Resource Status Code is used to indicate that a Generation Resource is performing a test, the QSE should notify ERCOT by 1800 in the Day-Ahead, - Review the list of approved Resources to be ONTEST, - ONTEST can be used by the QSE when in the start-up and shut-down mode. |  |
| Control Block Up/Down | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details>Unit tab - Control Block Current UP/DN are telemetry points that a QSE can use in emergency situations to communicate that a resources ability to adjust its output has been unexpectedly impaired. - If a QSE has a Control Block set for greater than 5 minutes, the system will set the corresponding (UP/DN) Too Long flag to indicate this to the operator. |  |
| ### Monitor Base Point Deviations |  |  |
| Monitor | REVIEW REFERENCE DISPLAY: EMS Applications>Related Displays>Expected Generation and Load Details>Top Ten Periodically: - Review the Top Ten generation deviations (remember to click the “Update Date” to refresh screen, - Call QSE and instruct them to follow their base point when reason if unknown. |  |
| ### Manual Override Checks |  |  |
| 1 | Market Participation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL and LDL Periodically: - Review the Manual HDL and LDL overrides to ensure they are still needed. IF: - Override exists; THEN: - Coordinate with the Transmission Operator to determine if override is still needed. |  |
| ### Dynamically Scheduled Resource |  |  |
| NOTE | Each QSE may not have more than one DSR Load. |  |
| DSR | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Analyst Displays>Gen Monitoring Displays>Dynamic Schedules>Load Based IF: - A DSR load signal fails for any reason for > than one 15 minute Settlement Interval; THEN: - Notify the QSE and notify the Helpdesk to suspend validation of DSR Output Schedule. IF: - A DSR load signal fails for more than 10 consecutive hours; THEN: - Notify the Helpdesk to have DSR suspended until the signal is reliably restored. |  |
| NOTE | IF: - The signal failure is identified to be an ERCOT communication problem; THEN: - ERCOT will not suspend the QSE’s ability to use DSR. |  |
| ### Monitor QSE Ancillary Services Obligation |  |  |
| Monitor |  | Monitor the Regulation A/S details, RRS details and Non-Spin details displays. |
| NOTE |  | If any A/S insufficiencies are identified in the HRUC solution, refer to the “Replacement of Ancillary Service Due to Undeliverable/Failure to Provide” section of the “Supplemental Ancillary Services Market” procedure. |
| Real-Time A/S Shortage |  | A workaround for the auto notification is below, the automated notification may occur sometime after post-go-live. QSEs receive automatic notifications via the MIS Certified Area when the sum of each of the QSEs Resources’ telemetered A/S Resource Responsibility with the QSEs total A/S Responsibility Do Not match. WHEN: - QSEs receive this notification; THEN: - The QSE shall notify ERCOT immediately of the expected duration of the QSEs inability to meet its obligation, AND - Within ten minutes, the QSE must: - Correct the telemetered A/S Resource Responsibility to provide sufficient capacity, OR - Provide both appropriate justification for not satisfying their A/S Obligation AND a plan to correct the shortfall that is acceptable. IF: - The QSE is unable to replace their A/S Obligation; THEN: - Notify the Shift Supervisor and determine if A/S shortage amount is sufficient enough for ERCOT to replace from existing offers. |
| Real-Time A/S Shortage |  | WHEN: - A QSE shows a Real-Time A/S shortage; NOTIFY: - The effected QSE of their QSEs Resources’ telemetered value and their A/S Resource Responsibility; THEN: - Within ten minutes, the QSE must: - Correct the telemetered A/S Resource Responsibility to provide sufficient capacity, OR - Provide both appropriate justification for not satisfying their A/S Obligation AND a plan to correct the shortfall that is acceptable. IF: - The QSE is unable to replace their A/S Obligation; THEN: - Notify the Shift Supervisor and determine if A/S shortage amount is sufficient enough for ERCOT to replace from existing offers. |
| A/S Difference in COP |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Participation>Physical Market>SASM Market>Failure To Provide IF: - A/S Difference (MW) column displays negative values in RED; THEN: - Verify that the Notification Flag column displays a “Y” (should automatically default). If necessary, change the “N” to “Y” and commit to database, - Press the “Send Notification” button and acknowledge the pop-up box indicating the notifications were sent, - Navigate to the Failure To Provide display and call the Market Participants that are displayed with a Failure MW, IF: - The QSE states that they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened. IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Failure To Provide section 6.7.2 of the Desktop Guide. |
| Infeasible A/S Capacity from RUC |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market> AS Replacement IF: - The Infeasible MW column is displaying MW values; THEN: - Change the Notification Flag to “Y” and commit to database, - Press the “Send Notification” button and acknowledge the pop-up box indicating the notifications were sent, - Navigate to the AS Replacement display and call the Market Participants that are displayed with an Infeasible MW. IF: - The QSE states that they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened; IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Undeliverable section 6.7.1 of the Desktop Guide. |
| NOTE |  | A QSE that has one or more of its Resources RUC-committed to provide Ancillary Services must increase its Ancillary Service Supply Responsibility by the total amount of RUC-committed Ancillary Service quantities. The QSE may only use a RUC-committed Resource to meet its Ancillary Service Supply Responsibility during that Resource’s RUC-Committed Interval if the Resource has been committed by the RUC process to provide Ancillary Service. The QSE shall indicate the exact amount and type of Ancillary Service for which it was committed as the Resource’s Ancillary Service Resource Responsibility and Ancillary Services Schedule for the RUC-Committed Intervals for both telemetry and COP information provided to ERCOT. Upon deployment of the Ancillary Services, the QSE shall adjust its Ancillary Services Schedule to reflect the amounts requested in the deployment. |

## 3.4	Responding to Capacity Shortages

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Capacity Shortages as requested by the Real-Time Operator.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If Non-Spin is being deployed at any time other than the top of the hour (less than 12 consecutive 5-minute intervals), deselect any Resources whose COP Non-Spin Resource Responsibility is “ZERO” for subsequent hours. (Refer to Desktop Guide section 6.2 “Non-Spin Deployment and Recall”) |
| Deployment | WHEN: - Notified by the Real-Time Operator to deploy Non-Spin for capacity shortages; THEN: - Coordinate with the Transmission Operator to verify the Non-Spin doesn’t create congestion, - Deploy Non-Spin, - Notify the RUC Operator of the deployment |
| Termination | WHEN: - Notified by the Real-Time Operator that the Non-Spin Reserve Service is no longer needed, AND - The resources have run for a minimum of 1 hour (12 consecutive 5-minute intervals); THEN: - Recall the Non-Spin, AND - Notify the RUC Operator of the Non-Spin termination. |

## 3.5	Potential DCS Event

Procedure Purpose:  To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.4.2(2)(a)(ii) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6.2 | EOP-001-0 R5 | EOP-002-2.1 R5, 6.1 |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC Recovery Criteria | Restore system frequency to the following limit within 15 minutes: - Scheduled frequency if it was greater than or equal to scheduled frequency prior to the disturbance, OR - Its pre-disturbance value if it was less than scheduled frequency prior to the disturbance. ERCOT ISO shall fully restore the minimum Contingency Reserve requirement of the ERCOT Region’s largest single contingency (1354 MW) as soon as practical. Within 90 minutes, ERCOT ISO will restore Responsive Reserves to 2300 MW or greater. This 90 minute restoration period begins at the end of the disturbance recovery period. |
| 1 | Until we get defect of sending 0 at the top of each hour when obligations go away and NPRR of having to make a hotline call at the top of each hour, deploy both group 1 and 2 together. WHEN: - Instructed by the Real-Time operator to deploy Load Resources for a DCS event; THEN: - Deploy both Group 1 and 2 (work-around) un-deployed Load Resources (see Desktop Guide section 6.1, if needed) (this deployment will send the QSEs an XML message). This must be done before the Hotline call, - Notify the Real-Time operator that XML deployments have been sent. |
| 2 | Skip this step for now, as a workaround the auto deployment at the hour boundary will be disabled until sometime after post-go-live. Obligations change from hour to hour, IF: - Crossing the top of an hour; THEN: - Confirm deployments for next hour by clicking “Approve” (if not done by 5 after the XML message will go out 5 minutes after the top), - Instruct the Real-Time operator to make another hotline call. |
| 3 | WHEN: - Notified by the Real-Time operator to recall Load Resources; THEN: - Send XML message to recall Load Resources, - Instruct the Real-Time operator to make a Hotline call to QSEs to end Emergency Notice and recall Load Resources. |
| PRC Below 2300 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Refer to the “Implement EEA” procedure. |
| Log | Enter log entry. |

## 3.7	Responding to Congestion Management Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R2, R4.2 | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 |
|  | IRO-004 R3 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If Non-Spin is being deployed at any time other than the top of the hour (less than 12 consecutive 5-minute intervals), deselect any Resources whose COP Non-Spin Resource Responsibility is “ZERO” for subsequent hours. (Refer to Desktop Guide section 6.2 “Non-Spin Deployment and Recall”) |
| Deployment | WHEN: - Notified by the Transmission Operator to deploy Non-Spin for relieving congestion on the transmission system; ASK: - Location; (i.e. Weather Zone) - On line - Quick Start Generation Resource (QSGR) or Off line - Non-Spinning Reserve (Non-Spin) status (i.e. ON/OFFNS) THEN: - Deploy Non-Spin on the specified resources - Notify the RUC Operator of the deployment |
| Termination | WHEN: - Notified by the Transmission Operator that the Non-Spin is no longer needed, AND - The resources have run for a minimum of 1 hour (12 consecutive 5-minute intervals); THEN: - Recall the Non-Spin, AND - Notify the RUC Operator of the Non-Spin termination. |
| ### Responding to North-Houston Interface Issues |  |
| Issue Watch & Deploy Non-Spin | WHEN: - Notified by the Transmission Operator to deploy Non-Spin in the Houston area for the North-Houston Interface; THEN: - Deploy Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) - Using the hotline, issue a Watch, - Post on MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for the North to Houston interface. ERCOT has deployed Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| Issue Emergency Notice & Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Deploy Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by XML (Refer to Desktop Guide section 6.1 “Loads providing RRS Deployment and Recall”) - Using the hotline, issue the Emergency Notice, - Post on MIS Public using Notice Builder. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT has issued an Emergency Notice for the North to Houston interface and has issued you an electronic directive for the deployment of specific Load Resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Recall Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML (Refer to Desktop Guide section 6.1 “Loads providing RRS Deployment and Recall”) - Using the hotline, cancel the Emergency Notice, - Cancel message on MIS Public using Notice Builder. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is canceling the Emergency Notice for the North to Houston interface and has issued you an electronic directive for the recall of Load Resource deployments. ERCOT is reminding everyone that a Watch is still in effect until further notice. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Recall Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) - Using the hotline, cancel the Watch, - Post on MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is canceling the Watch for the North to Houston interface. ERCOT has recalled Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log the actions taken. |

## 4.1	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve or reject Resource decommitments in the Operating Period.

| Protocol Reference | 6.4.6 | 6.4.6.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Operating Period |  |
| NOTE | The Operating Period is the two-hour period comprised of the Operating Hour and the clock hour preceding the Operating Hour. |
| NOTE | A Resource cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. |
| NOTE | A Resource must remain committed during any RUC-Committed Interval unless the Resource has a Forced Outage. If more Resources are requesting Decommitment than can be accommodated, ERCOT shall review those requests in order of receipt. |
| 1 | IF: - A QSE requests to de-commit a Resource that has been Self-Committed; THEN: - Determine if the Resource has an Ancillary Service responsibility. If yes, inquire how this AS will be replaced, - Notify the Transmission Operator to make determination if needed for congestion management, - Notify the Shift Supervisor to ensure that requests will not have a reliability impact. NOTIFY: - The QSE of ERCOT’s decision. |
| 2 | IF: - Request is granted; THEN: - Issue an electronic VDI - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type from Resource Level |
| 3 | Log actions taken. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 6.4.8.1 | 6.4.8.1.1 | 6.4.8.1.2 | 6.4.8.1.3 |
| --- | --- | --- | --- | --- |
|  | 3.16 (4) | 6.4.8.2 | 6.4.8.2.2 | 6.5.9(4) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - Once the notice is given, no further offers are eligible for that SASM. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services will have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify with the RUC Operator that the Hotline call notifying the Market that the DAM failed, - Make the following hotline notification before opening the SASM, - Procure all Ancillary Services for the next operating day through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.4 of the Desktop Guide: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [time] ERCOT will be opening a SASM to procure all Ancillary Services for [operating day] due to the Day-Ahead Market failure. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - Date - Each hour of SASM - Procured amount of each A/S requirement |
| 4 | Send information in an email to the following distribution list: - Shift Supervisors - Price Validation Team - Shift Engineers |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline Notification and post message on MIS Public using Notice Builder, - Procure more Ancillary Services through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.3 of the Desktop Guide. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch due to the need to increase the system wide A/S requirement above what was procured in the Day-Ahead Market due to [state the reason]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - Date - Each hour of SASM - Procured amount of each A/S requirement |
| 4 | Send information in an email to the following distribution list: - Shift Supervisors - Price Validation Team - Shift Engineers |
| 5 | Once verified that all Ancillary Service has been procured, cancel the Watch: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace AS capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the Ancillary Service capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to section 6.7.1 in the Desktop Guide). |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - Date - Each hour of SASM - Procured amount of each A/S requirement |
| 4 | Send information in an email to the following distribution list: - Shift Supervisors - Price Validation Team - Shift Engineers |
| Replacement of Ancillary Services in Real Time |  |
| NOTE | When issuing a VDI to a Resource for Real Time A/S insufficiency, ensure the QSE understands the unit is being brought online to provide an A/S. Also verify the QSE’s COP is updated when the unit is online. |
| 1 | IF: - A Real Time A/S shortage exists, AND - It is determined to be a reliability issue; THEN: - Issue a VDI to commit an off-line Resource that is qualified to provide the insufficient A/S in the time frame needed (Refer to the SASM section 6.7.5 of the Desktop Guide). - Choose “COMMIT” as the Instruction Type from Resource Level - In text, state “commit for replacement of [A/S type]” |

## 5.2	SASM Failure/Timeline Deviation

Procedure Purpose:  To manage SASM software failure or timeline deviation.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Failure of the SASM Software |  |
| 1 | IF: - The SASM workflow controller fails during any stage of the run; THEN: - Press the Abort button to cancel the current run, - Press the Shut Down button, - Press the Start Up button, - Press the Run All button to restart the sequence. |
| 2 | IF: - The SASM workflow controller continues to fail; NOTIFY: - Notify the appropriate ERCOT personnel. |
| ### Timeline Deviations |  |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - SASM process from opening a SASM market to the COP update is approximately 1 hour for an A/S plan increase. For replacement due to undeliverable/insufficient A/S, the timeline is 30 minutes. |
| A/S Plan Increase Timeline | Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - SASM Workflow Controller fails or needs to be restarted and cannot meet the timelines above; THEN: - Using the Hotline, notify the Market Participants that the SASM will be delayed. - Notify the appropriate ERCOT personnel. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is making notification that SASM has not met its timeline. ERCOT will manually commit as needed. [QSE] please repeat this back to me. That is correct, thank you.” |
| NOTE | NOTIFY: - The RUC Operator to determine if Resources can me manually committed within the timeframe needed. IF: - If needed in Real-time; THEN: - Refer to the Replacement of Ancillary Services in Real Time procedure, AND; - VDI to commit an off-line Resource that is qualified to provide the insufficient A/S in the time frame needed (Refer to the SASM section 6.7.5 of the Desktop Guide). - Choose “COMMIT” as the Instruction Type from Resource level - In text, state “commit for replacement of [A/S type]” |

## 6.1	Manage Resource Forced & Maintenance Outages

Procedure Purpose:  Monitor and respond to Resource Forced and Maintenance outages.

| Protocol Reference | 3.1.1(2) (j) | 3.1.4.2 | 3.1.4.4 | 3.1.4.5(1) |
| --- | --- | --- | --- | --- |
|  | 3.1.4.5(2) | 3.1.4.6(2) | 3.1.4.8 | 3.1.6.4(4) |
|  | 3.1.6.5(1) | 3.1.6.9(1) | 3.9.1(2) |  |
| Guide Reference |  |  |  | 6.4.7 |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The QSE should: - Immediately notify ERCOT of a forced outage, - Enter the forced outage in the Outage Scheduler within two hours, - Update their COP within 1 hour - Update their telemetry. A call to the QSE may be necessary if the above are not complete within the designated time frame. |
| NOTE | ERCOT Operators can only make the following changes in the Outage Scheduler: - Remove actual start/end time if it is within 2 hours of the time the MP entered the outage, - Change status, - Add notes If a MP needs assistance or is unable to enter their outages, direct them to Outage Coordination. Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes. |
| Notification | IF: - Maintenance Level 1 Outage is received, review the outage details; THEN: - Discuss the outage request with the Transmission Operator, - If no reliability issues exist, ACCEPT the outage. |
| Reliability Issues | IF: - The Maintenance Level 1 Outage of a Resource creates a system reliability issues; THEN: - Coordinate the start of the Resource Outage to ensure system reliability as long as the outage is allowed to start within 24 hours. |
| Maintenance Level 2 and 3 outages | IF: - Maintenance Level 2 and 3 outages are received; THEN: - DO NOT check the “Accept” box - Place the outage in “Study” status, AND - Notify the Outage Coordination group by e-mail (“OPS Outage Coordination” distribution list). |
| ### Material Deratings |  |
|  | IF: - A Resource’s capability is reduced by 10 MW and is expected to last more than 48 hours; THEN: - The QSE must do the following: - Enter the derating into the Outage Scheduler as a Forced Outage, - Replace AS responsibility if applicable - Update their COP to reflect the changes, - Update the necessary telemetered parameters for the Resource. |
| ### Short-Noticed Resource Outages |  |
|  | IF: - A newly proposed Resource Outage or proposed changes to a Planned Outage is submitted three days or less from the outage start date; THEN: - Notify Outage Coordination Group. |
| ### Opportunity Outages |  |
| NOTE | Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days. The QSE must give as much notice as practicable to ERCOT. |
| 1 | WHEN: - A Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, AND IF: - Approved by ERCOT; THEN: - The Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled. IF: - Reliability issues exist; THEN: - Reject the outage to ensure system reliability, IF: - No issues identified; THEN: - Approve the Outage as received, - Notify the QSE and Outage Coordination Group. |
| ### Returning from Planned Outage Early |  |
| Verify | IF: - A Resource returns from a Planned Outage early; THEN: - Coordinate with the Transmission and RUC Operators to determine if there is an associated transmission outage or any reliability issues exist. |
| Approve | IF: - No issues identified; THEN: - Notify the QSE of approval and to update their COP and Telemetry, - Notify the Outage Coordination Group. |
| Deny | IF: - Reliability issues, OR - Transmission is not available; THEN: - Coordinate between the TO and QSE to schedule a time agreeable to both parties for all facilities to be restored to service, - Notify the QSE within two hours, - Issue a VDI to stay Off-Line - Choose “Can Not Return Early From Outage” as the Instruction Type from Resource level. |
| Log | Log all appropriate information. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| ### Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted QSE’s and TOs should be notified via Hotline call. - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Deploy all available Non-Spin (if not previously deployed), - If necessary, refer to section 3.4 “Responding to Capacity Shortages” - If RMR Resources are not loaded, over-ride LDL as necessary, - If possible, manually override LDL for specific Resources to operate at full capacity, - Issue VDI to any QSEs with Generation Resources available and off-line (that were not bid in for Non-Spin) that can perform within the timeframe of the emergency - Choose “Commit” as the Instruction Type from Resource level, - Make EEA 1 posting to MIS Public using Notice Builder. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2A |  |
| 1 | Until we get defect of sending 0 at the top of each hour when obligations go away and NPRR of having to make a hotline call at the top of each hour, deploy both group 1 and 2 together. IF: - Physical Responsive Capability falls below 1750 MW; THEN: - Deploy Load Resources providing RRS as follows: - Less than 1750 MW, deploy Group 1 or 2. - As system conditions require, deploy remaining load resources. - Less than 1400 MW deploy Groups 1 & 2 simultaneously. - Notify Real-Time Operator when complete, XML message to deploy Load Resource must be done first before hotline call is made, - Notify Transmission Operator to implement EEA Level 2A, - Make EEA 2A posting to MIS Public using Notice Builder. |
| 2 | IF: Went straight to EEA Level 2A; THEN: - Ensure tasks in EEA Level 1 are complete. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2B |  |
| 1 | IF: - Unable to maintain system frequency at 60.00Hz, AND Load Resources providing RRS have been deployed and EILS has been procured; THEN: - Make EEA 2B posting to MIS Public using Notice Builder. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Make EEA 3 posting to MIS Public using Notice Builder. |
| 2 | Verify and log that all measures have been implemented. |