## Power Operations Bulletin # 508

ERCOT has posted/revised the NODAL Shift Supervisor Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Review Load Forecast

Procedure Purpose:  Load forecast should be as accurate as possible.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The EMMS systems provide two places where Mid-term Load Forecasts can be reviewed: - The EMS Load Forecast (LF) application provides an online load forecast. - The MMS replicates the load forecast information in the daily operating plan display summaries. The EMS online Load Forecast is considered the primary source for the mid-term Load Forecast information. The MMS load forecast summaries contained in the daily operating plan contain the same information however it depends on updates from the EMS LF tool to have current data. Therefore the MMS daily operating plan load forecast summary may contain older data than the EMS LF application. The MMS LF information should only be used during the day in case the EMS LF function is temporarily un-available. |
| 1 | Navigate to the EMS online load forecast study results and history displays. REVIEW REFERENCE DISPLAY: EMS Applications>Load Forecast>Related Displays>Mid-Term Forecasts (MLTF)>Load Forecast and Select the Day - Data – All current forecasts displayed - Chart – Current graph |
| 2 | IF the EMS online load forecast application is unavailable, REPORT failure to Help Desk and go to step 5. OTHERWISE, go to step 3. |
| 3 | Review the mid-term load forecast for each hour shown. |

| 4 | IF any anomalies are detected, consult with the control room staff. |
| --- | --- |
| 5 | Navigate to the MMS daily operation plan displays. REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary - System TCG Data & System Load |

## 4.2	Unannounced Resource Testing

Procedure Purpose: This procedure provides direction and guidelines for conducting unannounced testing of resources.

| Protocol Reference | 8.1.1.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.3.1 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Unannounced Resource Testing |  |
| NOTE | - Operations Planning will provide the list of resources to be tested. - The list of units [Season] is located on P:\SYSTEM OPERATIONS drive in the Performing Unannounced Unit Testing folder. - In addition, the Shift Supervisor may request at his discretion an unannounced test of any resource, other than Hydro, Wind and Nuclear-fueled Generation Resources. - Tests may be conducted as they best fit within the activities of the ERCOT Control Room, a minimum of 4 resources per week. - The resource to be tested must be on-line before beginning the test. - To identify potential congestion it may be necessary to conduct a Security Analysis Study using a Powerflow Base Case or Real-time Snap shot of the System. - Operations Planning will complete the following items: - Current Seasonal HSL(Net MW) - 30 Min Avg Real Time Telemetry (MW) - Additional Comments - Overall Test Results |
| Caution | - DO NOT perform an unannounced Generation Resource test during a Watch or EEA event. - If an unannounced Generation Resource test is underway when a Watch or EEA event commences, the test may be cancelled. |
| VDI | When performing a test, use the Electronic VDI tool: ISSUE: - VDI to QSE - Choose “UNANNOUNCED CAPACITY TEST (NOTE IF RETEST)” as the Instruction Type from Resource level - In text, state “RETEST” if applicable |
| Testing Rules | ISSUE a VDI instructing the resource to the HSL it has reported in its Resource Plan. If conducting a re-test, make sure “Re-test” is on the VDI. The QSE has the following time to reach its HSL, depending on its output when the test begins: - At LSL – 60 minutes to reach 90% of HSL, and an additional 20 minutes to reach HSL - Between LSL and 50 % of HSL – 60 minutes to reach HSL - Above 50 % of HSL – 30 minutes to reach HSL Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing VDI at [time] to perform an Unannounced Unit Test. Increase [Resource] to the current QSE’s telemetry HSL as shown. The [Resource] will have [XXX] amount of time to reach the reported HSL. Once the [Resource] has met the time requirement or reached its HSL, HOLD [Resource] at its HSL for at least 30 minutes. [QSE] please repeat this back to me. That is correct, thank you.” The QSE will release all Ancillary Service obligations carried by the unit to be tested and change the Resource status to “ONTEST.” When the resource reaches its HSL, HOLD that resource at its HSL for at least 30 minutes. NOTIFY the QSE that the test is complete, and RELEASE the resource from its VDI. If the resource fails to reach its HSL within the time frame, CONTINUE TO HOLD the resource for at least 30 minutes, and LOG this in the ERCOT logs. NOTIFY the QSE that the test is complete, and RELEASE the resource from its VDI. Typical script: “This is ERCOT operator [first and last name]. ERCOT is releasing VDI at [time]. The Unannounced Unit Test is complete for [Resource]. Submit the results from the test within 24 hours. [QSE] please repeat this back to me. That is correct, thank you.” COMPLETE the ERCOT values on the Unannounced Seasonal Generation Verification Test via the NDCRC application on the ERCOT MIS in a reasonable timeframe. MIS>Applications>NDCRC |
| Retest | QSE can request a retest up to two times per month: - If approved, a QSE-requested retest will take place either: - Within the first twenty-four (24) operating hours of the designated Generation Resource after the request for retest, OR - Three (3) Business Days after the request for retest - Any VDI issued as a result of a QSE-requested retest will be considered as an instructed deviation only for compliance purposes. ISSUE: - VDI to QSE - Choose “UNANNOUNCED CAPACITY TEST (NOTE IF RETEST)” as the Instruction Type from Resource level - In text, state “RETEST” |
| Notify | Notify test completion by e-mail (include resource(s), date and time) - OPS Planning - Shift Supervisors |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Regional Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 6.3.(1) | 22 (B) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-002-2.1 R3, R6.3, R7.2 | EOP-004-1 R1, R3.1 | EOP-001-0 R4.1, R5 | IRO-014-1 R1.1.2 |
|  | TOP-002-2 R4 | DOE OE-417 |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template around 0300 – 0400 and again around 1400 – 1500 each day. See section 2.7 of the Desktop Guide for instructions. DO NOT add editorial comments that reveal market sensitive data. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - Conditions change that required new notices to be issued or cancelled (e.g., OCN , Advisory, Watch, or Emergency Notice ) - A projected reserve capacity shortage develops - Local reliability concerns arise including actual overloads or loss of load - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas restrictions, not expected to cause reliability issues - A DCS event - Deployment of Load Resources Send updated report when conditions have returned to normal. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2A - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EEA Level 2A in effect Potential for EEA Level 2B - N/A – No EIL available - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 2B in effect Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - EEA Level 2B in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 3 in effect |  |
| ### Texas RE Event Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, within one hour: - COMPLETE the form located in Section 2.5 of the Desktop Guide:“Texas RE Event Form” - E-MAIL the form to the distribution group entitled “TRE Event” - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis process, events include the following: Category 1 Events: - Loss of a bulk power transmission components(s) in response to a single-phase line-to-ground fault with delayed clearing (stuck breaker or protection system failure) - Simultaneous loss of three or more BPS elements (i.e. generators, transmission lines, and buses 100kV and above) (Combine Cycle Train counts as one element) - Frequency below the Low Frequency Trigger Limit (FTL) or above the High FTL for more than 15 minutes - Special Protection System (“SPS”) activation (only if generation was removed from system) - DC-Tie trips - Unintended system separation resulting in an island of up to 1,000 MW Category 2 Events: - Loss of an entire generation station of five or more generators (aggregate generation of 500 MW or higher)(Combine Cycle Train counts as one generator) - Loss of off-site power to a nuclear generating station - Loss of all BPS control center voice or data functionality for 30 minutes or more (Includes ERCOT, QSE or TO) - Unplanned evacuation from BPS control center facility (Includes ERCOT, QSE, or TO) - Unintended system separation resulting in an island of 1,001 MW to 4,999 MW Category 3: - Loss of load or generation totaling 1,000 MW or more (excluding SPS/RAP, UFLS, or UVLS actuation) - Unintended system separation resulting in an island of 5,000 MW – 10,000 MW Category 4: - Loss of load or generation totaling 5,0001 MW – 9,999 MW (excluding SPS/RAP, UFLS, or UVLS actuation) Category 5: - Loss of load or generation totaling 10,000 MW or more |  |
| NOTE | If an OE-417 or NERC Preliminary Report is required, there is no need to also complete a Texas RE Report. |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations or designee when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". |  |
| OE-417 Reporting Events | DOE OE-417 initial reports are to be completed within 1 hour, forms can be downloaded at: ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc OE-417 reports are required for the following events: - System wide voltage reduction of 3 percent or more - Public appeal to reduce the use of electricity - Load shedding ≥ 100 MW - Uncontrolled loss of Firm Load ≥ 300 MW for 15 minutes or longer - Physical sabotage, terrorism or vandalism (suspected or real) - Cyber sabotage, terrorism or vandalism (suspected or real) - Fuel supply emergencies (fuel inventory ≤ 50% of normal) - Loss of electric service (≥ 50,000 for 1 hour or more) - Total system collapse |  |
| NERC IROL and Preliminary Disturbance Report EOP-004-1 | NERC Preliminary Disturbance reports are to be completed within 24 hours, forms can be downloaded at: http://www.nerc.com/page.php?cid=5¦66 NERC Disturbance reports are required for the following events: - Loss of generation ≥ 1,000 MW - IROL violation (self report) - Loss of major system component that significantly affect integrity of system - Voltage excursions equal to or greater than ±10 percent lasting more than five minutes - Loss of firm load demands totaling more than 200 MW or 50 percent of the total customers (applies to TOs) |  |
| 1 | When required to file a report (If Manager or designee is unavailable): Forward the TO or QSE report or the Director of Cyber Security’s report to: - NERC (esisac@nerc.com, fax (609) 452-9550) - DOE (doehqeoc@oem.doe.gov, fax (202) 586-8485) - “NERC and DOE Disturbance Reporting” e-mail list. |  |
| ### RCIS Reporting |  |  |
| NOTE | Refer to Section 2.2 in Desktop Guide: Operating State Alert Levels. |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” (ERCOT EEA Level 2A or 2B) - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| TEA Postings | There are four levels of Transmission Emergency Alert (TEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “System Emergency”: - “ERCOT is declaring TEA 1 on the North-Houston interface” - “ERCOT is declaring TEA 2 on the North-Houston interface; Load Resources have been deployed in the Houston area”. - “ERCOT is declaring TEA 3 on the North-Houston interface; firm load is being curtailed in the Houston area”. - “ERCOT is in TEA 0 and back to normal operations” |  |
| SEA Postings | There are four levels of Security Emergency Alerts (SEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “CIP Free Form”: - “ERCOT is declaring SEA 1 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 2 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 3 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is in SEA0 and no longer under threat”. |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2A, THEN: - Select the “SO EEA Level 2A” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2B, THEN: - Select the “SO EEA Level 2B” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2B” Scenario and activate notification, WHEN: - EEA Level 2B is terminated, THEN: - Select the “SO EEA Level 2B to EEA Level 2A” Scenario and activate notification, WHEN: - EEA Level 2A is terminated, THEN: - Select the “SO EEA Level 2A to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed, THEN: - Select the “Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 2.7.8 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO Monthly Test Message” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on P:\SYSTEM OPERATIONS drive in the PUCT Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” - The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| 1 | Weather Information - Enter the High and Low temperature forecast from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Enter the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Enter the Previous Day Actual MW. |  |
| 3 | Interchange - Enter the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Enter the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals - Enter the Generation scheduled outage MW total. - Enter the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves - Enter the Responsive Reserve requirement at the Project Peak. - Enter the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity - No action needed |  |
| 8 | Comments - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically during the day, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | When alerts and warnings for GMDs are issued for K-7 or higher: - Notify the TOs and QSEs by posting message on MIS Public us Request Shift Engineer to calculate limits manually if EMS is available.ing Notice Builder, - Log the information. |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability. |  |

## 10.2		EMMS and Interface System Failures

Procedure Purpose: Provide guidance to the Shift Supervisor for coordinating with the ERCOT IT Help Desk if critical functions or systems fail such that system operators and/or participants are precluded for performing and complying with their obligations and therefore jeopardizing the security of the system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1.1 R5 | EOP-008-0 R1.4 |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step |  | Action |  |
| --- | --- | --- | --- |
| 1 |  | If any Control Room computer systems (ICCP, Web Portal, MIS, or API) events, failures, or incidents that affect normal operations occur, - DETERMINE criticality and impact to the reliability to the grid, - CONTACT the ERCOT Help Desk immediately from the Supervisor Help Desk button on the Turret Phone or extension 6804. If necessary, contact the on-call IT person first then contact the Help Desk. |  |
| NOTE |  | For a complete EMMS failure, see Transmission and Security Procedure Section 3.3, Analysis Tool Outages and/or DC Tie Desk Procedure Section 4.1, Loss of Primary Control Center Functionality. |  |
| 2 |  | IF: - Any of the aforementioned systems fail and are effecting ERCOT systems or multiple Market Participants and will be unavailable for longer than 15 minutes; THEN: - Notify market participants of the problem and expected duration via Hotline, - Request additional assistance from other support staff. |  |
| 3 |  | When the problem is resolved, Notify all participants via Hotline of the problem resolution. |  |
| Log |  | Log the following: - Date - Time of event - Description of system alarms, events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| ## Data and/or Voice Communication Failures |  |  |  |
| 1 |  | Notify the Help Desk of the loss and REQUEST assistance to re-establish voice and/or data communications. - Telecommunications group will be responsible for voice communications. - EMMS Production group will be responsible for data communications |  |
| 2 |  | Use back-up communications if needed such as the Control Room cell phone, Standalone Satellite phone or the PBX Bypass phones to maintain communications with the other control room, TOs, QSEs, SPP and any other entities as needed. The list of phone numbers is located in the Phone Book at Shift Supervisor’s Desk and also programmed into the cell phone. |  |
| 3 |  | IF the criticality and impact of events or failures is such that Market Participants are, or will be affected before the problem can be resolved, THEN: - Instruct ERCOT System Operator to NOTIFY the other ERCOT Control Room and all market participants via Hotline of the problem and expected duration. If Hotline is unavailable utilize any of the following methods: - Control Room cell phone, PBX Bypass phones, or Standalone Satellite phone. - REQUEST additional assistance from other support staff, as needed. |  |
| NOTE |  | Steps 4 & 5 may be performed in any order. |  |
| 4 |  | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| 5 |  | When the problem is resolved, NOTIFY all participants via Hotline of the problem resolution. |  |
| ## Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms |  |  |  |
| NOTE |  | - Normal status for the Dynamic Rating, SCED Status, EMBP, SE, RTCA and RLC Status is indicated by each status box constant green on the “ERCOT & QSE Summary Page” in the PI system. - Failure of the PI server is indicated by abnormal status of Dynamic Rating, SE and RLC, accompanied by the PI system “flat-lining” - Dynamic Rating, SE and RLC status boxes flashing red AND PI flat-lining may indicate failure of the EMS. |  |
| Monitor |  | PERFORM the following as applicable to the indicated conditions: - IF only the Dynamic Ratings status box is flashing red, CONTACT the ERCOT Help Desk - TELL them the Dynamic Rating Alarm status in Processbook is flashing red and the dynamic ratings are not being sent to the SCADA in the EMS. - REQUEST they notify the on-call EMMS Production person of the situation. - IF only the RLC status box is flashing red, CONTACT the ERCOT Help Desk - TELL them the RLC Alarm status in Processbook is flashing red - DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the SCED Status box is flashing red, - Follow the Managing SCED Failures in the Real Time Desk Procedure. - If SCED failure can’t be resolved CONTACT the ERCOT Help Desk and DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the EMBP box is flashing red, - Determine the reason Emergency Base Point are being issued, - Remove the Emergency Base Point flag when condition allow, - If EMBP can’t be resolved CONTACT the ERCOT Help Desk and DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the SE status box is flashing red, CONTACT the ERCOT Shift Engineer - TELL them the SE Alarm status in Processbook is flashing red - IF only the RTCA status box is flashing yellow or red, CONTACT the ERCOT Shift Engineer - RTCA executes every 5 minutes, if RTCA doesn’t complete within the desired threshold the display changes colors - Greater than 10 minutes but less than 15 minutes turns - Yellow - Greater than 15 minutes turns - Red - TELL them the RTCA Alarm status in Processbook is flashing yellow/red |  |
| ## Building Security and Fire Alarms |  |  |  |
| NOTE | The Shift Supervisor or designee will ensure staff members adhere to emergency evacuation procedures and evacuate all team members from the Control Room if an emergency evacuation is required. |  |  |
| 1 | IF: - Building security or fire alarm sounds, THEN: - Contact Security’s Emergency Number if Security has not already made communications with the Control Room. |  |  |
| 2 | IF: - It is determined it is a drill, THEN: - Retrieve the ‘orange’ bag for the employee roster, - Account for each operator by marking them present and return form to Security staff at front desk (if able). IF: - If unable to return roster in a reasonable timeframe, CONTACT: - Security and request them to retrieve roster during the next patrol. |  |  |
| 3 | IF: - Control Room personnel are in danger or ordered to be evacuated, THEN: - Transfer control of the Grid to the Alternate Control Center (see “Loss of Primary Control Center Functionality” procedure Section 4.1 in the DC Tie Desk Procedure), - Request additional assistance from other support staff, - Evacuate the Control Room to a safe area for Zone #1, - Retrieve the ‘orange’ bag for the employee roster, - Account for each employee by marking them present at the rally point. |  |  |
| 4 | Notify the Manager, System Operations or designee as soon as practical. |  |  |
| ## Failure of the Emergency Generator |  |  |  |
| 1 | If the Facilities emergency generator fails to start, you will be notified by the Facilities Staff. |  |  |
| 2 | If the Facilities Staff or the Shift Supervisor determines that it will be more than 20 minutes before the emergency generator can be started, the Shift Supervisor may consider initiating the “Loss of Primary Control Center Functionality” procedure. |  |  |
| 3 | The Shift Supervisor or his/her delegated representative should notify the Manager, System Operations that the controls have been transferred to the other control center. |  |  |
| 4 | REQUEST additional assistance from other support staff as needed. |  |  |
| NOTE | See section 2.1 of the Desktop Guide: Emergency Communication/ Notification Guidelines. |  |  |