## Power Operations Bulletin # 509

ERCOT has posted/revised the NODAL Transmission and Security Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.2	Alarm Processing and Acknowledgment

Procedure Purpose: To monitor and acknowledge system alarms.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-1 R6, R8 | IRO-003-2 R2 | IRO-005-2 R1.1, R1.2 | TOP-002-2 R8 |
|  | TOP-006-1 R2, R5 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: |
| Categories | Tab 1: 345 KV Transmission Equipment Status Tab 2: 138 KV Transmission Equipment Status Tab 3: Generator Breaker, AVR, CAPS, REACTOR and SPS Status Tab 4: RLC alerts Tab 5: Transmission Line Overloads - Voltage Violations - Critical Alarms Tab 6: QKNET alarms Tab 7: ICCP status Tab 8: All other alarms |
| 1 | Monitor the Alarm Summary Display pages 3, 6 and 7 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as system conditions warrant. |
| 3 | Coordinate with the Real-Time Operator to clear the alarms approximately every 2 to 3 hours or as needed. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006 R1, R4 |
|  | IRO-002 R6, R8 | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| NOTE | For any post-contingency overload greater than 100%, determine if the overload is caused by a temporary outage on a transmission line(s) or a transmission facility. Refer to Post-Contingency Overloads section of this procedure. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the Emergency Management System (EMS) and an electronic copy is located on the ERCOT Market Information System (MIS) Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) located in the Outage Notes. - Unit specific dispatch instructions (Manual Dispatch or VDI) after declaring a Watch. - If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - The electronic version is located at P:\System Operation\Remedial Action Plans, - A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congesting management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – mitigate local congestion and increase W/N transfers - Big Lake – mitigate local congestion and increase W/N transfers - Firerock ETT – mitigate local congestion and increase W/N transfers - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - RTNET and RTCA have not solved within 10 minutes; THEN: - Notify Shift Engineer, AND - Refer to the “Analysis Tool Outages” procedure. |  |
| 2 | IF: - RTCA has run within 10 minutes; THEN: - Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |  |
| 3 | IF: - A major change of Resource or Transmission Element Status; THEN: - Re-start RTCA and VSAT. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Determine if the SCADA is of similar magnitude to the Pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Shift Engineer. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP, - Refer to “Managing Binding and Violated Constraints” of this Procedure. |  |
| 4 | IF: - Post-contingency overloads greater than 100% exist without an SPS (identified as RAS in EMS), RAP, PCAP, or TOAP in place to relieve; THEN: - Activate constraints as necessary, - Lower the value in the % Rating column in RTCAM to tighten the constraint (minimum of 95%), - Increase the value in the % Rating column in RTCAM to loosen the constraint (maximum of 105%), - Manually execute the SCED process, - Refer to “Managing Binding and Violated Constraints”. |  |
| 5 | IF: - There is an imminent threat to the reliability of the ERCOT system, caused by a Qualifying Facility (QF), and ERCOT decides to order the QF offline or to operate below its LSL; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT/ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Emergency Notification to QSEs, - Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to an immediate threat to the reliability of the ERCOT system that required directing a Qualifying Facility [offline/operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 6 | IF: - Post-contingency overloads greater than 100% of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Violated Constraints”. |  |
| 7 | IF: - Any RTCA results predict a Facility Rating will exceed post-contingency loading of 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL; THEN: - Refer to section 4.2 “Potential IROL’s”. |  |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Violated Constraints”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |  |
| 9 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Shift Engineer, - If there are known reasons that the contingency is unsolved, notify the Shift Engineer to verify system conditions have not changed. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A Quick Start Resource is needed and not given SCED base points; THEN: - Override LDL to a level greater than or equal to the COP LSL (DO NOT override while SCED is running). |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| ### Transmission Issues in the Areas of the CFE DC-Ties |  |  |
| 1 | IF: - Contingencies or unsolved contingencies cannot be corrected with congestion management techniques; THEN: - Determine if there are schedules over the CFE Ties that would help the situation. |  |
| 2 | IF: - DC-Tie schedules can be curtailed to alleviate the transmission issue; THEN: - Notify the DC Tie Operator to curtail the schedule(s), - Issue a Transmission Watch or Emergency, - Make Hotline call, - Make notification on MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Transmission [Watch or Emergency] due to a post contingency loss of (name of contingency) overloads (name of overloaded element).” [TO] please repeat this back to me. That is correct, thank you.” Edit script as needed to fit situation. |  |
| ### Managing Binding and Violated Constraints |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take manual action if the constraints become violated. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| 1 | IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk and control room staff, - Determine the need for resolving the constraint by over-riding LDL (hold up) and/or HDL (hold down) (DO NOT override while SCED is running). |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/violated constraints, limits, maximum shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for violated constraints). |  |
| 2 | IF: - The transmission element flows are greater than the limit (violated); THEN: - Verify that the successive SCED executions are reducing the flows on the subject constraints. |  |
| 3 | IF: - The constraint is not managed fast enough; THEN: - Create a “Suggestion Plan” for the constraint, - Take the appropriate manual action to resolve the violation, - Instruct the Shift Engineer to consult with the appropriate TO(s) to determine if there is a network re-configuration or post-contingency switching action that could be used to resolve the potential violation. |  |
| 4 | IF: - Any modifications are made to the constraints in TCM (e.g. changing to % Rating to tighten or loosen the constraint, activate a new constraint, or remove an active constraint); THEN: - Investigate units with large shift factors that are not being moved or are not following basepoints, - Manually execute SCED for each change (coordinate with Real-Time Operator), AND - Repeat the review process. |  |
| Log | Log all action taken. |  |
| ### Reaching Shadow Price Cap |  |  |
| NOTE | Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary Review the DSP Constraint Summary display, a constraint has reached its max shadow price cap when the Flow (MW) is higher than Limit (MW). |  |
| 1 | Steps that may be taken to resolve congestion when a transmission constraint is violated in SCED after the Shadow Price reaches price cap include: - Redistribution of Ancillary Services to increase the capacity available within a particular area, - Formulating a mitigation plan which may include - Transmission reconfiguration (switching) - Load rollover to adjacent feeders - Load shed plans - Commitment of additional units, - Re-dispatching generation through over-riding HDL and LDL (DO NOT override while SCED is running), |  |
| ### QSE Requests to De-Commit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a Resource; THEN: - Perform a real-time study to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Deployment/Termination of Non-Spin Reserve Service for Congestion |  |  |
| Deploy Non-Spin For Congestion | IF: - A particular Resource providing Non-Spin Reserve Service is needed to resolve an otherwise irresolvable constraint; THEN: - Notify the Resource Desk Operator to deploy Non-Spin on specific resources, AND - Contact the RUC Operator of the deployment. |  |
| Recall Non-Spin | WHEN: - The condition requiring the use of Non-Spin has been resolved; THEN: - Notify the Resource Desk Operator to recall Non-Spin on specific resources, AND - Contact the RUC Operator of the deployment. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure, - It will be necessary to manage transmission congestion manually by overriding HDL/LDL (DO NOT override while SCED is running). |  |
| 2 | Trouble Shooting: IF: - Transmission constraints are active, THEN: - Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |  |

## 4.2	Potential IROL’s

Procedure Purpose: To identify potential IROLs.

| Protocol Reference | 6.5.7.1.10 (3) | 6.5.9(1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R3.2, R4.2 | FAC-011-2 R1, R3 | IRO-002-1 R6, R8 | IRO-003-2 R1 |
|  | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R9, R16, R17 | TOP-002-2 R10 | TOP-004-2 R1, R6, R6.6 | TOP-008-1 R1 |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | IF SE results indicate and/or RTCA predicts any of the below conditions on the 138kV or 345kV system and no SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP exists; notify Operations Support Engineers: - Post contingent rating exceedance in excess of 125% of the SOL of the monitored facility (2-hour or Emergency Rating) - Basecase exceedance exist in the State Estimator greater than 100% of the SOL of the monitored facility (Continuous or Normal Rating) - An unsolved or divergent contingency is present - Under-voltage condition characterized by bus voltages of less than 90% across three or more related BES facilities - Over-voltage condition greater than 110% across three or more BES facilities |
| 1 | IF: - SCED is unable to resolve congestion and leading into an insecure state; THEN: - Confirm that pre-determined relevant RAPs are properly modeled in the system, - Override HDL (hold down) and/or LDL (hold up) making every effort not to surpass the HASL and/or LASL on the associated facility or facilities (DO NOT override while SCED is running), - Deactivate non-cascading contingency overload/constraints in TCM on the CAM display to remove from the SCED process, - Notify Resource Desk Operator if this caused “undeliverable” or “stranded” Ancillary Services, - Contact Shift Engineer to develop a Mitigation Plan, and - If all other mechanisms have failed, continue to step 2. |
| 2 | IF: - Still heading into an insecure state; THEN: - Over-ride HDL (hold down) and/or LDL(hold up) regardless of the HASL and/or LASL (DO NOT override while SCED is running), - Use Non-Spin Resources if available to resolve congestion, - Notify Resource Desk Operator if action caused “undeliverable” or “stranded” Ancillary Services if necessary, - Declare a Transmission Watch until Mitigation Plan is received, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |
| 3 | If Operations Support Engineer determines this to be an IROL after conducting offline studies. They will provide an IROL Tv (minutes). |
| 4 | Facility Rating violations must be relieved within the IROL Tv (minutes). |
| 5 | Make log entry: - Facility Rating violation being treated as potential IROL, - All actions implemented |

## 4.3	West-North Stability Limit

Procedure Purpose: Maintain Transmission stability between the West and North.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Refernce |  |  |  |  |
| NERC Standard | EOP-001 R4.2 | IRO-002 R6, R8 | IRO-003 R1 | IRO-004 R3 |
|  | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 | TOP-004 R1, R2, R6, R6.6 |
|  | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North stability limit is an IROL; The actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | IF: - The West-North stability limit calculated on the spreadsheet changes value or color; THEN: - Verify the value is accurate and update limit on RTMONI to give transparency to Market Participants, - Monitor as needed to the value shown on the spreadsheet. |
| NOTE | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change. It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| 2 | IF: - The monitored flow on the Stability-WN monitor is approaching 90% and wind generation is climbing; THEN: - Activate the appropriate constraint and manually execute RTCA and then SCED, - Post message on MIS Public using Notice Builder - Notify Real-Time Operator to make phone calls to any WGR not following their base points. Typical Message Script: “ERCOT is constraining for the West-North stability limit.” |
| 3 | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - Congestion management techniques fail to control the flow within 15 minutes; THEN: - Manually dispatch Wind Generation Resources down by over-riding HDLs (hold down) (DO NOT override while SCED is running). - Notify the control room staff. |
| Log | Log all actions taken. |

## 4.4	North-Houston Voltage Stability Limit

Procedure Purpose:  Maintain Transmission Stability between the North and Houston.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R2, R4.2 | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 |
|  | IRO-004 R3 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT Dynamic Voltage Stability Limit is an IROL; The actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards, |
| VSAT | - Ensure VSAT runs every hour, - Update RTMONI with new limit each hour to give transparency to Market Participants. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| North-Houston 345kV Circuit Outage | IF: - Any of the 345kV lines going into the Houston area has a forced outage; THEN: - Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor Step in this procedure. |
| Monitor | Monitor each of the following Reliability Margins: - O-H_L - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TOs in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| ≤400MW | - Activate the appropriate constraint, - Post message on MIS Public using Notice Builder. Typical Message Script: “ERCOT is constraining for the North-Houston voltage stability limit.” |
| ≤300MW | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL - Instruct Resource Desk Operator to deploy Non-Spin in the Houston area and make Hotline notification, - Issue a Transmission Watch by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. ERCOT is issuing a Watch for the North-Houston interface. Non-Spin is being deployed in the Houston area to help mitigate the North-Houston voltage stability limit which is an IROL. [TO] please repeat this back to me. That is correct, thank you.” |
| ≤200MW | VDI QSGR in the Houston area that were not bid in as Non-Spin. Over-ride LDLs as needed. - Determine QSRG in the Coast Weather Zone (WZ_COAST) - Choose “COMMIT” as the Instruction Type from Resource level |
| ≤100MW | - Instruct the Resource Desk Operator to deploy Load Resources providing RRS in Houston, - Issue a Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Real-Time Operator to make same Hotline notification to QSEs, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice for the North-Houston interface. Load Resources in the Houston area are being deployed to help mitigate the North-Houston voltage stability limit which is an IROL. [TO] please repeat this back to me. That is correct, thank you.” |
| 0MW ≥ 15 Minutes | - Instruct Centerpoint to drop firm load in 100 MW blocks. - Continue Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make NXT notification and RCIS posting. Typical Script for Centerpoint: This is ERCOT operator [first and last name]. ERCOT is continuing the Transmission Emergency Notice and is instructing Centerpoint to drop [*** MWs] of firm load for the North – Houston stability limit. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” Typical Script for Hotline: “ERCOT is continuing the Transmission Emergency Notice for the North-Houston interface. Firm Load is being shed in the Houston area to help mitigate the North-Houston voltage stability limit which is an IROL. [TO] please repeat this back to me. That is correct, thank you.” |
| Cancel | Make appropriate cancellations when back to normal operations. |
| Log | Log all actions taken. |

## 4.5	SPS, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 5.5.2 | 6.5.1.1(a),(c),(e) |  | 6.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.5.2(1) | 6.5.7.1.10 | 6.5.7.1.11(1),(4) | 6.5.7.8 |
|  | 6.5.9 | 6.5.9.1(1)(d) |  | 7.1 |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R2, R3.2, R3.3, R4.2 | IRO-003 R1 | IRO-005-2 R1.1,R1.2, R1.3, R1.7, R1.10, R3, R5, R9, R12, R13, R16, R17 | IRO-006-3 R1, R3, R4, R5, R6 |
|  | IRO-002-1 R6, R8 | IRO-004-1 R3 | TOP-001 R1, R2, R5 | TOP-002-2 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006-1 R3, R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6, R8 |
|  | PRC-001-1 R6 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at P:\Remedial Action Plans |
| NOTE | Special Protection Schemes (SPS) (identified as RAS in EMS) OR Remedial Action Plans (RAP) - EXAMINE the results of RTCA, - If the background has a color indicating a SPS or RAP, - Refer to Section 3.6 of the Desktop Reference Guide for actions to be taken based on the color of the background. |
| Directives | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log all actions taken. |
| Special Protection Systems (SPS) (Identified as RAS in EMS) |  |
| NOTE | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingency loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario, congestion management is not needed until the criteria in Section 3.6 of the Desktop Reference Guide, is met. |
| Monitor | Each SPS will be displayed on the “Real Time Values” spreadsheet, as the SPS activation threshold increases the display changes color as follows: - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 1 | Typically SPSs are to solve post-contingency overloads on the Transmission System. IF: - The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an SPS; THEN: - Utilize congestion management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the SPS will not mitigate all the overloaded elements automatically; THEN: - As system conditions warrant, utilize congestion management techniques to relieve the overload. |
| 3 | IF: - No reliability issues will arise as a result of a SPS’s operation; THEN: - At the Operator’s discretion, allow the SPS to perform its function. |
| 4 | IF: - A WGR SPS on the “Real Time Values” spreadsheet is greater than 90%; THEN: - Active the appropriate generic constraint in TCM. |
| 5 | IF: - An SPS operates; THEN: - Notify affected TO to reset SPS as system conditions warrant, - Notify Shift Supervisor of the need for a Texas RE Report if generation disconnected from the grid or a transmission line tripped. |
| SPS Posting | All SPSs are considered in-service unless otherwise notified by the TO. If the SPS is out of service, ERCOT will post the information on MIS Public using Notice Builder. Once the SPS is placed back in service, ERCOT will cancel the message. Typical message: The [name] SPS has been taken out of service. |
| Status Change | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated, - “OPS Planning” - “OPS Support Engineering” - “1 ERCOT System Operators” Typical message: The [name] SPS has been taken out of service. The [name] SPS has returned to service. |
| Remedial Action Plan (RAP) |  |
| 1 | TCM DOES NOT model RAP when generating constraints so they tend to over-constrain at 100% of emergency rating instead of 100% of the 15min rating. - Activate constraints as necessary, - Lower the value in the % Rating column in TCM to tighten the constraint (minimum 95%), - Increase the value in the % Rating column in TCM to loosen the constraint (maximum 105%). |
| 2 | IF: - A RAP exists for the contingency; THEN: - Review the RAP with the associated TO, - Notify the Shift Supervisor of the anticipated actions. |
| 3 | IF: - The contingency anticipated by the RAP takes place; THEN: - Direct the implementation of the RAP, - Respond to requests made by the TO in accordance with the RAP, - If necessary, continue to use additional congestion management methods, - When the contingency clears, notify the TO as soon as possible. |
| Pre-Contingency Action Plan (PCAP) |  |
| CAUTION | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. These actions may be taken to increase transmission transfer capability. |
| 1 | WHEN: - RTCA shows a post-contingency overload and a PCAP exists to resolve it; THEN: - Review the PCAP with the associated Transmission Operator, - Notify the Shift Supervisor of the anticipated actions, - Direct the execution of the PCAP with the associated Transmission Operator. Typical Script: “This is ERCOT Operator [first and last name]. ERCOT is instructing [TO] to implement the ****PCAP and [open/close] [breaker(s)]. [TO] please repeat this directive back to me. That is correct, thank you.” |
| NOTE | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 2 | IF: - Any PCAPs are still in use (reviewed each day between 0000 and 0500), AND - It is determined, in concurrence with the Shift Supervisor that it is no longer needed; THEN: - Direct the associated Transmission Operator to return the system to: - Its normal status, OR - Its status prior to implementation of the PCAP. |
| Mitigation Plan (MP) |  |
| NOTE | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. - With a MP, an operator does not need to declare a Watch for a post contingency overload, - If a MP is enacted and subsequent congestion management techniques do not control post contingency loading, issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder |
| 1 | IF: - RTCA shows a post-contingency overload greater than 100% of the Load Shed Rating; THEN: - Attempt to resolve the overload by using congestion management methods. |
| 2 | IF: - A MP exists for the contingency; THEN: - Review the MP with the associated TO, - TOP repeats back the directive to verify the plan is understood, - Notify the Shift Supervisor of the anticipated actions. |
| 3 | IF: - A MP does not exist or fails to relieve the overload for this contingency and the Outage Notes do not provide a plan; THEN: - REQUEST the Shift Engineer investigate the development of a MP or correct errors in the current plan. |
| 4 | IF: - The anticipated contingency takes place; THEN: - Direct the implementation of the MP to the TO, - TO repeats back directive to verify implementation is understood, - Respond as quickly as possible to requests made by the TO in accordance with the MP, - If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP. |
| 5 | WHEN: - The contingency clears; THEN: - Notify the TO as soon as possible. |
| Temporary Outage Action Plan (TOAP) |  |
| 1 | IF: - The post-contingency overload is due to a temporary outage on a transmission line(s) or a transmission facility; THEN: - Locate the outage in the Outage Notes, - Implement the associated actions. |

## 4.6	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security.

| Protocol Reference | 6.3.2(2) | 6.5.7.1.10(3) | 6.5.7.8 | 6.5.7.9(7) |
| --- | --- | --- | --- | --- |
|  | 6.5.9 (3) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R6 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The order of steps in this procedure is a recommendation. The System Operator will determine the sequence of steps, or any additional actions necessary to ensure system security. |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instruction under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |
| ### Manual Dispatch Instruction to take a Unit Off-Line |  |
| 1 | This step DOES NOT apply to Qualifying Facilities (QF). For QF’s, refer to Transmission Congestion Management/Post-Contingency Overloads/step 5. IF: - A manual dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue a VDI taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Ensure QSE updates telemetry. |
| ### Taking One CT of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one CT of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and determine which CT should receive the dispatch instruction, - Obtain the MW output impact the CT’s dispatch instruction will have on the steam unit, - Issue VDI to dispatch the CT off-line and instruct the QSE to adjust their CC configuration. - Choose “DECOMMIT” as the Instruction Type from Resource level |

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15 | 6.1.7 | 6.3.1 (1) | 6.3.2(2) |
| --- | --- | --- | --- | --- |
|  | 6.5.1.1(a)&(c) | 6.5.5.1(2) &(3) | 6.5.6 | 6.5.7 |
|  | 6.5.7.7 | 6.5.9.1(1)(c) | 6.6.7.1 | 6.7.6 |
| Guide Reference | 2.2.4 | 2.7.2(h)(ii) | 2.7.4.1(1) | 2.7.4.3 |
|  | 5.1.4 |  |  |  |
| NERC Standand | IRO-005-2 R1.2, R1.3, R1.4 | NUC-001-2 R4.2 | TOP-002-2 R8, R10 | VAR-001-1 R1, R2, R4, R6, R7, R8, R9, R10, R12 |
|  | VAR-002-1 R3.1 | IRO-002-1 R6, R8 | TOP-004-2 R6.2 | TOP-006-1 R2 |
|  | EOP-001-0 R4.2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "normal" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS). Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Voltage Tables | For Comanche Peak - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. For South Texas Project - System; - 345 kV. - Nominal Voltage; - 362.25 kV. - Tolerance; - +0% or -6.14%. - Maximum Voltage; - 362.25 kV. - Minimum Voltage; - 340 kV. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. When STP is in an alternate line up, the minimum voltage is 347 kV. When STP is in an alternate line up without the unit auxiliary transformer, the minimum voltage is 355 kV. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated in the voltage tables; THEN: - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate QSE. |
| ### Voltage Issues |  |
| NOTE | - Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Section 3.9 of the Desktop Guide. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damages is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implements and studies shall that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. |
| 1 | WHEN: - Indicated by SCADA alarms, OR - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. |
| 2 | When instructing a QSE to raise or lower bus voltage when area TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) should be as follows: Typical Script: “This is ERCOT Operator [first and last name]. ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| Exceed URL | For multi-generator busses, ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL until all On-Line Generation at the same transmission bus have been instructed to their respective CURLs or URLs. IF: - Instructing a QSE’s Generation Resource to exceed its Unit Reactive Limit (URL); THEN: - Issue a VDI to the QSE for exceeding the URL (Exceed URL VDI). The VDI must include the following: - Resource name - Specific voltage set point. - Start time - End time - Choose “HOLD X VOLTAGE LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| Reduce MW | IF: - MW output must be reduced to follow a voltage support instruction; THEN: - Issue a VDI to the QSE providing Voltage Support Service (VSS VDI). The VDI must include the following: - Resource name - MW level at time of instruction - MW level Resource needs to move to for Voltage Support - Start time - End time - Choose “STAY AT/ABOVE X MW/MVAR LEVEL” or “STAY AT/BELOW X MW/MVAR LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| NOTE | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure XX. |
| 1 | IF: - VSAT has not run in the last 80 minutes, OR - S-H or N-H 345kV circuit has a forced outage, OR - VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status; THEN: - Rerun the RTNET, RTCA, and RTDCP (VSA). If no change, then: - Notify the Shift Supervisor and Shift Engineer - As deemed necessary make the following Hotline call. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is experiencing problems with the Voltage Stability Analysis program. Maintain voltage levels as required by your procedures and notify ERCOT of any voltage issues within your system. [TO] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) more frequently than the periodic scheduled VSAT run. - Confirm VSAT indicates either “Normal” or “Pending”. Reliability Margin Table. Scenario Name; Safety Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. HHGT_G-O; 0MW. |
| For HHGT_G-O | For HHGT_G-O: Instruction the QSE to raise or lower bus voltage: Typical script: “This is ERCOT operator [first and last name]. ERCOT is instructing [QSE] to [raise or lower] voltage at [specified bus] by (+ 1 or 2 kV or – 1 or 2 kV) for a target of [target kV] [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| 3 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the Extra-Interface Limit pre-contingency value is less than the Safety Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 4. |
| 4 | Determine the contingency status in RTCA (solved/unsolved).IF: - Solved, - Have Shift Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Shift Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct HRUC Operator to commit additional resources in the weak bus area that are available. |
| 5 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 6 | Determine if the Extra-Interface Limit pre-contingency value is greater than the Reliability Margin Value. IF: - The Extra-Interface Limit pre-contingency value is greater than the Reliability margin; THEN: - No further action is required. OR IF: - The Extra-Interface Limit pre-contingency value is less than the Reliability margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 4. If no additional generation is available, continue. |
| 7 | IF: - No additional generation is available; THEN: - Ensure that the OPS Support Engineering group has been contacted to devise a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT. |
| NOTE | Operations Planning will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT SharePoint > Operations Support > AVR AND PSS Status |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, - Notify the appropriate TO of the change in status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “OPS Planning” - “OPS Support Engineering” - “1 ERCOT System Operators” |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. To update the “real time values” spreadsheet when any PSS is forced offline in the West zone: - Open the Stability Limit tab to verify units, - Enter 0 = PSS is offline; 1 = PSS online for each resource change. It allows the Operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |

## 7.4	Block Load Transfer

Procedure Purpose:  To transfer loads, located in ERCOT to a Non-ERCOT system or from a Non-ERCOT system to ERCOT during emergencies conditions.

| Protocol Reference | 6.5.9.5 | 6.5.9.5.1 | 6.5.9.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.4 |  |  |  |
| NERC Standard | EOP-001-0 R3.2, R4.2, R7.2, & R7.4 |  |  |  |

| Version: | 1 | Revision: | 1 | Effective Date: December 1, 2010 |
| --- | --- | --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Restoration of service to outage customers using BLT’s will be accomplished as quickly as possible if the transfers will not jeopardize the reliability of the ERCOT Interconnection. - BLTs that are comprised of looped systems may be tied to the non-ERCOT Control Area’s electrical system(s) through multiple interconnection points at the same time. Transfers of looped configurations are permitted only if all interconnection points are registered and netted under a single Electric Service Identifier (ESI ID) and represented by a single TSP or DSP or netted behind Non-Opt In Entity (NOIE) metering points. |
| ### ERCOT picks up Load for Non-ERCOT System |  |
| 1 | IF: - ERCOT is requested to pick up load for CFE, SERC, or SPP; THEN: - Consult with Shift Engineer to ensure no reliability issue exists, - Refer to Desktop Guide and determine the following: - Is the BLT registered, if “Yes”, proceed. (If not, see step 2) - Does the BLT require a VDI for settlement, - Is BLT in model, - Determine the amount of load being transferred into ERCOT, - Issue VDI to QSE if applicable - Choose “OTHER For QSE” - In text, state “BLT from SPP/CFE to ERCOT” - Send e-mail to “BLT” with information. |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Shift Engineer to ensure no reliability issue exists, - If no issues, allow the BLT, - Send e-mail to “BLT” with information and stating that it is not a registered BLT, - Determine the amount of load being transferred into ERCOT, - No VDI needed. |
| 3 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Issue an Emergency Notice and - Curtail or terminate the BLT. |
| ### Non-ERCOT System picks up Load for ERCOT |  |
| 1 | IF: - CFE, SERC, or SPP picks up load for ERCOT; THEN: - Consult with Shift Engineer to ensure no reliability issue exists, - Refer to Desktop Guide and determine the following: - Is the BLT registered, if “Yes”, proceed. (If not, see step 2) - Does the BLT require a VDI for settlement, - Is BLT in model, - Determine the amount of load being transferred out of ERCOT, - Issue VDI to QSE if applicable - Choose “OTHER For QSE” - In text, state “BLT from ERCOT to SPP/CFE” - Send e-mail to “BLT” with information. |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Shift Engineer to ensure no reliability issue exists, - If no issues, allow the BLT, - Send e-mail to “BLT” with information and stating that it is not a registered BLT, - Determine the amount of load being transferred out of ERCOT, - No VDI needed. |
| 3 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Issue an Emergency Notice and - Curtail or terminate the BLT. |