## Power Operations Bulletin # 510

ERCOT has posted/revised the NODAL Reliability Unit Commitment Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	Publish A/S Requirements and Review System Conditions

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

| Protocol Reference | 4.2.1.1 | 4.2.1.2 | 4.2.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1, R5 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Review and update A/S Requirements must be completed prior to 0500. - The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month. |
| ### Review Weather Data Information |  |
| 1 | REVIEW the Weather Data for the next operating day in the EMS. |
| 2 | REVIEW REFERENCE DISPLAY: EMS Applications>Weather Details>Real Time Displays>Weather Forecast Directory The Meterlogix phone number is (952) 882-4312. IF: - The Last Weather Source Update or Last Weather Read is less than one (1) hour old; THEN: - Using the usual sources, review the weather forecast for at least two days out. IF: - The data update or read is more than one (1) hour old; THEN: - Notify the Shift Supervisor and the Help Desk. |
| 3 | Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems. The trigger will usually be an extreme weather event which will cause temperatures to be below freezing for an extended period of time, though there could be other reasons. |
| ### Review and Select Load Forecast |  |
| 1 | - Review and Select load forecast for next day (Refer to Section 7.18 Select Day-Ahead MTLF in Desktop Guide). |
| NOTE | The Net Error Subtracted from the Load Forecast is scheduled based on the 2010 AS methodology. If ERCOT subtracts a MW value from the load forecast during the month additional Non-Spin will be procured. |
| ### Publish Ancillary Service Requirements |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| ### Invalid SPS/RAP due to Outage |  |
| 1 | Review outages notes and coordinate with Outage Coordinator and/or Shift Engineer to determine if an outage will have an effect on SPS/RAP/PCAPs. Market Participation > Physical Market > AS Market > AS Plan IF: - An SPS/RAP will be disabled next day due to an outage; THEN: - Notify the DAM operator to deactivate the invalid SPS/RAP. |
| ### Phase Shifter Tap Settings |  |
| 1 | The DAM Operator will make notification to the RUC Operator before they change the phase shifter tap settings for DAM. |
| 2 | When the DAM snapshots are complete, the DAM Operator will set the phase shifter tap settings back to the previous settings and notify the RUC Operator. |
| NOTE | Normal timeframe will be between 09:00 – 11:30 each day. If problems occur, contact the DAM Operator and see if they can replace the values earlier. |
| ### Priority Outages |  |
| 1 | A Priority Outage is one that affects generation. Prior to 1200: - From a review of the Outage Notes for the next Operating Day, make lists of Priority Outages, sorted by affected Transmission Operator, - The file is located in P:\DAY AHEAD – TDSP PRIORITY OUTAGE NOTIFICATION, - Print copies, - Fax the lists to the respective TOs accompanied by a request that within 30 minutes of the Actual Start and Actual End times of these Priority Outages, they enter the Actual Start and Actual End times in the Outage Scheduler, - Place in Daily Log File. |
| ### Verification of published A/S Requirements |  |
| NOTE | This step may be completed after 0600. |
| 1 | VERIFY by spot-checking the following information posted to the ERCOT Market Information System (MIS) for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - MIS; Grid; Transmission; Transmission Outages; Approved and Accepted Transmission Outages - Weather assumptions used to provide the system conditions forecast. - MIS; Markets; Day-Ahead Market; Operating Day System Conditions; Weather assumptions - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, and Non-spinning Reserve – NSPIN. - MIS; Markets; Day-Ahead Market; Ancillary Service Plans; DAM Ancillary Service Plan. |
| Log | LOG any significant problems including any action taken. |

## 4.2	Tasks prior to Execution of DRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.1 | 5.5.2(5) |
| --- | --- | --- | --- | --- |
|  | 5.5.2(9)(b) | 6.3.1(1) | 6.3.2(3)(a) | 6.4.2.5(3)(b) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### By 13:00 each day, perform the following |  |
| COP | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>Market Operator Data> Missing COP Check Market Participation>Monitoring>Event Manager>Events VERIFY: - “Missing COP Check” has automatically notified the QSEs of missing COPs; SELECT: - “START-NOW" in the Status column if not already completed by Market Operations. |
| Load Forecast | Review the Day Ahead Load Forecast in the EMS IF: - Adjustments need to be made in the EMS; THEN: - Adjust using the following: (Refer to Section 7.18 of the Desktop Reference Guide: Procedure to Select Day Ahead MTLF) Reference Displays: - Load Forecast - Similar Day Function - Load Forecast Scaling functions - Perform load scaling or - Perform peak scaling or - Perform factor scaling - Manually override forecast value(s) - Notify the Shift Supervisor if an invalid Load Forecast exists for the study period of DRUC. |
| Outage Notes/Off-Line Studies | IF: - Resources are needed for identified Voltage issues; THEN: - Once COPs have been updated, identify the appropriate resources that can be utilized if needed. |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow Parameters IF: - The EMSI Workflow Controller (Time Stamped – runs XX:50 every hour) function (data transfer between EMS and MMS) and Load Forecast are NOT running (should be continuous); THEN: - Notify Help Desk and Control Room Staff. |
| Bad/Suspect Telemetry | CHECK: - EMS Operator Alarms for major Generation Resources statuses with BAD/SUSPECT quality codes, IF: - Issues exists and will not be resolved before DRUC execution; THEN: - Discuss with Shift Supervisor if the DRUC should be run or delayed until the issues can be resolved. - Consider requesting Shift Engineer to manual over-ride of SCADA values (Be aware that this could skew the results), - If it is determined to delay DRUC, follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure. |
| RMR | IF: - The DAM market did not select a needed RMR Resource or it was determined later that an RMR Resource is needed; THEN: - Ensure COP status is “OFF”. - Manually commit (Refer to “Manual Commit” section of this procedure, if needed). |
| ### By 13:30 each day, perform the following |  |
| Deselect Contingencies | IF: - It has been determined with the help of Engineering Support that a contingency known to cause errors or that otherwise result in inconclusive study output in RUC; THEN: - After the Shift Engineer has deselected the contingency, - The contingency will be automatically posted no later than one hour after deselected to the MIS Secure Area. - MIS; Grid; Generation; Reliability Unit Commitment; Contingencies Deselected in RUC |
| NOTE | - The DRUC process may not be used to buy Ancillary Service unless the Ancillary Service Offers submitted in the DAM are insufficient to meet the requirements of the Ancillary Service Plan. - By default, Resources without an entry in COP are considered to have a Resource Status of OUT and are unavailable in RUC Procedure. |
| ### By 14:00 each day, perform the following |  |
| NOTE | As time permits, try to contact QSEs that have NOT submitted a COP for the DRUC study period. |
| Long Lead Times | Identify resources that have a lead-time greater than the DRUC timeline, WRUC results should be utilized for identifying resources with long lead-times. IF: - Resources are identified; THEN: - Commit the necessary resources as needed. |
| ### By 14:25 each day, perform the following |  |
| NOTE | If the DAM did not complete by 1330, then DRUC will be delayed. MPs need an hour between the completion of DAM and the opening of DRUC to update COPs. |
| Verify | Verify that the DAM has completed. IF: - DAM is aborted/ postponed after 1430; THEN: - Follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure. |
| Setting parameters for ONLINE | REVIEW REFERENCE DISPLAY: System Administration>Data Management Verify that “Connect to Schema” is set to “ONLINE”. |
| Verify | REVIEW REFERENCE DISPLAYS: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>DRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” |
| ### At 14:30 each day, perform the following |  |
| DSI | EXECUTE: - The DSI sequence VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact EMMS production support personnel immediately to determine the cause and expected time of resolution. |
| Verify | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MI DAM AS Insufficiency This display will give the Operator an indication if any A/S insufficiencies have occurred in DAM. If insufficiencies exist, the Operator can start looking at resources that can be committed to resolve the insufficiency in DSP. |
| E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS. IF: - Individual schedules need to be reviewed; THEN: - Go to the MI COP display and filter ‘ERCOT’ as the QSE name |
| Verify | - Identify and correct Bad/Suspect Telemetry - Modify Input for Block Load Transfer (BLT) movement - Modify Input for Verbal Dispatch Instructions Refer to Section 7.3 of the Desktop Guide |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays>External Input Data>DSI Data Processes>DSI Operator Manual Commitment IF: - An RMR unit is needed but is not to be considered in DRUC; THEN: - Commit unit before DRUC is executed. IF: - Additional resources are needed to solve for voltage issues; THEN: - Consult with the Shift Engineer and/or the Transmission and Security Desk Operator to determine which resources should be committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods; THEN: - Filter for the unit - Change ‘Auto’ to ‘On’, - List reason. |
| NOTE | If a RMR unit was committed in DSI Operator Manual Commitment and it is the only change since the DSI was last run the next step is not necessary. |
| Set Flags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the DRUC input data; CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No”, OR - “Use Save case set to “Yes” |
| Execute | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages Execute the entire DRUC sequence (Run All). |
| STNET Studies | Notify: - Shift Engineer to run NSA for each hour of the next operating Day. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 5.1 (9)&(11) | 5.3.(3) | 5.5.1(9) | 5.5.2 |
| --- | --- | --- | --- | --- |
|  | 5.5.3(2) | 6.3.1(1) | 6.4.6(4) | 6.4.8.1(3) |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | QSE’s may not change the quantity provided of each type A/S awarded through the procurement process or the aggregate amount of self-arranged A/S from the DAM. |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with the Market Operations and Shift Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published, IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for DRUC are invalid, - Notify the Manager or designee immediately, - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “Manage Capacity Insufficiency” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to “Use Suggestion Plan to Resolve Violated Constraints in DRUC” in Section 7.6, step 5 of the Desktop Guide. |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour, - Any under/over generation; THEN: - Be aware of these when running HRUC. |
| NOTE | The RUC process may not be used to buy A/S unless the A/S Offers submitted in the DAM are insufficient to meet the requirements of the A/S Plan. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Notified from Market Operations of A/S Insufficiency from DAM; THEN - Call the Market Participant and confirm that the unit can be started as required to supply the A/S Insufficiency, - Commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, entering the A/S amount in the reason column, - Refer to Section 7.1 of the Desktop Guide. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Shift Engineer to determine the validity; IF: - Invalid, no further action is required, - Valid; THEN - Locate the constraint on the DSP Constraint Summary display, - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, - Commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit; THEN - Determine the validity, - Determine the temporal constraints for each of the units, IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason. IF: - There is reliability reason requiring the resource commitment decision to be made immediately; - Resources with long start-up times - Resources returning from outages - Congestion or Capacity deficiencies that may create HRUC performance issues THEN: - Log the reason for not de-selecting the resource. |
| DRUC Committed For Capacity Shortage | IF: - DRUC recommends Resource(s)s for capacity; THEN - Determine if start-up time allows enough time to re-evaluate, and - De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: - Post an OCN and make Hotline call for projected Reserve Capacity shortage for hours short. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [hours]. [QSE] please repeat this back to me. That is correct, thank you.” |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Every effort should be made to manually commit resources that are needed before DRUC execution. IF: - Additional resources are needed to solve for transmission congestion or voltage issues and were not picked up in the DRUC run, AND - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period; THEN: - Change ‘blank’ to ‘Commit’ - List reason. |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments; DETERMINE IF: - Outage related’ - Possible Network Model error’ - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort; THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - External Input data - UC Displays - Input Display Menu - System TCG Data & System Load |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made; THEN: - Approve the results, OR IF: - The results are unacceptable; THEN: - Determine whether to rerun DRUC, OR - Follow the Manage DRUC Failure/Timeline Deviation procedure. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |

## 4.4	DAM/DRUC Failure/Timeline Deviation

Procedure Purpose: To address situations in which the DAM/DRUC process has failed.  Failures can be identified by software failure, results not approved in a timely manner or certain Emergency conditions.

| Protocol Reference | 4.1.2 | 4.5.2 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 | IRO-001 R9 |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### DAM Timeline Deviation/Failure |  |
| A/S Insufficiency | ERCOT will not begin executing the DAM sooner than 30 minutes after issuing a Watch. IF: - Notified by Market Operations of a A/S insufficiency in the DAM results; THEN: - Issue a Watch by making a Hotline (Market Operations will post message on the MIS): Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch due to insufficient Ancillary Services in the Day Ahead Market. ERCOT is requesting additional Ancillary Service Offers. [QSE] please repeat this back to me. That is correct, thank you.” |
| DAM Timeline Deviation | IF: - Notified by Market Operations that the DAM Market timeline is deviated; THEN: - Notify Shift Supervisor, - Issue a Watch by making a Hotline call (Market Operations will post message on the MIS): Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch for the timeline deviation of the Day Ahead Market for [effected date]; the start of DRUC will be delayed. Another hotline call will be made when DAM completes. [QSE] please repeat this back to me. That is correct, thank you.” |
| DAM Failure | IF: - Notified by Market Operations that the DAM Market has failed; THEN: - Notify Shift Supervisor and Resource Desk - Issue an Emergency Notice by making a Hotline call (Market Operations will post message on the MIS) : Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to the failure of the Day Ahead Market for [effected date] due to [state issue]. ERCOT will require all schedules and trades to be submitted in the Adjustment Period. QSEs will be notified by a Hotline call prior to ERCOT opening a SASM. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### DRUC Timeline Deviation/Failure |  |
| NOTE | After 1800, HRUC will run for the rest of the current day and the next day even if DRUC has not run successfully. |
| DRUC Delay | By 16:00 IF: - DRUC is delayed due to a system issue or delay in reviewing DRUC results; THEN: - Notify Shift Supervisor, - Issue a Watch by making a Hotline call - Post message on the MIS Public using Notice Builder: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch for the timeline deviation of DRUC for [effected date] due to [state issue]. DRUC will now start at [time]. [QSE] please repeat this back to me. That is correct, thank you.” |
| Abort Process | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow By 18:00 IF: - DRUC results cannot be approved; THEN: - “Abort DRUC Process” |
| 1 | IF: - DRUC software fails without expectation of timely repair, or due to time constraints due to not completing in a timely manner; THEN: - Notify the Help Desk and control room staff, - Issue an Emergency Notice by making a Hotline call - Posting message on the MIS Public using Notice Builder, - Be aware that you may need to procure any necessary Resources for the following Operating Day by VDI if RUC has failed. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to DRUC not completing by 1800 due to [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” |