## Power Operations Bulletin # 511

ERCOT has posted/revised the NODAL Transmission and Security Procedure Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006 R1, R4 |
|  | IRO-002 R6, R8 | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |

| Version: 1 | Revision: 2 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) located in the Outage Notes - Unit specific dispatch instructions (Manual Dispatch or VDI) - If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - The electronic version is located at P:\System Operation\Remedial Action Plans, - A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congesting management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – mitigate local congestion and increase W/N transfers - Big Lake – mitigate local congestion and increase W/N transfers - Firerock ETT – mitigate local congestion and increase W/N transfers - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - SE and/or RTCA is not solving; THEN: - Notify Shift Engineer, IF: - SE and/or RTCA has not solved for 15 minutes, THEN: - Refer to section 3.3 “Analysis Tool Outages” in this procedure. |  |
| 2 | IF: - RTCA has run within 10 minutes; THEN: - Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |  |
| 3 | IF: - A major change of Resource or Transmission Element Status; THEN: - Re-start RTCA and VSAT. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Determine if the SCADA is of similar magnitude to the Pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Shift Engineer. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP, - Refer to “Managing Binding and Exceeded Constraints” of this Procedure. |  |
| 4 | IF: - Post-contingency overloads greater than 100% exist without an SPS (identified as RAS in EMS), RAP, PCAP, or TOAP in place to relieve; THEN: - Activate constraints as necessary, - Lower the value in the % Rating column in RTCAM to tighten the constraint (minimum of 95%), - Increase the value in the % Rating column in RTCAM to loosen the constraint (maximum of 105%), - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 5 | IF: - There is an imminent threat to the reliability of the ERCOT system, caused by a Qualifying Facility (QF), and ERCOT decides to order the QF offline or to operate below its LSL; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT/ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to an immediate threat to the reliability of the ERCOT system that required directing a Qualifying Facility [offline/operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 6 | IF: - Post-contingency overloads greater than 100% of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 7 | IF: - Any RTCA results predict a Facility Rating will exceed post-contingency loading of 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL; THEN: - Refer to section 4.2 “Potential IROL’s”. |  |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |  |
| 9 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Shift Engineer, - If there are known reasons that the contingency is unsolved, notify the Shift Engineer to verify system conditions have not changed. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A Quick Start Resource is needed and not given SCED base points; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running), - Notify QSE as time permits. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| ### Transmission Issues in the Areas of the CFE DC-Ties |  |  |
| 1 | IF: - Contingencies or unsolved contingencies cannot be corrected with congestion management techniques; THEN: - Determine if there are schedules over the CFE Ties that would help the situation. |  |
| 2 | IF: - DC-Tie schedules can be curtailed to alleviate the transmission issue; THEN: - Notify the DC Tie Operator to curtail the schedule(s), - Issue a Transmission Watch (if giving advance notice) or Emergency (if advance notice cannot be given), - Make Hotline call, - Make notification on MIS Public using Notice Builder - Notify Real-Time Desk to make Hotline call to QSEs. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Transmission [Watch or Emergency] due to a post contingency loss of (name of contingency) overloads (name of overloaded element).” [TO] please repeat this back to me. That is correct, thank you.” Edit script as needed to fit situation. |  |
| ### Managing Binding and Exceeded Constraints |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| 1 | IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk and control room staff, - Determine the need for resolving the constraint by overriding LDL (hold up) and/or HDL (hold down) - DO NOT override while SCED is running, - Notify QSE as time permits. |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, maximum shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for exceeded constraints). |  |
| 2 | IF: - The transmission element flows are greater than the limit (exceeded); THEN: - Verify that the SCED executions are reducing the flows on the subject constraints, - Investigate units with large shift factors that are not being moved or are not following base points, - Create a “Suggestion Plan” for the constraint, - Instruct Shift Engineer to consult with the appropriate TO(s) to determine if there is a network re-configuration or post-contingency switching action that could be used to resolve the exceedance. |  |
| - Log | Log all action taken. |  |
| ### Reaching Shadow Price Cap |  |  |
| NOTE | Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary Review the DSP Constraint Summary display, a constraint has reached its max shadow price cap when the Flow (MW) is higher than Limit (MW). |  |
| 1 | Steps that may be taken to resolve congestion when a transmission constraint is exceeded in SCED after the Shadow Price reaches price cap include: - Verify base points are being followed, - Redistribute A/S to increase the capacity available to SCED, - Instruct QSE to remove the appropriate A/S and to update telemetry, - Notify Resource Operator with undeliverable A/S type, amount and hours from the Resource(s), - Removing a unit from ONTEST, - Commit/decommit additional units, - Formulate a mitigation plan which may include - Transmission reconfiguration (switching) - Load rollover to adjacent feeders - Load shed plans, - Re-dispatch generation through overriding HDL/LDL - DO NOT override while SCED is running - Notify QSE (this could exceed ramp rate), - Relax constraint until other actions can be taken. |  |
| ### QSE Requests to Decommit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure, - It may be necessary to manage transmission congestion manually by overriding HDL/LDL if a large exceedance has occurred - DO NOT override while SCED is running, - Notify QSE as time permits. |  |
| 2 | Trouble Shooting: IF: - Transmission constraints are active, THEN: - Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |  |

## 4.2	Potential IROL’s

Procedure Purpose: To identify potential IROLs.

| Protocol Reference | 6.5.7.1.10 (3) | 6.5.9(1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R3.2, R4.2 | FAC-011-2 R1, R3 | IRO-002-1 R6, R8 | IRO-003-2 R1 |
|  | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R9, R16, R17 | TOP-002-2 R10 | TOP-004-2 R1, R6, R6.6 | TOP-008-1 R1 |

| Version: 1 | Revision: 2 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | IF SE results indicate and/or RTCA predicts any of the below conditions on the 138kV or 345kV system and no SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP exists; notify Operations Support Engineers: - Post contingent rating exceedance in excess of 125% of the SOL of the monitored facility (2-hour or Emergency Rating) - Basecase exceedance exist in the State Estimator greater than 100% of the SOL of the monitored facility (Continuous or Normal Rating) - An unsolved or divergent contingency is present - Under-voltage condition characterized by bus voltages of less than 90% across three or more related BES facilities - Over-voltage condition greater than 110% across three or more BES facilities |
| 1 | IF: - SCED is unable to resolve congestion and leading into an insecure state; THEN: - Confirm that pre-determined relevant RAPs are properly modeled in the system, - Override HDL/LDL making every effort not to surpass the HASL/LASL on the associated facility or facilities - DO NOT override while SCED is running, - Notify QSE as time permits, - Deactivate non-cascading contingency overload/constraints in TCM on the CAM display to remove from the SCED process, - Notify Resource Desk Operator if this caused “undeliverable” or “stranded” Ancillary Services, - Contact Shift Engineer to develop a Mitigation Plan, and - If all other mechanisms have failed, continue to step 2. |
| 2 | IF: - Still heading into an insecure state; THEN: - Override HDL/LDL regardless of the HASL/LASL - DO NOT override while SCED is running, - Notify QSE as time permits, - Use Non-Spin Resources if available to resolve congestion, - Notify Resource Desk Operator if action caused “undeliverable” or “stranded” Ancillary Services if necessary, - Declare a Transmission Watch until Mitigation Plan is received, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |
| 3 | If Operations Support Engineer determines this to be an IROL after conducting offline studies. They will provide an IROL Tv (minutes). |
| 4 | Facility Rating violations must be relieved within the IROL Tv (minutes). |
| 5 | Make log entry: - Facility Rating violation being treated as potential IROL, - All actions implemented |

## 4.3	West-North Stability Limit

Procedure Purpose: Maintain Transmission stability between the West and North.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Refernce |  |  |  |  |
| NERC Standard | EOP-001 R4.2 | IRO-002 R6, R8 | IRO-003 R1 | IRO-004 R3 |
|  | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 | TOP-004 R1, R2, R6, R6.6 |
|  | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |  |

| Version: 1 | Revision: 2 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North stability limit is an IROL; The actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | IF: - The West-North stability limit calculated on the spreadsheet changes value or color; THEN: - Verify the value is accurate and update limit on RTMONI to give transparency to Market Participants, - Monitor as needed to the value shown on the spreadsheet. |
| NOTE | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change. It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| 2 | IF: - The monitored flow on the Stability-WN monitor is approaching 90% and wind generation is climbing; THEN: - Activate the appropriate constraint and manually execute RTCA and then SCED, - Post message on MIS Public using Notice Builder - Notify Real-Time Operator to make phone calls to any WGR not following their base points. Typical Message Script: “ERCOT is constraining for the West-North stability limit.” |
| 3 | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - Congestion management techniques fail to control the flow within 15 minutes; THEN: - Manually dispatch Wind Generation Resources down by overriding HDL (DO NOT override while SCED is running), - Notify QSE as time permits, - Notify the control room staff. |
| Log | Log all actions taken. |

## 5.1	Outages

Procedure Purpose:  Monitor and Respond to various types of equipment outages, both Transmission and Generation, in order to maintain reliability of the ERCOT Grid.

| Protocol Reference | 3.1.1 | 3.10.7.5.1 (3) | 3.1.5.1(2) | 3.1.1(2) |
| --- | --- | --- | --- | --- |
|  | 3.1.4.5(2) | 3.1.4.5(1) | 3.1.4.6(2) | 3.1.4.7(2) |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-003 R1, R4 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT Operators can only make the following changes in the Outage Scheduler: - Remove actual start/end time if it is within 2 hours of the time the MP entered the outage, - Change status, - Add notes If a MP needs assistance or is unable to enter their outages, direct them to Outage Coordination. Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes. |
| NOTE | Forced Outages should be verbally communicated to ERCOT and must be entered into the Outage Scheduler if it is to remain an Outage for longer than two hours. |
| 1 | IF: - An Emergency Condition is declared; THEN: - Determine if Outages can be returned to service if causing negative impacts to reliability, - Make a Hotline call and post Emergency Notice message on MIS Public using Notice Builder. |
| ### Monitor Mode |  |
| 1 | IF: - Any outages, either planned or forced, that may require additional monitoring; THEN: - Mark the outages in the Outage Scheduler OS Monitored Outage display as deemed necessary, - Verify that the marked outages are in monitor mode, - Continue to monitor the marked outages. |
| ### Forced and Unavoidable Extensions |  |
| 1 | IF: - A Forced or Unavoidable Extension is received, review the outage details; THEN: - Monitor congestion and make appropriate changes as necessary, - Determine if it will have an effect on previously approved outages which may be to withdrawn. |
| ### Remedial Switching Action |  |
| Definition | “Remedial Switching Action” is a Forced Outage sub-type in the Outage Scheduler. ERCOT must approve all Remedial Switching Actions prior to implementation by TSPs and post such outages to the MIS Secure Area. |
| < 3 Days in length | Remedial Switching Actions are limited to a maximum of 3 days. |
| > 3 Days in length | If the Remedial Switching Action is required to remain active for longer than 3 days, a Planned Outage must be submitted to change the position of effected breakers and switches. |
| Approve | IF: - No issues identified; THEN: - Approve the Outage as received. |
| Reject | IF: - Reliability issues; THEN: - Notify Shift Engineer; - Reject the outage to ensure system reliability. |
| Restoration | Breakers and switches in a Remedial Switching Action must be able to be returned to their normal position within 4 hours or less (this allows for drive time for remote switches w/o SCADA). |
| Log | Log all appropriate information. |
| ### Maintenance Outages |  |
| Definition | When a Maintenance Outage is received, the Outage Scheduler will determine the correct Level the outage falls into: - Level 1- Equipment that must be removed from service within 24 hours to prevent a potential Forced Outage; - Level 2 - Equipment that must be removed from service within seven days to prevent a potential Forced Outage; and - Level 3 - Equipment that must be removed from service within 30 days to prevent a potential Forced Outage. |
| Verify Level 1 | IF: - A Maintenance Level 1 Outage is received, review the outage; THEN: - Run a study to determine if the outage will cause any reliability issues. |
| Approve Level 1 | IF: - No issues identified; THEN: - Accept the Outage as received. |
| Deny Level 1 | IF: - Reliability issues; THEN: - Coordinate the start of the outage with the TO to ensure system reliability as long as the outage is allowed to start within 24 hours. |
| Maintenance Level 2 and 3 Outages | IF: - Maintenance Level 2 and 3 outages are received; THEN: - DO NOT check the “Accept” box, - Place the outage in “Study” status, AND - Notify the Outage Coordination group by e-mail (“OPS Outage Coordination” distribution list). |
| Log | Log all appropriate information. |
| ### Consequential Outages |  |
| 1 | WHEN: - A TO enters the breaker and switch statuses associated with an Electrical Bus; THEN: - A downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus. |
| Evaluate | IF: - The TO has submitted the outage in the Outage Scheduler; THEN: - As time permits, perform a study to determine the effects the outage has on the ERCOT system and evaluate the request and verify the Outage meets the applicable requirements. |
| No Violations | IF: - NO, violations of applicable reliability standards exist; THEN: - Approve the request in the Outage Scheduler. |
| Yes Violations | IF: - YES, violations of applicable reliability standards exist; THEN: - Reject the request in the Outage Scheduler. |
| Log | Log all action taken. |
| ### Returning from Planned Outage Early |  |
| 1 | IF: - Notified by a TO or Resource Desk Operator that an outage is returning early from a Planned Outage; THEN: - Monitor congestion and make appropriate changes as necessary. |
| ### Guidelines for Withdrawal of an Outage |  |
| 1 | IF: - Security analysis and/or Operator experience indicates that an “Approved” or “Active” outage may have an adverse impact on system reliability; THEN: - Review the restoration time of the outage and if necessary, - ERCOT may withdraw the outage. |
| 2 | WHEN: - ERCOT withdraws an outage via the Outage Scheduler; THEN: - Enter an explanation in the “Reviewers Notes” listing the reliability concerns that caused the withdrawal, - Notify the following, by e-mail, as soon as possible: - OPS Outage Coordination - OPS Support Engineering - 1 ERCOT Shift Supervisors - Include the following information: - From Station – To Station (if applicable) - The planned Start and End date of the outage. |
| 3 | IF: - A TO or QSE reports that the outage in question has progressed to a point that withdrawal is not practicable within the outages designated restoration time; THEN: - Record this information in the “Outage Scheduler Reviewer’s Notes”, - Log the outage in the Transmission Security Log, - Inform the Shift Supervisor, - Continue monitoring system security, - Request Shift Engineers to develop Mitigation plan if necessary. |
| ### Approval of an Outage on Transmission Devices of More than one hour duration |  |
| 1 | IF: - A verbal request for permission to remove a transmission device from service for more than one hour is received; THEN: - Verify with the TO that the work being done will not prevent the device from being placed back in service immediately if needed, - As time permits, determine that such operation will not affect the reliability of the Transmission System, - If outage will cause reliability issues, go to Step 2 - If no impact to the system, go to 3. |
| 2 | IF: - System reliability is impacted; THEN: - Discuss with the TO the possibility of postponing the outage to a later time OR deny the request. |
| 3 | IF: - There is no reliability issue; THEN: - Verbally approve for the TO to remove a transmission device from service. - Instruct TO to make notification when device is place back in service. |
| Log | Log all appropriate information. |
| ### Simple Transmission Outage |  |
| NOTE | A Simple Transmission Outage is a classification of outage that can be removed from service without effecting LMP prices or causing congestion. The Outages are limited to the following 3 basic descriptions: - Expanded Bus Outage - Generator Breaker Maintenance - Open-ended Lines Refer to Section 3.2 of the Desktop Reference Guide. |
| 1 | IF: - The outage meets the requirements of a Simple Transmission Outage, - Has been submitted between 1 and 2 days in advance, - Has a duration of the outage of 12 hours, AND - Has a less restoration time of 1 hour or less; THEN: - ERCOT will approve or reject within 8 business hours after receipt. |
| ### Opportunity Outages |  |
| Definition | An Outage that may be accepted by ERCOT when a specific Resource is Off-Line due to an Outage. |
| 1 | WHEN: - An Outage is submitted on a Resource that has an approved Transmission Facilities Opportunity Outage request on file; THEN: - A pop up will appear when the Resource outage is entered into the Outage Scheduler. These outages are retained for up to 90 days in the Outage Scheduler. |
| Determine | If Reliability issues are identified |
| 2 | IF: - Reliability issues exist; THEN: - Coordinate the start of the outage with the TO to ensure system reliability. |
| 3 | IF: - No issues identified; THEN: - Accept the Outage as received, - ERCOT must give as much notice as practicable to the TO, - The TO may start the approved Outage as soon as practical after receiving authorization to proceed by ERCOT. |