## Power Operations Bulletin # 514

ERCOT has posted/revised the NODAL Real Time Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.3.2(2) | 6.5.7.6.2.2 | 6.5.9.1(1)(b) | 8.2 (2)(b)(vii) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6, R7, R8 | BAL-005-0.b R8 | BAL-007 (Field Trial) | EOP-002-2.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 5, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 587 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -587 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, - Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) |
| Base Point Deviation | IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations > +/- 0.10 Hz | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz; THEN: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) - If unit trip, name of unit that tripped - Approximate MW on the unit when trip occurred - Actual Frequency and amount of RRS deployed - Approximate ERCOT load. |
| ### Response to High Frequency |  |
| BAAL Sheet | Open realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| Monitor | IF: - Frequency is above 60.05 Hz and continuing to climb or exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - CHECK if “Generation To Be Dispatched” (GTBD) is adequate to serve the predicted load, - Manually run SCED. |
| 10 MINUTES | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points (GEN-LDL), - Enter operator manual offset into “DSI Generation Requirement Manual Adjustment” to lower generation (the operator manual offset will continue to be deployed until removed), - Manually run SCED. |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points (GEN-LDL), - Re-adjust “DSI Generation Requirement Manual Adjustment” if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED, - Log the event and notify Shift Engineer to send an event notification to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| Stable | IF: - An operator manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Open realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously to start spreadsheet. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.90 Hz - Load Resource providing RRS – 59.7 Hz |
| Monitor/ Deploy | IF: - Frequency is below 59.95 Hz and continuing to drop or is below 59.95 > 5 minutes, AND - Regulation Up service remains and is deploying; THEN: - CHECK if “Generation To Be Dispatched” (GTBD) is adequate to serve the predicted load, - Manually run SCED. IF: - Out of Up Regulation; THEN: - Select the Activate Manual Responsive Reserve, - Enter the Manual RRS Desired MW level, - Select Commit. |
| 10 Minutes | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter operator manual offset into “DSI Generation Requirement Manual Adjustment” to increase generation (the operator manual offset will continue to be deployed until removed), - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Notify the Shift Supervisor of the need to possibly commit additional Resources: - Resource Operator will issue a VDI for intra-hour - Notify RUC Operator for the next HRUC run. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust “DSI Generation Requirement Manual Adjustment” if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED, - Log the event and notify Shift Engineer to send notification of the event to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust DSI Generation Requirement Manual Adjustment if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points, - Re-adjusted “DSI Generation Requirement Manual Adjustment” if necessary (the operator manual offset will continue to be deployed until removed), - Manually run SCED. |
| Stable | IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An operator manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Austin) |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source - Contact the Help Desk, - Notify the other Control Room Operators that SCED results could be skewed due to incorrect Frequency telemetry. |

## 3.2	Automatic Generation Control (AGC) Failure

Procedure Purpose:  To ensure that frequency is maintained in the event of an AGC failure.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 5, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Failure Indication/ Issues | IF: - The EMS frequency control is not functioning as indicated by: - AGC is SUSPENDED or PAUSED OR - “Last AGC Cycle” time on Generation Area Status display is not updating OR - AGC operation adversely impacts the reliability of the Interconnection, OR - SCED and EMS are not functioning, AND - The problem cannot be resolved quickly; THEN: - Verify the status of RLC - If RLC is also failed, proceed using the AGC and RLC Failure procedure. - If RLC is still functioning properly, continue - Determine which QSE has ample Capacity to place on Constant Frequency Control. (REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data), - Direct that QSE to go on “Constant Frequency”, by issuing an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into ‘Monitor” mode, - Using the Hotline, notify all QSEs that ERCOT is having AGC issues and has placed a QSE on constant frequency, Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to AGC issues and has placed a QSE on Constant Frequency. All remaining Resources should continue to follow their SCED Base Points. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” - Notify the Transmission Operator to make the same Hotline call to the TOs, - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| QSE Control Issues | IF: - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Coordinate with another QSE that has ample Capacity and place them on Constant Frequency Control. (Remember to take the first QSE off Constant Frequency). |
| QSE Capacity Issues | IF: - The QSE on Constant Frequency notifies ERCOT of Capacity issue; THEN: - Determine available Capacity for SCED and enter an operator manual offset OR - Issue electronic VDI(s) as needed, to Commit/Decommit additional generation to maintain Grid Reliability. - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level |
| AGC Issues Resolved | WHEN: - ERCOT AGC Control is functioning properly; THEN: - Direct QSE to come off “Constant Frequency” by ending the electronic VDI, - Place ERCOT AGC back into “ON” mode, - Using the Hotline, notify all QSEs, - Instruct the Resource Operator to cancel message on MIS utilizing Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Emergency Notice due to AGC issues and has returned to normal operations. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings.” - Notify the Transmission Operator to make the same Hotline call to the TOs, - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| Log | Log all actions taken. |

## 3.3	Resource Limit Calculator (RLC) Failure

Procedure Purpose:  To ensure that frequency is maintained in the event of a RLC failure.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Failure Indication | The Resource Limit Calculator (RLC) can fail independently of AGC. If RLC fails, no SCED Base Points will be dispatched to the market. A RLC failure will be displayed to the Operator in the upper right corner of the RLC display as follows: - Process Status: RLC Up (Normal Operation) - Process Status: RLC Down (will be displayed in RED when failed) - RLC (PI Alarm) will be flashing RED. |
| NOTE | Once RLC is down, SCED is not functioning properly even though SCED is still available; the results are not valid as the input from RLC is not valid. |
| RLC Issues | IF: - RLC has failed; THEN: - Verify the status of AGC - IF AGC is also failed proceed using the AGC and RLC Failure procedure. - IF AGC is still functioning properly, continue |
| Hotline | Issue the following Market Notice: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to a SCED failure. ERCOT will activate Emergency Basepoints as needed. [QSE] please repeat this back to me. That is correct, thank you.” - Notify the Transmission Operator to issue their Hotline notification - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| EBP Deployments | MONITOR: - Regulation Service (Up/Dn) margins to ensure Frequency can be adequately maintained, AND - Capacity margins for each QSE. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Manual activate Emergency BP, - Enter the EBP increment/decrement as needed to control Frequency and recall deployed Regulation. |
| RLC Issues Resolved | WHEN: - RLC is restored; THEN: - Cancel the Emergency Notice. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is cancelling the Emergency Notice. All QSE please follow SCED Base Points. [QSE] please repeat this back to me. That is correct, thank you.” - Notify the Transmission Operator to issue their Hotline notification - Instruct the Resource Operator to cancel the message on MIS utilizing Notice Builder. |
| Log | Log all actions taken. |

## 3.4	AGC and RLC Failure

Procedure Purpose:  To ensure that Frequency is maintained in the event that AGC and RLC fail simultaneously.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Failure Indications | AGC: - AGC is SUSPENDED or PAUSED, - “Last ACE crossing zero” time on the Generation Area Status page is not updating, - AGC operation adversely impacts the reliability of the Interconnection, - SCED and EMS are not functioning, - Problem cannot be resolved quickly RLC: - Process Status: RLC Down will be displayed in RED in the upper right hand corner of the RLC display - RLC (PI Alarm) will be flashing RED. |
| AGC/RLC Issues | IF: - AGC and RLC fail simultaneously; THEN: - Determine which QSE has ample Capacity to place on Constant Frequency Control (REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data), - Direct the selected QSE to go on “Constant Frequency” by issuing an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into “Monitor” mode, - Using the Hotline, notify all QSEs Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to an issue with AGC and SCED. ERCOT has placed a QSE on Constant Frequency. Please hold your current output until instructed by ERCOT. ERCOT will be issuing unit specific deployments to individual QSEs as needed to maintain Frequency. [QSE] please repeat this back to me. That is correct, thank you.” - Notify the Transmission Operator to issue their Hotline notification - Instruct the Resource Operator to post a message on MIS utilizing Notice Builder. |
| QSE Control Issues | IF: - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Determine which QSE has the most available Capacity, - Issue a unit specific instructions to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |
| System Wide Capacity Issue | IF: - There is no longer any available Capacity to issue unit specific deployments; THEN: - Issue electronic VDI(s) as needed, to Commit/Decommit additional Generation to maintain Grid Reliability - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level. |
| AGC/RLC Issues Resolved | WHEN: - AGC and RLC is restored; THEN: - Direct QSE to come off ‘constant frequency’ by ending electronic VDI, - Place ERCOT AGC back into “ON” mode, - Cancel VDI(s) for additional generation, if issued - Remove the Emergency Base Point flag, - Using the Hotline, notify all QSEs Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is cancelling the Emergency Notice. All QSE’s please follow SCED Base Points. [QSE] please repeat this back to me. That is correct, thank you.” - Notify Transmission Operator to issue their Hotline notification - Instruct the Resource Operator to cancel message on MIS utilizing Notice Builder. |
| Log | Log all actions taken. |

## 4.1	Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved and that the solution is reasonable.

| Protocol Reference | 3.8.3 | 6.3.2(2) | 6.5.7.1.13(3) | 6.5.7.6.2.1(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.7.6.2.2 | 6.5.7.6.2.1(1) | 6.5.7.6.2.1(4) | 6.5.1.1(b) |
|  | 6.5.5.2(6) | 6.5.7.6.2.3 | 6.5.9.1(2) |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Workflow Controller Messages |  |
| NOTE | The SCED Workflow Controller provides three color coded messages as indicated in the following: - GREEN – Informational (i) and Success (s) - BLUE – Warning (w) - RED – Error (e) and Fatal Error (f) |
| 1 | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages Monitor SCED Workflow Controller logs for “Warning” and “Error” messages. |
| 2 | IF: - The log indicates an “Error” or “Fatal Error”; THEN: - Contact the Help Desk and notify all Control Room staff, - Attempt to resolve the issue following, refer to Section 5.5 of the Desktop Guide, - Refer to Section 4.2 “Managing SCED Failures” in this procedure. |
| ### SCED Solution Time Parameter |  |
| NOTE | Typically SCED should produce a solution within 20 seconds. It is highly desirable to have at least 3 executions of SCED in any 15 minute period. |
| Automatic Trigger | Verify that SCED is automatically triggered: - Periodically every 5 minutes - About 60 seconds after RRS is automatically deployed by LFC IF: - SCED is not automatically executed (but has not failed); THEN: - Manually execute SCED, - Immediately notify the Shift Supervisor and Shift Engineer, - Continue to manually execute SCED approximately every 5 minutes until the condition is corrected. |
| Manual Trigger | SCED may be manually triggered when the following is identified: - Frequency deviates +/-0.05 Hz for more than 5 minutes - Generation Resource trips and Frequency is > 59.91 Hz - When approximately 50% of Regulation has been deployed - Approximately 60 seconds after Generation Resources providing RRS have been deployed. - As frequently as needed after Load Resources providing RRS have been deployed. |
| LOG | Log all actions taken as necessary. |
| ### Exceeding West – North Stability Limit |  |
| 1 | IF: - Notified by the Transmission Operator that the West – North has exceeded the limit for 5 minutes; THEN: - Issue Hotline call to QSEs: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. The West to North flow is exceeding the stability limit, ERCOT is directing all QSEs representing Wind Generation Resources in the West to not exceed your base points. While the West to North is active, QSEs are to ensure HSLs represent WGR’s power potential. This directive is in effect until ERCOT de-activates the West to North constraint. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log all actions taken as necessary. |
| ### Large Resource Trips or Runbacks |  |
| 1 | IF: - A QSE has the loss of any Resource greater than 200 MW; THEN: - Review the following: - Ensure their telemetry reflects the trip, - Manually deploy SCED if needed, - Determine the impact on (HASL-GEN), AND - If Non-Spin is needed, ask the Resource Operator to deploy it. - Notify Control Room staff of all actions taken - Log the event. |
| ### Quick Start Generation Resource |  |
| QSGR | A Generation Resource that while in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test which establishes the amount of capacity that can be deployed within a ten minute period. |
| COP | The QSE for a QSGR that is available for deployment by SCED shall set the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spin service, then the A/S Resource Responsibility for Non-Spin shall be set to the Resource’s Non-Spin obligation in the COP. If the Resource’s Non-Spin obligation is less than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP Resource Status to ON, otherwise it shall be set to OFFNS. |
| Telemeter | The QSGR shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED. |
| SCED | If a QSGR comes On-Line as a result of a Base Point less than its COP LSL, the QSE representing the QSGR may request a manual override from the ERCOT Operator within the first ten minutes after the SCED time stamp, and the ERCOT Operator shall set the LDL to a level greater than or equal to the COP LSL. |
| Log | Log all actions taken as necessary. |
| ### Generation Resource Shut-down/Start-up Process |  |
| NOTE | ERCOT’s preferred methodology for moving a generator output down to a state suitable for de-synchronization: - All A/S Responsibility assigned to the Resource must first be moved to other Generation Resources, - Generation Resources are expected to be on normal SCED control until reaching no greater than 110% of the units normal LSL before changing status to “ONTEST”. This can be accomplished by the QSE doing one of the following: - Allow SCED to move the unit down to LSL by normal dispatch; - The QSE may telemeter the unit’s HSL=LSL in order for SCED to move the unit to LSL at normal ramp rate; then when at or below 110% of LSL, the QSE changes the unit status to “ONTEST” for shut-down. |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to their telemetry (Resource status, Resource limits, A/S responsibilities, etc) |
| Market Participant Over-ride | IF: - Market Participant cannot fix the issue in a timely manner; THEN: - Ask the Market Participant to over-ride the bad telemetry. |
| Market Participant unable to Override | IF: - For some reason, the Market Participant cannot over-ride the bad telemetry; THEN - Request the Shift Engineer to over-ride the bad telemetry, - Manually run SCED, if needed. |

## 5.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Projected Reserve Capacity Shortage that could affect System Reliability and may require more Resources. - There is a Tropical Storm/Hurricane in the Gulf, entering the Gulf or a newly formed Storm projected to impact Texas. - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and the maximum temperature is expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Wet weather, such as a Tropical Storm making land fall. - Unplanned Transmission Outages that may impact System Reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse Reliability impacts and Contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Tropical Storm/Hurricane currently projected to impact Texas. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term Operating Reliability. - In such circumstances ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market (DAM) in accordance with ERCOT Procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission System conditions are such that operations within first contingency criteria are not likely or possible due to Forced Outages or other conditions. - Loss of communications or a control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from the Market Participants. - There is a Hurricane in the Gulf with expected landfall in Texas affecting the Grid Reliability - http://www.nhc.noaa.gov - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and the maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - A Transmission condition has been identified that requires Emergency Energy from any of the CFE DC-Ties - Conditions have developed that require additional Ancillary Services in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based Congestion Management techniques embedded in SCED will not be adequate to resolve Transmission Violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require Operations with active Transmission Violations - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the Reliability of the ERCOT System - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum Reliability Standards during the Operating Period utilizing every Resource practically obtainable from the Market - ERCOT forecasts an inability to meet applicable Reliability Standards and has exercised all other reasonable options - A Transmission condition has been identified causing unreliable Operation or overloaded elements - A Single Severe Contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements for which no practicable Resource solution exists - ERCOT has determined a fuel shortage exists that would affect Reliability - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time deadlines - DRUC failure - HRUC failure - SASM failure - SCED failure |
| ### Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify QSEs: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public utilizing Notice Builder. - For “free form” messages, the only option is “Public” - For “free form” messages, the “Notice Priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Log all actions taken. |

## 5.4	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - Physical Responsive Capability supplied from generation is greater than 1354 MW; THEN: - Using the Hotline, notify all QSEs of firm load restoration. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], ERCOT is currently restoring firm load. [QSE] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Maintain Physical Responsive Capability supplied from generation equal to 1354 MW while restoring firm load. |
| ### Move From EEA Level 3 to EEA Level 2B |  |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - Physical Responsive Capability supplied from generation is equal to 1354 MW, AND - All firm load has been restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 3 to EEA 2B: - Coordinate with the Resource Desk and begin recalling Load Resources (if restoring Load Resources and EILS together, see script in 2a) (PRC must be ≥ 2300 before EILS can be restored). - Maintain a minimum of 1354 MW of Physical Responsive Capability supplied from Generation Resources while Load Resources are being recalled. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is moving from EEA 3 to EEA 2B. QSEs are to recall their Load Resources at this time. [QSE] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move From EEA Level 2B to EEA Level 2A |  |
| 1 | IF: - The System can maintain Physical Responsive Capability equal to or greater than 1750 MW, AND - All Load Resources have been instructed to be recalled, AND - Sufficient Regulation Service exists to control to 60 Hz. THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 2B to EEA 2A. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is moving from EEA 2B to EEA 2A. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Appeals through the public news media for voluntary energy conservation may be terminated, after conferring with the Shift Supervisor |
| 3 | Verify and log that all measures have been implemented. |
| ### Move From EEA Level 2A to EEA Level 1 |  |
| 1 | IF: - The System can maintain Physical Responsive Capability equal to or greater than 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Using the hotline, notify all QSEs to recall EILS. Typical script for recalling Load Resources and EILS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is moving from EEA 2B to EEA 1. QSEs are to recall their Load Resources and EILS at this time. [QSE] please repeat this back to me. That is correct, thank you.” OR Typical script for recalling EILS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is moving from EEA 2A to EEA 1. QSE are to recall their EILS at this time. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. - Using the Hotline, notify all QSEs of the reduction from EEA 2A to EEA 1. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is moving from EEA 2A to EEA 1. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Move From EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain Physical Responsive Capability equal to or greater than 2300 MW, AND - All Load Resources and EILS have been instructed to be restored, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency power from the DC Ties is no longer needed; THEN: - Uncheck the EEA flag in EMS and make inactive, - Using the hotline, notify all QSEs of the reduction from EEA 1 to EEA 0. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is terminating the EEA. A Watch still remains in effect. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Cancel Watch |  |
| 1 | WHEN: - Physical Responsive Capability is equal to or greater than 3000 MW, AND - Non-Spin has been recalled; THEN: - Cancel Watch Typical script: “This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for Physical Responsive Capability. Physical Responsive Capability is now above 2500 MW. At this time, Resource testing may resume. [QSE] please repeat this back to me. That is correct, thank you.” |