## Power Operations Bulletin # 515

ERCOT has posted/revised the NODAL Trasmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006 R1, R4 |
|  | IRO-002 R6, R8 | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |

| Version: 1 | Revision: 3 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |
| CAUTION | IF: At any time, the prescribed measures within this procedure fail to resolve the congestion, AND The transmission system is beyond “First Contingency Criteria”; THEN: Issue a Watch, Make a Hotline call and post Watch message on MIS Public using Notice Builder. |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. Error! Hyperlink reference not valid.A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| NOTE | Congestion Management Techniques consist of: SCED Phase Shifters Remedial Action Plan (RAP) Pre-Contingency Action Plan (PCAP) Mitigation Plan (MP) – enacted Post-Contingency Temporary Outage Action Plans (TOAP) located in the Outage Notes Unit specific dispatch instructions (Manual Dispatch or VDI) If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at P:\System Operation\Remedial Action Plans, A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, TOAPs are usually located in the daily Outage Notes. |
| Phase Shifters | Phase shifters can be used to help with congesting management: Putnam – NW/WN transfers to increase transfer capability Yellow Jacket – mitigate local congestion and increase W/N transfers Big Lake – mitigate local congestion and increase W/N transfers Firerock ETT – mitigate local congestion and increase W/N transfers Nelson Sharp – valley import during outages Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages North Laredo – control Laredo import issues during outages |
| Evaluate Real Time Contingency Analysis (RTCA) Results |
| 1 | IF: SE and/or RTCA is not solving; THEN: Notify Shift Engineer, IF: SE and/or RTCA has not solved for 15 minutes, THEN: Refer to section 3.3 “Analysis Tool Outages” in this procedure. |
| 2 | IF: RTCA has run within 10 minutes; THEN: Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |
| 3 | IF: A major change of Resource or Transmission Element Status; THEN: Re-start RTCA and VSAT. |
| Post-Contingency Overloads |
| 1 | IF: Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: Determine if the SCADA is of similar magnitude to the Pre-contingency value. Example: Review the MW and MVAR flows |
| 2 | IF: Inaccurate; THEN: DO NOT employ congestion management techniques, Notify the Shift Supervisor and Shift Engineer. |
| 3 | IF: Accurate; THEN: Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP, Refer to “Managing Binding and Exceeded Constraints” of this Procedure. |
| 4 | IF: Post-contingency overloads greater than 100% exist without an SPS (identified as RAS in EMS), RAP, PCAP, or TOAP in place to relieve; THEN: Activate constraints as necessary, Lower the value in the % Rating column in RTCAM to tighten the constraint (minimum of 95%), Increase the value in the % Rating column in RTCAM to loosen the constraint (maximum of 105%), Manually execute the SCED process, Refer to “Managing Binding and Exceeded Constraints”. |
| 5 | IF: There is an imminent threat to the reliability of the ERCOT system, caused by a Qualifying Facility (QF), and ERCOT decides to order the QF offline or to operate below its LSL; THEN: Issue VDI to the appropriate QSE(s), Choose “DECOMMIT/ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level Issue an Emergency Notification via Hotline call to TOs, Instruct the Real-Time Operator to make Hotline call to QSEs, Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to an immediate threat to the reliability of the ERCOT system that required directing a Qualifying Facility [offline/operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |
| 6 | IF: Post-contingency overloads greater than 100% of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: Constraint needs to be controlled within the next 5 minutes; THEN: Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, Manually execute the SCED process, Refer to “Managing Binding and Exceeded Constraints”. |
| 7 | IF: Any RTCA results predict a Facility Rating will exceed post-contingency loading of 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL; THEN: Refer to section 4.2 “Potential IROL’s”. |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: A valid Thermal overload exists in Real-Time; THEN: Activate constraints as necessary, Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, Manually execute the SCED process, Refer to “Managing Binding and Exceeded Constraints”, Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |
| 9 | Periodically check the “Contingency Solution Results” display: IF: Unsolved contingencies exist; THEN: Run the State Estimator again, If unsolved contingencies remain, notify the Shift Engineer, If there are known reasons that the contingency is unsolved, notify the Shift Engineer to verify system conditions have not changed. |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: For Dispatch Instructions that are a part of the testing; or During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or During Force Majeure Events that threaten the reliability of the ERCOT System. |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: A Quick Start Resource is needed and not given SCED base points; THEN: Override LDL to a level greater than or equal to the COP LSL DO NOT override while SCED is running), Notify QSE as time permits. |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR A Resource is generating more than their telemetered HSL; THEN: SCED will set the HDL=LDL=MW making the Resource undispatchable, Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) Disregard WGRs unless transmission constraint is active. |
| Transmission Issues in the Areas of the CFE DC-Ties |
| 1 | IF: Contingencies or unsolved contingencies cannot be corrected with congestion management techniques; THEN: Determine if there are schedules over the CFE Ties that would help the situation. |
| 2 | IF: DC-Tie schedules can be curtailed to alleviate the transmission issue; THEN: Notify the DC Tie Operator to curtail the schedule(s), Issue a Transmission Watch (if giving advance notice) or Emergency (if advance notice cannot be given), Make Hotline call, Make notification on MIS Public using Notice Builder Notify Real-Time Desk to make Hotline call to QSEs. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a Transmission [Watch or Emergency] due to a post contingency loss of (name of contingency) overloads (name of overloaded element).” [TO] please repeat this back to me. That is correct, thank you.” Edit script as needed to fit situation. |
| Managing Binding and Exceeded Constraints |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: EMS/TCM Constraint List, EMS/TCM Constraint: Generator Shift Factors |
| 1 | IF: No shift factors are passed for the constraint; THEN: Contact Help Desk and control room staff, Determine the need for resolving the constraint by overriding LDL (hold up) and/or HDL (hold down) DO NOT override while SCED is running, Notify QSE as time permits. |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, maximum shadow price, and current real-time flows on the following displays: DSP Constraint Summary, DSP Suggestion Plan (if need for exceeded constraints). |
| 2 | IF: The transmission element flows are greater than the limit (exceeded); THEN: Verify that the SCED executions are reducing the flows on the subject constraints, Investigate units with large shift factors that are not being moved or are not following base points, Create a “Suggestion Plan” for the constraint, Instruct Shift Engineer to consult with the appropriate TO(s) to determine if there is a network re-configuration or post-contingency switching action that could be used to resolve the exceedance. |
| Log | Log all action taken. |
| Reaching Shadow Price Cap |
| NOTE | Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary Review the DSP Constraint Summary display, a constraint has reached its max shadow price cap when the Flow (MW) is higher than Limit (MW). |
| 1 | Steps that may be taken to resolve congestion when a transmission constraint is exceeded in SCED after the Shadow Price reaches price cap include: Verify base points are being followed, Redistribute A/S to increase the capacity available to SCED, Instruct QSE to remove the appropriate A/S and to update telemetry, Notify Resource Operator with undeliverable A/S type, amount and hours from the Resource(s), Removing a unit from ONTEST, Commit/decommit additional units, Formulate a mitigation plan which may include Transmission reconfiguration (switching) Load rollover to adjacent feeders Load shed plans, Re-dispatch generation through overriding HDL/LDL only if there is not a market solution, DO NOT override while SCED is running Notify QSE (this could exceed ramp rate), Relax constraint until other actions can be taken. |
| QSE Requests to Decommit a Resource |
| 1 | IF: Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, Notify the RUC Operator with determination. |
| Managing Congestion during SCED Failure |
| 1 | IF: SCED fails; THEN: Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure, It may be necessary to manage transmission congestion manually by overriding HDL/LDL if a large exceedance has occurred DO NOT override while SCED is running, Notify QSE as time permits. |
| 2 | Trouble Shooting: IF: Transmission constraints are active, THEN: Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |

## 4.2	Potential IROL’s

Procedure Purpose: To identify potential IROLs.

| Protocol Reference | 6.5.7.1.10 (3) | 6.5.9(1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R3.2, R4.2 | FAC-011-2 R1, R3 | IRO-002-1 R6, R8 | IRO-003-2 R1 |
|  | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R9, R16, R17 | TOP-002-2 R10 | TOP-004-2 R1, R6, R6.6 | TOP-008-1 R1 |

| Version: 1 | Revision: 3 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | IF SE results indicate and/or RTCA predicts any of the below conditions on the 138kV or 345kV system and no SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP exists; notify Operations Support Engineers: Post contingent rating exceedance in excess of 125% of the SOL of the monitored facility (2-hour or Emergency Rating) Basecase exceedance exist in the State Estimator greater than 100% of the SOL of the monitored facility (Continuous or Normal Rating) An unsolved or divergent contingency is present Under-voltage condition characterized by bus voltages of less than 90% across three or more related BES facilities Over-voltage condition greater than 110% across three or more BES facilities |
| 1 | IF: SCED is unable to resolve congestion and leading into an insecure state; THEN: Confirm that pre-determined relevant RAPs are properly modeled in the system, Deactivate non-cascading contingency overload/constraints in TCM on the CAM display to remove from the SCED process, Notify Resource Desk Operator if this caused “undeliverable” or “stranded” Ancillary Services, Contact Shift Engineer to develop a Mitigation Plan, and If all other mechanisms have failed, continue to step 2. |
| 2 | IF: Still heading into an insecure state; THEN: Notify Resource Desk Operator if action caused “undeliverable” or “stranded” Ancillary Services if necessary, Declare a Transmission Watch until Mitigation Plan is received, Make a Hotline call and post Watch message on MIS Public using Notice Builder. |
| 3 | If Operations Support Engineer determines this to be an IROL after conducting offline studies. They will provide an IROL Tv (minutes). |
| 4 | Facility Rating violations must be relieved within the IROL Tv (minutes). |
| 5 | Make log entry: Facility Rating violation being treated as potential IROL, All actions implemented |

## 4.3	West-North Stability Limit

Procedure Purpose: Maintain Transmission stability between the West and North.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Refernce |  |  |  |  |
| NERC Standard | EOP-001 R4.2 | IRO-002 R6, R8 | IRO-003 R1 | IRO-004 R3 |
|  | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 | TOP-004 R1, R2, R6, R6.6 |
|  | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |  |

| Version: 1 | Revision: 3 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North stability limit is an IROL; The actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | IF: The West-North stability limit calculated on the spreadsheet changes value or color; THEN: Verify the value is accurate and update limit on RTMONI to give transparency to Market Participants, Monitor as needed to the value shown on the spreadsheet. |
| NOTE | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. To update the spreadsheet when any PSS is forced offline in the West zone. Open the Summary tab to verify units Enter 0 = PSS is offline, 1 = PSS online for each resource change. It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| 2 | IF: The monitored flow on the Stability-WN monitor is approaching 80%; THEN: Activate the appropriate constraint (ease up on constraint as situation allows), Post message on MIS Public using Notice Builder, Notify Real-Time Operator to make phone calls to any WGR not following their base points. Typical Message Script: “ERCOT is constraining for the West-North stability limit.” |
| 3 | IF: West – North exceeds 100%; THEN: Notify Real-Time desk to follow procedure and make Hotline call to all QSEs. |
| 4 | IF: Congestion management techniques fail to control the flow within 15 minutes; THEN: Notify QSEs with the largest WGR base point deviation and give directive to go to zero immediately, Issue electronic VDI as time permits, Notify the control room staff. |
| 5 | IF: Congestion management techniques fail to control the flow within 20 minutes; THEN: Issue directive to TO to open WGR breaker with the largest WGR base point deviation (refer to Real-Time spreadsheet tab “West Wind”), Issue electronic VDI as time permits, Notify the control room staff. |
| Log | Log all actions taken. |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: January 5, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OCN |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. There is a Tropical Storm/Hurricane in the Gulf. Either entering the Gulf or a newly formed storm projected to impact Texas according to the “National Hurricane Center” (http://www.nhc.noaa.gov). A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. Wet weather, such as a tropical storm making land fall. Unplanned Transmission Outages that may impact System reliability. When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| Advisory |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. There is a Tropical Storm/Hurricane in the Gulf. Currently projected to impact Texas according to the “National Hurricane Center” http://www.nhc.noaa.gov. When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. Loss of communications or control condition is anticipated or significantly limited. ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| Watch |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. There is a hurricane in the Gulf and an expected landfall in Texas affecting grid reliability - http://www.nhc.noaa.gov A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. Conditions have developed such that additional Ancillary Services are needed in the Operating Period Insufficient Ancillary Services or Energy Offers in the DAM or in SASM Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations The need to immediately procure Ancillary Services from existing offers ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| Emergency Notice |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. SCED fails to reach a solution Loss of Primary Control Center Functionality Load Resource deployment for North-Houston voltage stability ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. A transmission condition has been identified causing unreliable operation or overloaded elements. A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. ERCOT has determined a fuel shortage exists that would affect reliability. ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time deadlines. DRUC failure HRUC failure SASM failure SCED failure |
| Scripts |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | All notices must be posted on the MIS Public using Notice Builder. For “free form” messages, the only option is “public” For “free form” messages, the “Notice priority” will be specified as follows: OCN type messages – low priority Advisory/Watch type messages – medium priority Emergency type messages – high priority |
| Log | Make log entry. |