## Power Operations Bulletin # 520

ERCOT has posted/revised the NODAL Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Compliance Monitoring

Procedure Purpose: To monitor QSE performance

| Protocol Reference | 3.9.1(7) & (8) | 6.3.2(2) | 6.4.2.5 (2) | 6.4.2.5(3)(b) |
| --- | --- | --- | --- | --- |
|  | 6.4.8.1(1) | 6.5.7.5(2) | 6.5.9(3) | 8.1.1.3(3) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### Monitor Resource Status for Discrepancies |  |  |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instructions under normal conditions and Emergency Conditions. During Emergency Conditions, ERCOT may verbally request QSEs to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |  |
| Monitor COP | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>COP Monitor Periodically: - Review the COP changes utilizing the Date/Time of Submission column as a reference; IF: - A QSE has changed a resource status code, resource parameter, or ancillary service on a specific resource; THEN: - Review the change in the COP Monitor, AND - Notify the QSE representing the resource if the change is unacceptable to ERCOT. |  |
| Telemetered Status | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>Consistency Checks IF: - Discrepancy is identified between a COP and telemetered Resource Status; THEN: - Call the QSE representing Resource to determine the correct resource status and have them make the necessary correction. NOTE: It is not necessary to make calls for inconsistent telemetry/COP for quick start units. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Area Status>Nodal Operational Status>Resource Limit Data>Unit Tab WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) |  |
| ON TEST | - If the ONTEST Resource Status Code is used to indicate that a Generation Resource is performing a test, the QSE should notify ERCOT by 1800 in the Day-Ahead, - Review the list of approved Resources to be ONTEST, - ONTEST can be used by the QSE when in the start-up and shut-down mode. |  |
| Control Block Up/Down | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details>Unit tab - Control Block Current UP/DN are telemetry points that a QSE can use in emergency situations to communicate that a resources ability to adjust its output has been unexpectedly impaired. - If a QSE has a Control Block set for greater than 5 minutes, the system will set the corresponding (UP/DN) Too Long flag to indicate this to the operator. |  |
| ### Manual Override Checks |  |  |
| 1 | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL and LDL Periodically: - Review the Manual HDL and LDL overrides to ensure they are still needed. IF: - Override exists; THEN: - Coordinate with the Transmission Operator to determine if override is still needed. |  |
| ### Dynamically Scheduled Resource |  |  |
| NOTE | Each QSE may not have more than one DSR Load. |  |
| DSR | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Analyst Displays>Gen Monitoring Displays>Dynamic Schedules>Load Based IF: - A DSR load signal fails for any reason for > than one 15 minute Settlement Interval; THEN: - Notify the QSE and notify the Helpdesk to suspend validation of DSR Output Schedule. IF: - A DSR load signal fails for more than 10 consecutive hours; THEN: - Notify the Helpdesk to have DSR suspended until the signal is reliably restored. |  |
| NOTE | IF: - The signal failure is identified to be an ERCOT communication problem; THEN: - ERCOT will not suspend the QSE’s ability to use DSR. |  |
| ### Monitor QSE Ancillary Services Obligation |  |  |
| Monitor |  | Monitor the Regulation A/S details, RRS details and Non-Spin details displays. |
| NOTE |  | If any A/S insufficiencies are identified in the HRUC solution, refer to the “Replacement of Ancillary Service Due to Undeliverable/Failure to Provide” section of the “Supplemental Ancillary Services Market” procedure. |
| Real-Time A/S Shortage |  | WHEN: - A QSE shows a Real-Time A/S shortage; NOTIFY: - The effected QSE of their QSEs Resources’ telemetered value and their A/S Resource Responsibility; THEN: - Within ten minutes, the QSE must: - Correct the telemetered A/S Resource Responsibility to provide sufficient capacity, OR - Provide both appropriate justification for not satisfying their A/S Obligation AND a plan to correct the shortfall that is acceptable. IF: - The QSE is unable to replace their A/S Obligation; THEN: - Notify the Shift Supervisor and determine if A/S shortage amount and reliability need is sufficient enough for ERCOT to replace from existing offers. |
| A/S Difference in COP |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Participation>Physical Market>SASM Market>Failure To Provide IF: - A/S Difference (MW) column displays negative values in RED; THEN: - Verify that the Notification Flag column displays a “Y” (should automatically default). Change the “Y” to “No” for past hours and next day hours. Commit to database, - Press the “Send Notification” button and acknowledge the pop-up box indicating the notifications were sent, - Navigate to the Failure To Provide display and call the Market Participants that are displayed with a Failure MW, IF: - The QSE states that they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened. IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Failure To Provide section 6.7.2 of the Desktop Guide. |
| Infeasible A/S Capacity from RUC |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market> AS Replacement IF: - The Infeasible MW column is displaying MW values; THEN: - Change the Notification Flag to “Y” and commit to database, - Press the “Send Notification” button and acknowledge the pop-up box indicating the notifications were sent, - Navigate to the AS Replacement display and call the Market Participants that are displayed with an Infeasible MW. IF: - The QSE states that they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened; IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Undeliverable section 6.7.1 of the Desktop Guide. |
| NOTE |  | A QSE that has one or more of its Resources RUC-committed to provide Ancillary Services must increase its Ancillary Service Supply Responsibility by the total amount of RUC-committed Ancillary Service quantities. The QSE may only use a RUC-committed Resource to meet its Ancillary Service Supply Responsibility during that Resource’s RUC-Committed Interval if the Resource has been committed by the RUC process to provide Ancillary Service. The QSE shall indicate the exact amount and type of Ancillary Service for which it was committed as the Resource’s Ancillary Service Resource Responsibility and Ancillary Services Schedule for the RUC-Committed Intervals for both telemetry and COP information provided to ERCOT. Upon deployment of the Ancillary Services, the QSE shall adjust its Ancillary Services Schedule to reflect the amounts requested in the deployment. |

## 3.2	QSE Request to Move Ancillary Services

Procedure Purpose:  Evaluate QSE requests for moving Ancillary Services from one resource to another or through a trade with another QSE.

| Protocol Reference | 6.4.6 (7) | 6.4.6 (8) | 6.4.8.1.3 (2) | 6.5.7.5(2) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - A QSE may elect to change a Resource providing Ancillary Service to an alternate Resource; however they are NOT permitted to change the quantity of each type of Ancillary Service awarded. - Movement of A/S Resource responsibility from a Resource during the Adjustment Period is accomplished by use of COP updates. - A QSE may vary the quantity of A/S Resource Responsibility on Resources without obtaining prior ERCOT approval during the time window beginning 30 seconds prior to a five-minute clock interval and ending ten seconds prior to that five minute clock interval, provided the QSE complies with its total A/S Obligation. |
| Evaluate Request | IF: - A QSE makes notification to move any type of A/S from one resource to another or through a trade with another QSE; THEN: - Log the information. |
| Infeasible | IF: - It is determined later to be infeasible; THEN: - Notify the QSE that the A/S needs to be moved or replaced by ERCOT. |
| ERCOT Replaces at QSE Request | IF: - The QSE informs ERCOT that all or part of the A/S needs to be replaced; THEN: - Determine if the insufficient amount is significant enough to replace through SASM. - Refer to the “Replacement of A/S Due to Failure to Provide” in the SASM procedure. |

## 3.3	Responding to Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.9.4.1 | 6.5.9.4(5) | 6.5.7.6.2.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.1(1) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002 R2.4 | EOP-001 R3.1 | EOP-002 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005 R1.4, R1.5, R4 |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at management’s discretion, may issue an appeal through the public news media for voluntary energy conservation at any time. - System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. - If Non-Spin Reserve Service is being deployed at any time other than the top of the hour (less than 12 consecutive 5-minute intervals), deselect any Resources whose COP Non-Spin Resource Responsibility is “ZERO” for subsequent hours. |
| ### Advisory |  |
| 1 | IF: - Physical Responsive Capability falls below 3000 MW; THEN: - Coordinate with the Real Time Operator, AND - Post on MIS Public using Notice Builder. Typical posting: “ERCOT is issuing an Advisory for Physical Responsive Capability less than 3000 MW.” |
| 2 | Make log entry. |
| ### Watch |  |
| 1 | IF: - Physical Responsive Capability falls below 2500 MW; THEN: - Coordinate with the Real Time Operator and Transmission Operator, AND - Utilize Non-Spin that can be deployed to increase the Physical Responsive Capability (see Section 6.2 in Desktop Guide), - Post on MIS Public using Notice Builder. Typical posting: “ERCOT is issuing a Watch for Physical Responsive Capability less than 2500 MW”. |
| 2 | Make log entry. |
| ### Cancelation |  |
| 1 | IF: - (HDL-GEN) ≥ deployed Non-Spin plus 500 MW, AND - Physical Responsive Capability is ≥ 3000 MW; THEN: - Coordinate with the Real Time Desk and recall Non-Spin by sending a Zero MW XML (Refer to Desktop Guide section 6.2 “Recall All Non-Spin or Partial Non-Spin Recall”), AND - End message on MIS Public using Notice Builder. |

## 3.4	Responding to Capacity Shortages

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Capacity Shortages as requested by the Real-Time Operator.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If Non-Spin is being deployed at any time other than the top of the hour (less than 12 consecutive 5-minute intervals), deselect any Resources whose COP Non-Spin Resource Responsibility is “ZERO” for subsequent hours. (Refer to Desktop Guide section 6.2 “Non-Spin Deployment and Recall”) |
| Deployment | WHEN: - Notified by the Real-Time Operator to deploy Non-Spin for capacity shortages; THEN: - Coordinate with the Transmission Operator to verify the Non-Spin doesn’t create congestion, - Deploy Non-Spin, (Refer to Desktop Guide section 6.2 “Deploy All Non-Spin or Partial Non-Spin deployment”) - Notify the RUC Operator of the deployment |
| Termination | WHEN: - Notified by the Real-Time Operator that the Non-Spin Reserve Service is no longer needed - ; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide section 6.2 “Recall All Non-Spin or Partial Non-Spin Recall”) AND - Notify the RUC Operator of the Non-Spin termination. |

## 3.5	Potential DCS Event

Procedure Purpose:  To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.4.2(2)(a)(ii) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6.2 | EOP-001-0 R5 | EOP-002-2.1 R5, 6.1 |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC Recovery Criteria | Restore system frequency to the following limit within 15 minutes: - Scheduled frequency if it was greater than or equal to scheduled frequency prior to the disturbance, OR - Its pre-disturbance value if it was less than scheduled frequency prior to the disturbance. ERCOT ISO shall fully restore the minimum Contingency Reserve requirement of the ERCOT Region’s largest single contingency (1354 MW) as soon as practical. Within 90 minutes, ERCOT ISO will restore Responsive Reserves to 2300 MW or greater. This 90 minute restoration period begins at the end of the disturbance recovery period. |
| 1 | WHEN: - Instructed by the Real-Time operator to deploy Load Resources for a DCS event; THEN: - Deploy either “Group 1” or “Group 1 & 2” Load Resources (see Desktop Guide section 6.1 Loads Providing RRS Deployment and Recall, if needed) (this deployment will send the QSEs an XML message). This must be done before the Hotline call, - Notify the Real-Time operator that XML deployments have been sent. |
| NOTE | Load Resources will remain deployed, even if the responsibility changes, until the “Deployment End Time” is met or they are manually recalled by the Operator. |
| 2 | The deployment must be either extended or recalled before the Deployment End Time. If this is not done, the deployment will end without sending out recall messages, IF: - Extending Current Deployments; THEN: - Deploy either “Group 1” or “Group 1 & 2” Load Resources (see Desktop Guide section 6.1 Extending Current Deployments, if needed) (this deployment will continue to send the QSEs an XML message). , - Instruct the Real-Time operator to make another hotline call. |
| 3 | WHEN: - Notified by the Real-Time operator to recall Load Resources; THEN: - Send XML message to recall Load Resources, (see Desktop Guide section 6.1 Recall (Full or Partial), if needed) - Instruct the Real-Time operator to make a Hotline call to QSEs to end Emergency Notice and recall Load Resources. |
| PRC Below 2300 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Refer to the “Implement EEA” procedure. |
| Log | Enter log entry. |

## 3.7	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R2, R4.2 | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 |
|  | IRO-004 R3 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 3 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Issue Watch & Deploy Non-Spin | WHEN: - Notified by the Transmission Operator to deploy Non-Spin in the Houston area for the North-Houston Interface; THEN: - Deploy Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) (Refer to Desktop Guide section 6.2 “Partial Non-Spin deployment”) - Using the hotline, issue a Watch, - Post on MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North to Houston interface. ERCOT has deployed Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| Issue Emergency Notice & Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Deploy Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by XML (Refer to Desktop Guide section 6.1 “Deployment for Congestion/IROL”) - Using the hotline, issue the Emergency Notice, - Post on MIS Public using Notice Builder. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT has issued an Emergency Notice for the North to Houston interface and has issued you an electronic directive for the deployment of specific Load Resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Recall Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML (Refer to Desktop Guide section 6.1 “Recall (Full or Partial)”) - Using the hotline, cancel the Emergency Notice, - Cancel message on MIS Public using Notice Builder. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Emergency Notice for the North to Houston interface and has issued you an electronic directive for the recall of Load Resource deployments. ERCOT is reminding everyone that a Watch is still in effect until further notice. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Recall Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML, (Refer to Desktop Guide section 6.2 (“Partial Non-Spin Recall”) - Using the hotline, cancel the Watch, - Post on MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the North to Houston interface. ERCOT has recalled Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log the actions taken. |

## 4.1	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve or reject Resource decommitments in the Operating Period.

| Protocol Reference | 6.4.6 | 6.4.6.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Operating Period |  |
| NOTE | - The Operating Period is the two-hour period comprised of the Operating Hour and the clock hour preceding the Operating Hour - A QSE may request to decommit a Resource other than a QSGR for any interval that is not a RUC-Committed Interval by verbally requesting ERCOT to consider its request - A QSE may decommit a QSGR without any request for any interval that is neither a RUC-Committed Interval nor an interval in which a manual override by the ERCOT Operator. |
| 1 | IF: - A QSE requests to de-commit a Resource that has been Self-Committed (other than a QSGR); THEN: - Determine if the Resource has an Ancillary Service responsibility. If yes, inquire how this AS will be replaced, - Notify the Transmission Operator to make determination if needed for congestion management, - Notify the Shift Supervisor to ensure that requests will not have a reliability impact. NOTIFY: - The QSE of ERCOT’s decision. |
| 2 | IF: - Request is granted; THEN: - Issue an electronic VDI - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type from Resource Level |
| 3 | Log actions taken. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 6.4.8.1 | 6.4.8.1.1 | 6.4.8.1.2 | 6.4.8.1.3 |
| --- | --- | --- | --- | --- |
|  | 3.16 (4) | 6.4.8.2 | 6.4.8.2.2 | 6.5.9(4) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - Once the notice is given, no further offers are eligible for that SASM. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services will have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify with the RUC Operator that the Hotline call notifying the Market that the DAM failed, - Make the following hotline notification before opening the SASM, - Procure all Ancillary Services for the next operating day through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.4 of the Desktop Guide: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx] ERCOT will be opening a SASM to procure all Ancillary Services for [operating day] due to the Day-Ahead Market failure. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline Notification and post message on MIS Public using Notice Builder, - Procure more Ancillary Services through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.3 of the Desktop Guide. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch due to the need to increase the system wide A/S requirement above what was procured in the Day-Ahead Market due to [state the reason]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | Once verified that all Ancillary Service has been procured, cancel the Watch: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace AS capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the Ancillary Service capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to section 6.7.1 in the Desktop Guide). |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| Replacement of Ancillary Services in Real Time |  |
| NOTE | When issuing a VDI to a Resource for Real Time A/S insufficiency, ensure the QSE understands the unit is being brought online to provide an A/S. Also verify the QSE’s COP is updated when the unit is online. |
| 1 | IF: - A Real Time A/S shortage exists, AND - It is determined to be a reliability issue; THEN: - Issue a VDI to commit an off-line Resource that is qualified to provide the insufficient A/S in the time frame needed (Refer to the SASM section 6.7.5 of the Desktop Guide). - Choose “COMMIT” as the Instruction Type from Resource Level - In text, state “commit for replacement of [A/S type]” |
| NOTE | The QSE will need to telemeter the Resource status as “ONREG”. |

## 5.2	SASM Failure/Timeline Deviation

Procedure Purpose:  To manage SASM software failure or timeline deviation.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Failure of the SASM Software |  |
| 1 | IF: - The SASM workflow controller fails during any stage of the run; THEN: - Press the Abort button to cancel the current run, - Press the Shut Down button, - Press the Start Up button, - Press the Run All button to restart the sequence. |
| 2 | IF: - The SASM workflow controller continues to fail; NOTIFY: - Notify the appropriate ERCOT personnel. |
| ### Timeline Deviations |  |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - SASM process from opening a SASM market to the COP update is approximately 1 hour for an A/S plan increase. For replacement due to undeliverable/insufficient A/S, the timeline is 30 minutes. |
| A/S Plan Increase Timeline | Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - SASM Workflow Controller fails or needs to be restarted and cannot meet the timelines above; THEN: - Using the Hotline, notify the Market Participants that the SASM will be delayed. - Notify the appropriate ERCOT personnel. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is making notification that SASM has not met its timeline. ERCOT will manually commit as needed. [QSE] please repeat this back to me. That is correct, thank you.” |
| NOTE | NOTIFY: - The RUC Operator to determine if Resources can be manually committed within the timeframe needed. IF: - If needed in Real-time; THEN: - Refer to the Replacement of Ancillary Services in Real Time procedure, AND; - VDI to commit an off-line Resource that is qualified to provide the insufficient A/S in the time frame needed (Refer to the SASM section 6.7.5 of the Desktop Guide). - Choose “COMMIT” as the Instruction Type from Resource level - In text, state “commit for replacement of [A/S type]” |

## 7.1	Market Notices

Procedure Purpose:  Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - There is a Tropical Storm/Hurricane in the Gulf, either entering the Gulf or a newly formed storm projected to impact Texas. - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Wet weather, such as a tropical storm making land fall. - Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Tropical Storm/Hurricane currently projected to impact Texas. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Hurricane in the Gulf with expected landfall in Texas affecting the grid reliability. - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time deadlines. - DRUC failure - HRUC failure - SASM failure - SCED failure |
| ### Scripts |  |
| Hotline | Hotline calls are usually made by Real-Time Operator, the scripts below are for reference if needed: Notify QSEs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the only option is “public” - For “free form” messages, the “Notice priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| ### Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted QSE’s and TOs should be notified via Hotline call. - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Deploy all available Non-Spin (if not previously deployed), (see Desktop Guide section 6.2 “Non-Spin Deployment and Recall”, if needed) - If necessary, refer to section 3.4 “Responding to Capacity Shortages” - If RMR Resources are not loaded, over-ride LDL as necessary, - If possible, manually override LDL for specific Resources to operate at full capacity, - Issue VDI to any QSEs with Generation Resources available and off-line (that were not bid in for Non-Spin) that can perform within the timeframe of the emergency - Choose “Commit” as the Instruction Type from Resource level, - Make EEA 1 posting to MIS Public using Notice Builder. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2A |  |
| 1 | IF: - Physical Responsive Capability falls below 1750 MW; THEN: - Deploy Load Resources providing RRS as follows: (see Desktop Guide section 6.1 “Loads Providing RRS Deployment and Recall”, if needed) - Less than 1750 MW, deploy Group 1. - As system conditions require, deploy remaining load resources. - Less than 1400 MW deploy “BOTH” Groups simultaneously. - Notify Real-Time Operator when complete, XML message to deploy Load Resource must be done first before hotline call is made, - Notify Transmission Operator to implement EEA Level 2A, - Make EEA 2A posting to MIS Public using Notice Builder. IF: - Extending Current Deployments; THEN: - Deploy either “Group 1”, or “BOTH” Load Resources (see Desktop Guide section 6.1 “Extending Current Deployments”, if needed) (this will continue to send the same deployments to the QSEs). |
| 2 | IF: Went straight to EEA Level 2A; THEN: - Ensure tasks in EEA Level 1 are complete. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2B |  |
| 1 | IF: - Unable to maintain system frequency at 60.00Hz, AND Load Resources providing RRS have been deployed and EILS has been procured; THEN: - Make EEA 2B posting to MIS Public using Notice Builder. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Make EEA 3 posting to MIS Public using Notice Builder. |
| 2 | Verify and log that all measures have been implemented. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | If 2300 MW of Physical Responsive Capability is not restored within 75 minutes, reduce MW loading on Resources(s) to bring reserves up. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - Physical Responsive Capability supplied from generation is greater than 1354 MW; THEN: - Transmission Operator will restore firm load. |
| 2 | Maintain Physical Responsive Capability supplied from generation equal to 1354 MW while restoring firm load. |
| ### Move from EEA Level 3 to EEA Level 2B |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - Physical Reserve Capability supplied from generation is equal to 1354 MW, AND - All firm loads have been restored; THEN: - When instructed by the Real-Time Operator to recall Load Resources, - Send XML message to recall Load Resources, (see Desktop Guide section 6.1 “Recall (Full or Partial)”, if needed) - Make EEA 3 to EEA 2B posting to MIS Public using Notice Builder. - If restoring Load Resources and EILS together make appropriate posting EEA 3 to EEA 2A. |
| ### Move from EEA Level 2B to EEA Level 2A |  |
| 1 | IF: - The system can maintain Physical Responsive Capability equal to or greater than 1750 MW, AND - All Load Resources have been instructed to be recalled, AND - Sufficient Regulation Service exists to control to 60 Hz, THEN: - Make EEA 2B to EEA 2A posting to MIS Public using Notice Builder. |
| ### Move from EEA Level 2A to EEA Level 1 |  |
| 1 | IF: - The system can maintain Physical Responsive Capability equal to or greater than 2300 MWs AND - Confirm Load Resources and EILS have been instructed to be restored; THEN: - Make EEA 2A to EEA 1 posting to MIS Public using Notice Builder. |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain Physical Responsive Capability equal to or greater than 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Make EEA 1 to EEA 0 posting to MIS Public using Notice Builder. |
| ### Cancel Watch |  |
| 1 | WHEN: - (HDL-Gen) ≥ deployed Non-Spin plus 500 MW, AND - Physical Responsive Capability is ≥ 3000 MW; THEN: - Recall Non-Spin by sending a Zero MW XML (Refer to Desktop Guide section 6.2 “Recall All Non-Spin or Partial Non-Spin Recall”), AND - Update message on MIS Public using Notice Builder. |

## 8.2	Monthly Testing of Satellite Phones

Procedure Purpose: To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001 R2 | EOP-005 R5 |  |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with the TOs. As the Shift Supervisor makes the call to the individual TO, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TO. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Section 8.7 of the Desktop Guide) for a list of the TOs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Bridge are Desk specific, located on the bottom right of page 11 of the MX Turret phone as identified below: - BKST RUC – RUC Desk - BKST RES – Resource Desk - BKST RTD – Real-Time Desk - BKST TS#1 – Transmission Desk |
| 1 | IF: - The preprogrammed number does not function correctly; THEN: - Refer to the ERCOT Satellite Phone User Guide (See Section 8.7 of the Desktop Guide) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the TOs fails to connect to the Bridge call; THEN: - Investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the TOs not able to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |
| ### Alternate Control Center |  |
| 1 | When working out of the alternate during the monthly scheduled dates: - Test the turret Satellite phone on each desk. |
| 2 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |