## Power Operations Bulletin # 521

ERCOT has posted/revised the NODAL Transmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	Site Failovers and Database Loads

Procedure Purpose: To provide notice to the Market Participants when ERCOT performs site failovers and database loads.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Database Loads | Approximately 5 - 30 minutes before a database load, make the following Hotline call to TOs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a Database load on its Energy & Market Management Systems. During this time, SCED BP will reflect accurate dispatch instructions. In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes. |
| Site Failovers | Approximately 5 - 30 minutes before a database load, make the following Hotline call to TOs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx] on [Month **, ****], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 30 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. |
| Site Failover Posting | Verify with Real-Time operator that posting will be made. The site failover message is already built in Notice Builder under “EMS Site Failover”. |

## 2.4	Switching Control Centers

Procedure Purpose: To provide notice to the Market Participants when ERCOT is working from the Alternate Control Center.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Hotline Call | When transferring operations from primary site to alternate site (and vice versa). Make the following hotline call to TOs: Typical Script for working from Alternate site: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the alternate control center until further notice, use the OPX numbers for Austin. [TO], please repeat that back to me. Typical Script for working from Primary site: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the primary control center until further notice, use the OPX numbers for Taylor. [TO], please repeat that back to me. That is correct, thank you.” |
| MIS Posting | Verify with Real-Time operator that posting was made. Typical Posting for working from Alternate site: ERCOT is working from alternate control center. Typical Posting for working from Primary site: ERCOT is working from primary control center. |

## 3.3	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002 R8, R9 | NUC-001 | TOP-004 R4 |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT |
| 1 | IF: - RTCA or the State Estimator has not solved within the last 10 minutes, THEN: - Notify Shift Engineer, - Refer to Section 3.1 of the Desktop Guide and run through the checklist, - Request Shift Engineer to calculate limits manually if EMS will be unavailable for an extended period of time. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 15 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to issue an Advisory to the TOs: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator have not solved in the last 15 minutes. Please monitor your own service area and notify ERCOT if you exceed the normal rating of your transmission elements. Report West - North and North – Houston stability limits if power flows reach 90% of their respective limits. Continue to monitor voltages in your area and notify ERCOT of any forced line operations.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Notify the appropriate Nuclear Plant’s QSEs and inform them that ERCOT’s RTCA is not function and is expected to be functional within approximately [# minutes]. |
| 4 | Post Advisory message on MIS Public using Notice Builder. |
| 5 | Once RTCA and State Estimator are operational: Make a Hotline call to cancel the Advisory to the TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT’s RTCA and State Estimator are functioning and we are back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 6 | Notify the appropriate Nuclear Plant’s QSEs to inform them that RTCA is now functional. |
| 7 | Cancel Advisory message on MIS Public using Notice Builder. |
| 8 | If VSAT has not solved within 1.5 hours: - Manually run VSAT, - If no results, notify Shift Engineer, - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |
| 9 | Make log entry of events. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-003 R1 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006 R1, R4 |
|  | IRO-002 R6, R8 | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |

| Version: 1 | Revision: 4 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. Error! Hyperlink reference not valid.A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) located in the Outage Notes - Unit specific dispatch instructions (Manual Dispatch or VDI) - If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - The electronic version is located at P:\System Operation\Remedial Action Plans, - A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congesting management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – mitigate local congestion and increase W/N transfers - Big Lake – mitigate local congestion and increase W/N transfers - Firerock ETT – mitigate local congestion and increase W/N transfers - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - SE and/or RTCA is not solving; THEN: - Notify Shift Engineer, IF: - SE and/or RTCA has not solved for 15 minutes, THEN: - Refer to section 3.3 “Analysis Tool Outages” in this procedure. |  |
| 2 | IF: - RTCA has run within 10 minutes; THEN: - Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |  |
| 3 | IF: - A major change of Resource or Transmission Element Status; THEN: - Re-start RTCA and VSAT. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Determine if the SCADA is of similar magnitude to the Pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Shift Engineer. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP, - Refer to “Managing Binding and Exceeded Constraints” of this Procedure. |  |
| 4 | IF: - Post-contingency overloads greater than 100% exist without an SPS (identified as RAS in EMS), RAP, PCAP, or TOAP in place to relieve; THEN: - Activate constraints as necessary, - Lower the value in the % Rating column in RTCAM to tighten the constraint (minimum of 95%), - Increase the value in the % Rating column in RTCAM to loosen the constraint (maximum of 105%), - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 5 | IF: - There is an imminent threat to the reliability of the ERCOT system, caused by a Qualifying Facility (QF), and ERCOT decides to order the QF offline or to operate below its LSL; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT/ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to an immediate threat to the reliability of the ERCOT system that required directing a Qualifying Facility [offline/operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 6 | IF: - Post-contingency overloads greater than 100% of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 7 | IF: - Any RTCA results predict a Facility Rating will exceed post-contingency loading of 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL; THEN: - Refer to section 4.2 “Potential IROL’s”. |  |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |  |
| 9 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Shift Engineer, - If there are known reasons that the contingency is unsolved, notify the Shift Engineer to verify system conditions have not changed. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A Quick Start Resource is needed and not given SCED base points; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running), - Notify QSE as time permits. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| ### Transmission Issues in the Areas of the CFE DC-Ties |  |  |
| 1 | IF: - Contingencies or unsolved contingencies cannot be corrected with congestion management techniques; THEN: - Determine if there are schedules over the CFE Ties that would help the situation. |  |
| 2 | IF: - DC-Tie schedules can be curtailed to alleviate the transmission issue; THEN: - Notify the DC Tie Operator to curtail the schedule(s), - Issue a Transmission Watch (if giving advance notice) or Emergency (if advance notice cannot be given), - Make Hotline call, - Make notification on MIS Public using Notice Builder - Notify Real-Time Desk to make Hotline call to QSEs. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission [Watch or Emergency] due to a post contingency loss of (name of contingency) overloads (name of overloaded element).” [TO] please repeat this back to me. That is correct, thank you.” Edit script as needed to fit situation. |  |
| ### Managing Binding and Exceeded Constraints |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| 1 | IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk and control room staff, - Determine the need for resolving the constraint by overriding LDL (hold up) and/or HDL (hold down) - DO NOT override while SCED is running - DO NOT override a Resource ONTEST, - Notify QSE as time permits. |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, maximum shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for exceeded constraints). |  |
| 2 | IF: - The transmission element flows are greater than the limit (exceeded); THEN: - Verify that the SCED executions are reducing the flows on the subject constraints, - Investigate units with large shift factors that are not being moved or are not following base points, - Create a “Suggestion Plan” for the constraint, - Instruct Shift Engineer to consult with the appropriate TO(s) to determine if there is a network re-configuration or post-contingency switching action that could be used to resolve the exceedance. |  |
| Log | Log all action taken. |  |
| ### SCED not able to Solve Congestion (reaching shadow price cap) |  |  |
| NOTE | Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary Review the DSP Constraint Summary display, a constraint has reached its max shadow price cap when the Flow (MW) is higher than Limit (MW). |  |
| 1 | Steps that may be taken to resolve congestion when a transmission constraint is exceeded in SCED after the Shadow Price reaches price cap include: - Verify telemetry is correct, - Verify base points are being followed, - Redistribute A/S to increase the capacity available to SCED, - Instruct QSE to remove the appropriate A/S and to update telemetry, - Notify Resource Operator with undeliverable A/S type, amount and hours from the Resource(s), - Removing a unit from ONTEST, - Commit/decommit additional units, - Formulate a mitigation plan which may include - Transmission reconfiguration (switching) - Load rollover to adjacent feeders - Load shed plans, - Re-dispatch generation through overriding HDL/LDL only if there is not a SCED solution, - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - Release binding constraint, if feasible - Notify QSE (this could exceed ramp rate) |  |
| ### QSE Requests to Decommit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Initiate the Emergency Notice Hotline call, AND - Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 2 | Trouble Shooting: IF: - Transmission constraints are active, THEN: - Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |  |

## 4.3	West-North Stability Limit

Procedure Purpose: Maintain Transmission stability between the West and North.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Refernce |  |  |  |  |
| NERC Standard | EOP-001 R4.2 | IRO-002 R6, R8 | IRO-003 R1 | IRO-004 R3 |
|  | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 | TOP-004 R1, R2, R6, R6.6 |
|  | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |  |

| Version: 1 | Revision: 4 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North stability limit is an IROL; The actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| 1 | IF: - The West-North stability limit calculated on the spreadsheet changes value or color; THEN: - Verify the value is accurate and update limit on RTMONI to give transparency to Market Participants, - Monitor as needed to the value shown on the spreadsheet. |
| NOTE | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change. It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| 2 | IF: - The monitored flow on the Stability-WN monitor is approaching 70%; THEN: - Activate the West-North constraint, - Post message on MIS Public using Notice Builder, Typical Message Script: “ERCOT is constraining for the West-North stability limit.” |
| 3 | Once wind output is controlled, keep constrained around 80% – 85% IF: - West – North exceeds 100% for 10 minutes; THEN: - Instruct QSEs with the largest WGR base point deviation to zero immediately (violate ramp rate), - Issue electronic VDI as time permits, - Notify the control room staff. Typical Script: “This is ERCOT operator [first and last name]. The West to North flow is exceeding the stability limit; At [xx:xx] ERCOT is instructing you to take [unit name] to zero effective immediately, which means you may violate your ramp rate. I will be sending you an electronic VDI shortly. [QSE] please repeat this back to me. That is correct, thank you.” |
| 4 | IF: - Congestion management techniques fail to control the flow within 20 minutes; THEN: - Issue directive to TO to open WGR breaker with the largest WGR base point deviation (refer to Real-Time spreadsheet tab “West Wind”), - Issue electronic VDI as time permits, - Notify the control room staff. |
| Log | Log all actions taken. |

## 4.4	North-Houston Voltage Stability Limit

Procedure Purpose:  Maintain Transmission Stability between the North and Houston.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R2, R4.2 | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 |
|  | IRO-004 R3 | IRO-005 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT Dynamic Voltage Stability Limit is an IROL; The actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards, |
| VSAT | - Ensure VSAT runs every hour, - Update RTMONI with new limit each hour to give transparency to Market Participants. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| North-Houston 345kV Circuit Outage | IF: - Any of the 345kV lines going into the Houston area has a forced outage; THEN: - Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor Step in this procedure. |
| Monitor | Monitor each of the following Reliability Margins: - O-H_L - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TOs in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| ≤400MW | - Activate the appropriate constraint, - Post message on MIS Public using Notice Builder. Typical Message Script: “ERCOT is constraining for the North-Houston voltage stability limit.” |
| ≤300MW | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL - Instruct Resource Desk Operator to deploy Non-Spin in the Houston area and make Hotline notification, - Issue a Transmission Watch by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North-Houston interface. Non-Spin is being deployed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| ≤200MW | VDI QSGR in the Houston area that were not bid in as Non-Spin. Override LDLs as needed. - Determine QSRG in the Coast Weather Zone (WZ_COAST) - Choose “COMMIT” as the Instruction Type from Resource level |
| ≤100MW | - Instruct the Resource Desk Operator to deploy Load Resources providing RRS in Houston, - Issue a Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Real-Time Operator to make same Hotline notification to QSEs, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice for the North-Houston interface. Load Resources in the Houston area are being deployed to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| 0MW ≥ 15 Minutes | - Instruct Centerpoint to drop firm load in 100 MW blocks. - Continue Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make NXT notification and RCIS posting. Typical Script for Centerpoint: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is instructing Centerpoint to drop [*** MW] of firm load for the North – Houston stability limit. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” Typical Script for Hotline: “At [xx:xx], ERCOT is continuing the Transmission Emergency Notice for the North-Houston interface. Firm Load is being shed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| Cancel | Make appropriate cancellations when back to normal operations. |
| Log | Log all actions taken. |

## 4.5	SPS, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 5.5.2 | 6.5.1.1(a),(c),(e) |  | 6.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.5.2(1) | 6.5.7.1.10 | 6.5.7.1.11(1),(4) | 6.5.7.8 |
|  | 6.5.9 | 6.5.9.1(1)(d) |  | 7.1 |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R2, R3.2, R3.3, R4.2 | IRO-003 R1 | IRO-005-2 R1.1,R1.2, R1.3, R1.7, R1.10, R3, R5, R9, R12, R13, R16, R17 | IRO-006-3 R1, R3, R4, R5, R6 |
|  | IRO-002-1 R6, R8 | IRO-004-1 R3 | TOP-001 R1, R2, R5 | TOP-002-2 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006-1 R3, R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6, R8 |
|  | PRC-001-1 R6 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. The electronic version is located at P:\Remedial Action Plans |
| NOTE | Special Protection Schemes (SPS) (identified as RAS in EMS) OR Remedial Action Plans (RAP) - EXAMINE the results of RTCA, - If the background has a color indicating a SPS or RAP, - Refer to Section 3.6 of the Desktop Reference Guide for actions to be taken based on the color of the background. |
| Directives | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log all actions taken. |
| Special Protection Systems (SPS) (Identified as RAS in EMS) |  |
| NOTE | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingency loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario, congestion management is not needed until the criteria in Section 3.6 of the Desktop Reference Guide, is met. |
| Monitor | Each SPS will be displayed on the “Real Time Values” spreadsheet, as the SPS activation threshold increases the display changes color as follows: - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 1 | Typically SPSs are to solve post-contingency overloads on the Transmission System. IF: - The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an SPS; THEN: - Utilize congestion management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the SPS will not mitigate all the overloaded elements automatically; THEN: - As system conditions warrant, utilize congestion management techniques to relieve the overload. |
| 3 | IF: - No reliability issues will arise as a result of a SPS’s operation; THEN: - At the Operator’s discretion, allow the SPS to perform its function. |
| 4 | IF: - A WGR SPS on the “Real Time Values” spreadsheet is greater than 90%; THEN: - Active the appropriate generic constraint in TCM. |
| 5 | IF: - An SPS operates; THEN: - Notify affected TO to reset SPS as system conditions warrant, - Notify Shift Supervisor of the need for a Texas RE Report if generation disconnected from the grid or a transmission line tripped. |
| SPS Posting | All SPSs are considered in-service unless otherwise notified by the TO. If the SPS is out of service, ERCOT will post the information on MIS Public using Notice Builder. Once the SPS is placed back in service, ERCOT will cancel the message. Typical message: The [name] SPS has been taken out of service. |
| Status Change | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated, - “OPS Planning” - “OPS Support Engineering” - “1 ERCOT System Operators” Typical message: The [name] SPS has been taken out of service. The [name] SPS has returned to service. |
| Remedial Action Plan (RAP) |  |
| 1 | TCM DOES NOT model RAP when generating constraints so they tend to over-constrain at 100% of emergency rating instead of 100% of the 15min rating. - Activate constraints as necessary, - Lower the value in the % Rating column in TCM to tighten the constraint (minimum 95%), - Increase the value in the % Rating column in TCM to loosen the constraint (maximum 105%). |
| 2 | IF: - A RAP exists for the contingency; THEN: - Review the RAP with the associated TO, - Notify the Shift Supervisor of the anticipated actions. |
| 3 | IF: - The contingency anticipated by the RAP takes place; THEN: - Direct the implementation of the RAP, - Respond to requests made by the TO in accordance with the RAP, - If necessary, continue to use additional congestion management methods, - When the contingency clears, notify the TO as soon as possible. |
| Pre-Contingency Action Plan (PCAP) |  |
| CAUTION | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. These actions may be taken to increase transmission transfer capability. |
| 1 | WHEN: - RTCA shows a post-contingency overload and a PCAP exists to resolve it; THEN: - Review the PCAP with the associated Transmission Operator, - Notify the Shift Supervisor of the anticipated actions, - Direct the execution of the PCAP with the associated Transmission Operator. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [TO] to implement the ****PCAP and [open/close] [breaker(s)]. [TO] please repeat this back to me. That is correct, thank you.” |
| NOTE | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 2 | IF: - Any PCAPs are still in use (reviewed each day between 0000 and 0500), AND - It is determined, in concurrence with the Shift Supervisor that it is no longer needed; THEN: - Direct the associated Transmission Operator to return the system to: - Its normal status, OR - Its status prior to implementation of the PCAP. |
| Mitigation Plan (MP) |  |
| NOTE | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. - With a MP, an operator does not need to declare a Watch for a post contingency overload, - If a MP is enacted and subsequent congestion management techniques do not control post contingency loading, issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder |
| 1 | IF: - RTCA shows a post-contingency overload greater than 100% of the Load Shed Rating; THEN: - Attempt to resolve the overload by using congestion management methods. |
| 2 | IF: - A MP exists for the contingency; THEN: - Review the MP with the associated TO, - TOP repeats back the directive to verify the plan is understood, - Notify the Shift Supervisor of the anticipated actions. |
| 3 | IF: - A MP does not exist or fails to relieve the overload for this contingency and the Outage Notes do not provide a plan; THEN: - REQUEST the Shift Engineer investigate the development of a MP or correct errors in the current plan. |
| 4 | IF: - The anticipated contingency takes place; THEN: - Direct the implementation of the MP to the TO, - TO repeats back directive to verify implementation is understood, - Respond as quickly as possible to requests made by the TO in accordance with the MP, - If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP. |
| 5 | WHEN: - The contingency clears; THEN: - Notify the TO as soon as possible. |
| Temporary Outage Action Plan (TOAP) |  |
| 1 | IF: - The post-contingency overload is due to a temporary outage on a transmission line(s) or a transmission facility; THEN: - Locate the outage in the Outage Notes, - Implement the associated actions. |

## 4.6	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security.

| Protocol Reference | 6.3.2(2) | 6.5.7.1.10(3) | 6.5.7.8 | 6.5.7.9(7) |
| --- | --- | --- | --- | --- |
|  | 6.5.9 (3) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R6 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The order of steps in this procedure is a recommendation. The System Operator will determine the sequence of steps, or any additional actions necessary to ensure system security. |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instruction under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |
| ### Manual Dispatch Instruction to take a Unit Off-Line |  |
| 1 | This step DOES NOT apply to Qualifying Facilities (QF). For QF’s, refer to Transmission Congestion Management/Post-Contingency Overloads/step 5. IF: - A manual dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue a VDI taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Ensure QSE updates telemetry. |
| ### Taking One CT of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one CT of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and determine which CT should receive the dispatch instruction, - Obtain the MW output impact the CT’s dispatch instruction will have on the steam unit, - Issue VDI to dispatch the CT off-line and instruct the QSE to adjust their CC configuration. - Choose “DECOMMIT” as the Instruction Type from Resource level |
| ### Manual Commit of a Resource |  |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition; THEN: - Issue a VDI to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - See Desktop Guide Section 8.3 for additional information to submit a correct VDI. |
| 2 | Log information. |

## 4.7	Responding to Diminishing Reserves

Procedure Purpose: Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 6.5.9.4.1 | 6.5.9.4(5) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002 R2.4 | EOP-001 R3.1 | EOP-002 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005 R1.4, R1.5, R4 |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at management’s discretion, may issue an appeal through the public news media for voluntary energy conservation at any time. - System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. - Resource Desk Operator will post message on MIS Public. |
| ### Advisory |  |
| 1 | IF: - Physical Responsive Capability falls below 3000 MW; THEN: - Using the Hotline, issue an Advisory. Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory due to Physical Responsive Capability has fallen below 3000 MW. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Watch |  |
| 2 | IF: - Physical Responsive Capability falls below 2500 MW; THEN: - Using the Hotline, issue a Watch. Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to Physical Responsive Capability has fallen below 2500 MW. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log actions |
| ### Cancelation |  |
| 1 | WHEN: - Advisory or Watch is canceled; THEN: - Using the hotline cancel the Notice. Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. Physical Responsive Capability is now above 2500 MW. [TO] please repeat this back to me. That is correct, thank you.” OR Typical script: “This is ERCOT Operator [first and last name]. ERCOT is canceling the Advisory for Physical Responsive Capability. Physical Responsive Capability is now above 3000 MW. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15 | 6.1.7 | 6.3.1 (1) | 6.3.2(2) |
| --- | --- | --- | --- | --- |
|  | 6.5.1.1(a)&(c) | 6.5.5.1(2) &(3) | 6.5.6 | 6.5.7 |
|  | 6.5.7.7 | 6.5.9.1(1)(c) | 6.6.7.1 | 6.7.6 |
| Guide Reference | 2.2.4 | 2.7.2(h)(ii) | 2.7.4.1(1) | 2.7.4.3 |
|  | 5.1.4 |  |  |  |
| NERC Standand | IRO-005-2 R1.2, R1.3, R1.4 | NUC-001-2 R4.2 | TOP-002-2 R8, R10 | VAR-001-1 R1, R2, R4, R6, R7, R8, R9, R10, R12 |
|  | VAR-002-1 R3.1 | IRO-002-1 R6, R8 | TOP-004-2 R6.2 | TOP-006-1 R2 |
|  | EOP-001-0 R4.2 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "normal" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS). Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Voltage Tables | For Comanche Peak - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. For South Texas Project - System; - 345 kV. - Nominal Voltage; - 362.25 kV. - Tolerance; - +0% or -6.14%. - Maximum Voltage; - 362.25 kV. - Minimum Voltage; - 340 kV. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. When STP is in an alternate line up, the minimum voltage is 347 kV. When STP is in an alternate line up without the unit auxiliary transformer, the minimum voltage is 355 kV. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated in the voltage tables; THEN: - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate QSE. |
| ### Voltage Issues |  |
| NOTE | - Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Section 3.9 of the Desktop Guide. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damages is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implements and studies shall that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. |
| 1 | WHEN: - Indicated by SCADA alarms, OR - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. |
| 2 | When instructing a QSE to raise or lower bus voltage when area TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) should be as follows: Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| Exceed URL | For multi-generator busses, ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL until all On-Line Generation at the same transmission bus have been instructed to their respective CURLs or URLs. IF: - Instructing a QSE’s Generation Resource to exceed its Unit Reactive Limit (URL); THEN: - Issue a VDI to the QSE for exceeding the URL (Exceed URL VDI). The VDI must include the following: - Resource name - Specific voltage set point. - Start time - End time - Choose “HOLD X VOLTAGE LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| Reduce MW | IF: - MW output must be reduced to follow a voltage support instruction; THEN: - Issue a VDI to the QSE providing Voltage Support Service (VSS VDI). The VDI must include the following: - Resource name - MW level at time of instruction - MW level Resource needs to move to for Voltage Support - Start time - End time - Choose “STAY AT/ABOVE X MW/MVAR LEVEL” or “STAY AT/BELOW X MW/MVAR LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| NOTE | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure XX. |
| 1 | IF: - VSAT has not run in the last 80 minutes, OR - S-H or N-H 345kV circuit has a forced outage, OR - VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status; THEN: - Rerun the RTNET, RTCA, and RTDCP (VSA). If no change, then: - Notify the Shift Supervisor and Shift Engineer - As deemed necessary make the following Hotline call. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is experiencing problems with the Voltage Stability Analysis program. Maintain voltage levels as required by your procedures and notify ERCOT of any voltage issues within your system. [TO] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) more frequently than the periodic scheduled VSAT run. - Confirm VSAT indicates either “Normal” or “Pending”. Reliability Margin Table. Scenario Name; Safety Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. HHGT_G-O; 0MW. |
| For HHGT_G-O | For HHGT_G-O: Instruction the QSE to raise or lower bus voltage: Typical script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specified bus] by (+ 1 or 2 kV or – 1 or 2 kV) for a target of [target kV] [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| 3 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the Extra-Interface Limit pre-contingency value is less than the Safety Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 4. |
| 4 | Determine the contingency status in RTCA (solved/unsolved).IF: - Solved, - Have Shift Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Shift Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct HRUC Operator to commit additional resources in the weak bus area that are available. |
| 5 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 6 | Determine if the Extra-Interface Limit pre-contingency value is greater than the Reliability Margin Value. IF: - The Extra-Interface Limit pre-contingency value is greater than the Reliability margin; THEN: - No further action is required. OR IF: - The Extra-Interface Limit pre-contingency value is less than the Reliability margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 4. If no additional generation is available, continue. |
| 7 | IF: - No additional generation is available; THEN: - Ensure that the OPS Support Engineering group has been contacted to devise a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT. |
| NOTE | Operations Planning will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT SharePoint > Operations Support > AVR AND PSS Status |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, - Notify the appropriate TO of the change in status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “OPS Planning” - “OPS Support Engineering” - “1 ERCOT System Operators” |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. To update the “real time values” spreadsheet when any PSS is forced offline in the West zone: - Open the Stability Limit tab to verify units, - Enter 0 = PSS is offline; 1 = PSS online for each resource change. It allows the Operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - There is a Tropical Storm/Hurricane in the Gulf. Either entering the Gulf or a newly formed storm projected to impact Texas according to the “National Hurricane Center” (http://www.nhc.noaa.gov). - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Wet weather, such as a tropical storm making land fall. - Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Tropical Storm/Hurricane in the Gulf. Currently projected to impact Texas according to the “National Hurricane Center” http://www.nhc.noaa.gov. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a hurricane in the Gulf and an expected landfall in Texas affecting grid reliability - http://www.nhc.noaa.gov - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution - Loss of Primary Control Center Functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time deadlines. - DRUC failure - HRUC failure - SASM failure - SCED failure |
| ### Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on the MIS Public using Notice Builder. - For “free form” messages, the only option is “public” - For “free form” messages, the “Notice priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted, QSEs should be notified via Hotline call (see 2b for typical script). - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Using the Hotline, notify all TOs to implement EEA 1. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is implementing EEA 1 due to Physical Responsive Capability is below 2300 MW. [TO] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | - Relax transmission constraints to provide additional generation at the expense of temporarily creating a security violation as long as the violation does not physically overload any single Transmission Element above its emergency rating, - Inquire about the availability of registered BLTs (see Section in Desktop Guide). |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2A |  |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| 1 | IF: - Physical Responsive Capability falls below 1750MW; THEN: - Using the Hotline, notify all TOs to implement EEA 2A and any measures associated with EEA 1, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is implementing EEA 2A; - Load Resources providing RRS have been deployed, - Reduce customer loads by using distribution voltage reduction measures, if deemed beneficial. [TO] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | - Unless already in effect, verify with the shift supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Typical Script: “This is ERCOT Operator [first and last name]; this is a courtesy call to inform you that ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2B |  |
| NOTE | If no EILS exists, skip EEA 2B and proceed to EEA 3 if needed. If the amount of EILS available for deployment equals or exceeds 500 MW. EILS may be deployed as a single block or in two groups. |
| 1 | IF: - Unable to maintain system frequency at 60.00Hz AND Load Resources providing RRS have been deployed and EILS has been procured; THEN: - Using the Hotline, notify all TOs to implement EEA 2B and any measures associated with EEA 1 and 2A, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is implementing EEA 2B. EILS are being deployed. [TO] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Using the Hotline, notify all TOs to implement EEA 3 and any measures associated with EEA 1, 2A, and 2B, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is implementing EEA 3. ERCOT is instructing all Transmission Operators to shed their share of [amount] MW. Transmission Operators are to report to ERCOT when this is complete. [TO] please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - Physical Responsive Capability supplied from generation is greater than 1354 MW; THEN: - Using the Hotline, notify all TOs of firm load restoration. Typical Script when only restoring a portion of the firm load: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is instructing all Transmission Operators to restore their share of [amount] MW leaving [amount] MW still off. Report to ERCOT when this task is complete. [TO] please repeat this back to me. “That is correct, thank you.” OR Typical Script when restoring all firm load: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is instructing all Transmission Operators to restore all firm load. Report to ERCOT when this task is complete. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 3 to EEA Level 2B |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - Physical Reserve Capability supplied from generation is equal to 1354 MW, AND - All firm load has been restored; THEN: - Using the hotline, notify all TOs of the reduction from EEA 3 to EEA 2B: - Notify the TOs that Load Resources are being restored (if restoring Load Resources and EILS together, see script in 3a). - Rescind distribution voltage reduction measures as appropriate. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 3 to EEA 2B. All Load Resources are being recalled. Any TO that implemented distribution voltage reduction measures can return to normal operation”. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 2B to EEA Level 2A |  |
| 1 | IF: - The system can maintain Physical Responsive Capability equal to or greater than 1750 MW, AND - All Load Resources have been instructed to be recalled, AND - Sufficient Regulation Service exists to control to 60 Hz; THEN: - Using the hotline, notify all TOs that EILS are being restored. Typical script for recalling Load Resources and EILS: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2B to EEA 2A. All Load Resources and EILS are being recalled. [TO] please repeat this back to me. That is correct, thank you.” OR Typical script for recalling EILS: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2B to EEA 2A. All EILS are being recalled. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 2A to EEA Level 1 |  |
| 1 | IF: - The system can maintain Physical Responsive Capability equal to or greater than 2300 MW AND - All Load Resources and EILS have been instructed to be restored; THEN: - Using the hotline, notify all TOs of the reduction from EEA 2A to EEA 1, - If BLTs were implemented, restore. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2A to EEA 1, [if Block Load Transfers have been executed please coordinate with ERCOT to restore them as system conditions permit]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain Physical Responsive Capability equal to or greater than 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Using the hotline, notify all TOs of the reduction from EEA 1 to EEA 0. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is terminating EEA. A Watch still remains in effect. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Cancel Watch |  |
| 1 | WHEN: - Physical Responsive Capability is equal to or greater than 3000 MW, AND - Non-Spin has been recalled; THEN: - Cancel Watch Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. Physical Responsive Capability is now above 2500 MW. [TO] please repeat this back to me. That is correct, thank you.” |

## 7.5	Restoration of Primary Control Center Functionality

Procedure Purpose:  To be performed once Transmission and Security Operator has arrived at ACC.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: | 1 | Revision: | 1 | Effective Date: January 31, 2011 |
| --- | --- | --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| - Congestion Management | Continue with congestion management either manually or with systems. Check with other Operators to determine if any VDIs were issued. |
| Return to Normal TO Notification | When ready to resume normal operation, place the following Hotline call to the TOs: - Typical Script: - “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is canceling the Emergency Notice and is resuming normal operations from the [alternate/primary] control center. [Select TO], Please repeat that back for me. That is correct, thank you.” |
| Nuclear Plants | Notify the appropriate Nuclear Plant’s QSE and inform them that they should notify the plants that ERCOT has canceled the Emergency Notice and RTCA and State Estimator are now functional. |
| Log | Make log entries as needed. |

## 8.1	Hurricane / Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | There is an [Hurricane / Tropical Storm] in the Gulf with a chance of landfall in Texas. ERCOT will issue the following notifications and directives as storm conditions change according to the National Hurricane Center (http://www.nhc.noaa.gov) |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | Consult with the Shift Supervisor and Real-Time Operator to determine the appropriate Market Notification that should be issued based on the severity level of the storm and the location of the coastal region that will be impacted. |
| OCN | Issue an OCN to inform all TO there is a Tropical Storm/Hurricane in the Gulf, either entering the Gulf or a newly formed storm projected to impact Texas. Typical Script: “This call requires everyone to remain on the line until it is complete. [TOs] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a [tropical storm/hurricane] [Name] has [Entered/Formed] in Gulf of Mexico and is projected to impact Texas. - ERCOT will be reviewing planned outages associated with the impact area of the storm to determine if they should be rejected. - ERCOT will be reviewing existing outages for the possibility of withdrawing approval and restoring the outages associated with the impact area of the storm to service. TOs may be impacted are instructed to: - Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities. - Immediately notify ERCOT and make preparations to test its’ Backup Site communications if TOs plan to relocate operations to a backup control centers. ERCOT will continue to monitor the Storm and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory | Issue an Advisory to all TOs if the [Tropical Storm/Hurricane] is currently projected to impact Texas. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the [tropical storm/hurricane] [Name] in the Gulf of Mexico and is currently projected to impact Texas according to the National Hurricane Center. ERCOT is continuing to review outages to determine their priority for restoration. TOs that may be impacted are instructed to: - Review internal preparations and report to ERCOT on the status of operations (to include status of primary/backup control centers, and any staffing changes at primary/backup control centers, due to evacuations) - Immediately notify ERCOT, and make preparations to test failover communications/systems between Backup Control Centers and ERCOT if relocation becomes necessary. - Test all communications channels including Satellite phones prior to the hurricane making landfall. - Test their Communication with other TDSP's and QSEs prior to the hurricane making landfall. - File/update DOE Form 417 to Shift Supervisor ERCOT will continue to monitor the Storm and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch | Issue a Watch to all TOs when ERCOT has been notified of a confirmed time and location of Landfall affecting the grid reliability. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the [Hurricane] [Name] in the Gulf of Mexico expected to make landfall at <time>. TOs that are impacted are instructed to : - Restore any remaining outages that can be returned to service. Prepare to lose load and expect high voltage conditions as the [hurricane/tropical storm] approaches landfall. - Coastal TOs, in harm’s way are to report any transmission facility damage due to tidal surge or storm damage. - File/update DOE Form 417 to Shift Supervisor ERCOT will continue to monitor the Storm and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency | Issue an Emergency Notice when confirmation is received that adverse conditions such as Storm Surge or Hurricane force winds have moved inland and are affecting the grid reliability. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice adverse conditions such as Storm Surge or Hurricane force winds associated with the [Hurricane/] have moved inland and are effecting the grid along the Texas Coast TOs are instructed to : - Be preparing to lose load and expect high voltage conditions as the storm moves inland. - File/update DOE Form 417 to Shift Supervisor ERCOT will continue to monitor the Storm and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |

## 8.2	Severe Cold Weather

Procedure Purpose: To ensure ERCOT is prepared for Severe Cold Weather Operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | There is a severe cold weather system approaching with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing that has a possibility of impacting major metropolitan areas. ERCOT will issue the following notifications and instructions as conditions change. (http://www.noaa.gov) |
| NOTE |  | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| OCN |  | Using the Hotline, issue an OCN to all TOs when there is a severe cold weather system approaching with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing that has a possibility of impacting major metropolitan areas. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a severe cold weather system approaching with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing that has a possibility of impacting major metropolitan areas. - ERCOT will be reviewing planned outages associated with the impact of the approaching cold weather and existing outages for the possibility of restoring the outages on high priority equipment. TOs are instructed to: - Review emergency operating procedures and immediately notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the cold weather system and will convey information and instructions as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory |  | Using the Hotline, issue an Advisory to all TOs when the approaching cold weather system is expected enter the ERCOT service area, and will arrive with temperatures expected to be in mid to low 20°F range and maximum temperatures expected to remain near or below freezing impacting 50% or more of major metropolitan areas. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the approaching cold weather system is expected enter the ERCOT service area, and will arrive with temperatures expected to be in mid to low 20°F range and maximum temperatures expected to remain near or below freezing, ERCOT is continuing to review outages to determine their priority for restoration. TOs are instructed to: - Review emergency operating procedures and immediately notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the cold weather system and will convey information and instructions as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch |  | Using the Hotline, issue a Watch to all TOs when the cold weather system has entered the ERCOT service area, temperatures are in mid to low 20°F range and maximum temperatures will remain near or below freezing impacting 50% or more of major metropolitan areas. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the cold weather system that has begun to enter the ERCOT service area, temperatures are in mid to low 20°F range and maximum temperatures will remain near or below freezing impacting 50% or more of major metropolitan areas. TOs are instructed to : - Restore all outaged lines as appropriate and report back to ERCOT. - Review emergency operating procedures and immediately notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency Notice | Using the Hotline, issue an Emergency Notice when confirmation is received that the cold weather system is in the ERCOT service area and temperatures are in mid to low 20°F range and maximum temperatures are near or below freezing. The frigid temperatures are beginning to have adverse impact on the ERCOT System. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. The cold weather system is in the ERCOT service area, temperatures are in mid to low 20°F range and maximum temperatures are near or below freezing. The frigid temperatures are beginning to have adverse impact on the ERCOT System [state what the adverse impacts are]. - Prepare for higher than usual loads and the possibility of load shedding. - Review emergency operating procedures and immediately notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |  |
| Post | Issuance of an OCN, Advisory, Watch and Emergency Notice requires: - Posting on MIS Public using Notice Builder |  |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |  |

## 8.3	Other Significant Weather Events

Procedure Purpose:  Monitor severe weather conditions which can arise with little or no warning that can have an impact on the ERCOT grid.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: January 31, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Knowledge of a significant weather event that could or does require intervention to ensure system reliability, ERCOT will notify TOs through the use of MIS Public and Hotline. Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight line winds - Hail - Severe lightening - Flooding |
| OCN | Typical Script: “This call is for informational purposes and requires everyone to remain on the line until it is complete. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [OCN] due to [type of weather event] in the [location on the grid]. If you experience any transmission outages or significant loss of load as a direct result of the weather event, immediately notify ERCOT. |
| Posting | Within this procedure, the Resource Desk Operator (or as designated by the Shift Supervisor) is responsible for posting each Market Notification on MIS Public using Notice Builder. |
| Condition Termination | When the situation requiring the notification is relieved, notify TOs, via MIS Public using Notice Builder. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |