## Power Operations Bulletin # 523

ERCOT has posted/revised the NODAL Shift Supervisor Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.2	Capacity and Reserve Monitoring

Procedure Purpose:  To monitor capacity for SCED dispatch and total system capacity for providing Ancillary Services.

| Protocol Reference | 6.3.2(2) | 6.5.9.1(1)(a) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-01 R3.1, R4.2 | EOP-002 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-002 R5 | IRO-005-2 R1.4, R1.5 |

| Version: | 1 | Revision: | 2 | Effective Date: March 25, 2011 |
| --- | --- | --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Capacity Monitoring |  |
| 1 | Monitor the Excel MAI: IF: - Load forecast is reasonable AND “Adj. Max Capacity Room” shows insufficient capacity; THEN: - Verify that HRUC has identified the insufficient capacity situation. IF: - Load forecast is reasonable AND; THEN: - Verify that HRUC has identified the insufficient capacity situation. |
| 2 | IF: - HRUC has not identified the insufficient capacity; THEN: - Have RUC Operator verify that HRUC is using a reasonable forecast AND update if necessary, - Ensure Resource commitments are being made, if needed. |
| 3 | Triggers to deploy Non-Spin MONITOR: The Generation Area Status Page and the OpsMon Dashboard IF: - (HDL-GEN) ≤ 200 MW during normal ramps, AND - Avail_CAP_30Min ≤ 1000 - ; THEN: - Verify that the Resource Desk Operator has deployed half of available Non-Spin. IF: - (HDL-GEN) ≤ 200 MW during normal ramps, AND - Avail_CAP_30Min ≤ 500; THEN: - Verify that the Resource Operator has deployed all of available Non-Spin, IF: - Additional capacity is required, THEN: - Verify the RUC Operator is aware of the requirement to commit additional Resources for the next hour. |
| 4 | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue a VDI, instructing resources to be removed from service, - Priority should be on Resources that resolve congestion. |
| ### Reserve Monitoring |  |
| 1 | IF: - Physical Responsive Capability (PRC) is ≤ 3000 MW; VERIFY: - That an Advisory has been issued with Hotline call made and posting to the MIS Public. |
| 2 | IF: - Physical Responsive Capability (PRC) is ≤ 2500 MW; VERIFY: - That a Watch has been issued with Hotline call made and posting to the MIS Public, AND - Resource Operator has deployed enough Non-Spin to recover the PRC to 2500 MW or higher. |

## 5.3	Notification of a Protective Relay or Equipment Failure Report

Procedure Purpose:  Notification to support groups.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 6.2.3 | 6.2.4 |  |  |
| NERC Standard | PRC-001 R2.2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC | “If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible.” |
| 1 | Notify the shift engineer or the on-call engineer when notified that a protective relay or equipment failure reduces system reliability and there is no back-up protective relay available. A corrective action plan will need to be implemented to limit exposure to the BES. |
| 2 | - After notification from a TO or QSE, NOTIFY by e-mail: - OPS Support Engineering - OPS Planning - Shift Supervisors - The subject line of the e-mail should read “Protective Relay or Equipment Failure.” - Include in the e-mail: - Entity Name - Brief description - Contact information - Any significant information |
| 3 | If a TO or QSE e-mails a “Mis-Operation Relay form”, forward to the above identified e-mail address. |
| 4 | Log information available in the Log as time permits. |

## 5.5	Supervise Coordination with SPP and CFE

Procedure Purpose:  To ensure proper notification and coordination takes place.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R4.2, R4.3 | IRO-005-2 R1.9 | IRO-014 R1.1 | TOP-002 R4 |

| Version: 1 | Revision: 1 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The ERCOT ISO is only connected to another RC through asynchronous ties. The coordination and communication that must take place with SPP and CFE is outlined below. It is the responsibility of the Shift Supervisor to ensure this coordination takes place. - DC-Tie Tagging Activities - EEA Levels - Outages on DC-Ties - BLT’s - Arming of the Monticello SPS - ERCOT System Blackout Communications with CFE will be coordinated through AEP Corpus (Turret phone button labeled AEP TDSP). |
| 1 | Confirm that the DC Tie schedules and E-Tags were properly verified. Ensure that the “after-the-fact checkout” is performed each night and e-mailed to the appropriate entities as outlined in the DC-Tie Procedures. |
| 2 | ERCOT’s EEA status must be communicated to the SPP Reliability Coordinator (Turret phone button labeled SPP RC) as outlined in the DC-Tie procedures. |
| 3 | All planned and forced outages that affect the DC-Ties shall be coordinated with the Tie Operator(s) and SPP (if SPP DC-Ties affected). A message must also be posted on the MIS Public using Notice Builder for planned outages on any commercial DC-Ties. |
| 4 | Notify the SPP Reliability Coordinator when a BLT is initiated between ERCOT and SPP, as outlined in the Transmission & Security procedures. |
| 5 | Notify the SPP Reliability Coordinator when the Monticello SPS arms. If the SPS activates, the DC-E will trip. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Regional Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 6.3.(1) | 22 (B) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-002-2.1 R3, R6.3, R7.2 | EOP-004-1 R1, R3.1 | EOP-001-0 R4.1, R5 | IRO-014-1 R1.1.2 |
|  | IRO-015-2 R15 | TOP-002-2 R4 | DOE OE-417 |  |

| Version: 1 | Revision: 3 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template around 0300 – 0400 and again around 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - Conditions change that required new notices to be issued or cancelled (e.g., OCN , Advisory, Watch, or Emergency Notice ) - A projected reserve capacity shortage develops - Local reliability concerns arise including actual overloads or loss of load - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas restrictions, not expected to cause reliability issues - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Send updated report when conditions have returned to normal. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2A - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EEA Level 2A in effect Potential for EEA Level 2B - N/A – No EIL available - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 2B in effect Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - EEA Level 2B in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 3 in effect |  |
| ### Texas RE Event Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, within one hour: - COMPLETE the form located in Section 2.5 of the Desktop Guide:“Texas RE Event Form” - E-MAIL the form to Manager, System Operations - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis process, events include the following: Category 1 Events: - Loss of a bulk power transmission components(s) in response to a single-phase line-to-ground fault with delayed clearing (stuck breaker or protection system failure) - Simultaneous loss of three or more BPS elements (i.e. generators, transmission lines, and buses 100kV and above) (Combine Cycle Train counts as one element) - Frequency below the Low Frequency Trigger Limit (FTL) or above the High FTL for more than 15 minutes - Special Protection System (“SPS”) activation (only if generation was removed from system) - DC-Tie trips (loss of entire converter station) - Unintended system separation resulting in an island of up to 1,000 MW Category 2 Events: - Loss of an entire generation station of five or more generators (aggregate generation of 500 MW or higher)(Combine Cycle Train counts as one generator) - Loss of off-site power to a nuclear generating station - Loss of all BPS control center voice or data functionality for 30 minutes or more (Includes ERCOT, QSE or TO) - Unplanned evacuation from BPS control center facility (Includes ERCOT, QSE, or TO) - Unintended system separation resulting in an island of 1,001 MW to 4,999 MW Category 3: - Loss of load or generation totaling 1,000 MW or more (excluding SPS/RAP, UFLS, or UVLS actuation) - Unintended system separation resulting in an island of 5,000 MW – 10,000 MW Category 4: - Loss of load or generation totaling 5,0001 MW – 9,999 MW (excluding SPS/RAP, UFLS, or UVLS actuation) Category 5: - Loss of load or generation totaling 10,000 MW or more |  |
| NOTE | If an OE-417 or NERC Preliminary Report is required, notify Manager, System Operations. |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations or designee when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". |  |
| OE-417 Reporting Events | DOE OE-417 initial reports are to be completed within 1 hour, forms can be downloaded at: ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc OE-417 reports are required for the following events: - System wide voltage reduction of 3 percent or more - Public appeal to reduce the use of electricity - Load shedding ≥ 100 MW as a result of manual, underfrequency, or undervoltage load shedding - Uncontrolled loss of Firm Load ≥ 300 MW for 15 minutes or longer - Physical sabotage, terrorism or vandalism (suspected or real) - Cyber sabotage, terrorism or vandalism (suspected or real) - Fuel supply emergencies (fuel inventory ≤ 50% of normal) - Loss of electric service (≥ 50,000 for 1 hour or more) - Total system collapse |  |
| NERC IROL and Preliminary Disturbance Report EOP-004-1 | NERC Preliminary Disturbance reports are to be completed within 24 hours, forms can be downloaded at: http://www.nerc.com/page.php?cid=5¦66 NERC Disturbance reports are required for the following events: - Loss of generation ≥ 1,000 MW - IROL violation (self report) - Loss of major system component that significantly affect integrity of system - Voltage excursions equal to or greater than ±10 percent lasting more than five minutes - Loss of firm load demands totaling more than 200 MW or 50 percent of the total customers (applies to TOs) |  |
| 1 | When required to file a report (If Manager or designee is unavailable): Forward the TO or QSE report or the Director of Cyber Security’s report to: - NERC (esisac@nerc.com, fax (609) 452-9550) - DOE (doehqeoc@oem.doe.gov, fax (202) 586-8485) - “NERC and DOE Disturbance Reporting” e-mail list. |  |
| ### RCIS Reporting |  |  |
| NOTE | Refer to Section 2.2 in Desktop Guide: Operating State Alert Levels. |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” (ERCOT EEA Level 2A or 2B) - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| TEA Postings | There are four levels of Transmission Emergency Alert (TEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “System Emergency”: - “ERCOT is declaring TEA 1 on the North-Houston interface” - “ERCOT is declaring TEA 2 on the North-Houston interface; Load Resources have been deployed in the Houston area”. - “ERCOT is declaring TEA 3 on the North-Houston interface; firm load is being curtailed in the Houston area”. - “ERCOT is in TEA 0 and back to normal operations” |  |
| SEA Postings | There are four levels of Security Emergency Alerts (SEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “CIP Free Form”: - “ERCOT is declaring SEA 1 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 2 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 3 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is in SEA0 and no longer under threat”. |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2A, THEN: - Select the “SO EEA Level 2A” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2B, THEN: - Select the “SO EEA Level 2B” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2B” Scenario and activate notification, WHEN: - EEA Level 2B is terminated, THEN: - Select the “SO EEA Level 2B to EEA Level 2A” Scenario and activate notification, WHEN: - EEA Level 2A is terminated, THEN: - Select the “SO EEA Level 2A to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed, THEN: - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 2.7.8 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on P:\SYSTEM OPERATIONS drive in the PUCT Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” - The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| 1 | Weather Information - Enter the High and Low temperature forecast from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Enter the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Enter the Previous Day Actual MW. |  |
| 3 | Interchange - Enter the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Enter the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals - Enter the Generation scheduled outage MW total. - Enter the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves - Enter the Responsive Reserve requirement at the Project Peak. - Enter the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity - No action needed |  |
| 8 | Comments - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically during the day, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | When alerts and warnings for GMDs are issued for K-7 or higher: - Notify the TOs and QSEs by posting message on MIS Public using Notice Builder, Log the information. |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |

## 7.2	EEA Implementation Checklist

shift Supervisor – EEA IMPLEMENTATION Check List

| Time | Action | Comment |
| --- | --- | --- |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - MIS messages posted |  |
|  | - SPP/CFE Updated |  |
|  | - NXT System activated |  |
|  | - RCIS Posting |  |
|  | EEA Level 1 Implementation | PRC <2300 MW |
|  | - Non-Spin deployed |  |
|  | - Resource testing suspended |  |
|  | - Online RMRs loaded to full output |  |
|  | - Emergency Energy Procedures implemented across CFE DC-Ties |  |
|  | - EEA 1 Schedule requested across SPP DC-Ties |  |
|  | - Verbal RUC issued |  |
|  | - Settlements VDI issued |  |
|  | - Inquire about BLT availability |  |
|  | EEA Level 2A Implementation | PRC <1750MW |
|  | - Load Resources deployed - Block 1 (<1750MW) - Block 2 (as needed) - Both (<1400MW) - Settlements VDI issued |  |
|  | - Emergency Energy Procedures implemented across SPP DC-Ties |  |
|  | - Notify TO’s of Load Resource deployment |  |
|  | - BLTs initiated if available |  |
|  | - Distribution voltage reduction as appropriate |  |
|  | - Verify with Manager that appeals for voluntary energy conservation through the public news media are enacted |  |
|  | - Verbal RUC for non-utilized remaining capacity |  |
|  | - Settlements VDI issued |  |
|  | EEA Level 2B Implementation | Load Resources-RRS deployed & EILS procured & unable to maintain Freq at 60.00 Hz |
|  | - EILS deployed (if procured) - Settlements VDI issued |  |
|  | - Notify TO’s of EILS deployment |  |
|  | EEA Level 3 Implemention | Unable to maintain Freq at 59.8 Hz. |
|  | - Firm Load shed ordered (100 MW blocks) |  |
|  | - Notify QSE’s of Firm Load shed |  |
|  | - Load shed achieved |  |
|  | - NERC Report (Verify Manager will do) |  |

## 7.3	EEA Restoration Checklist

Shift Supervisor – EEA Restoration Check List

| IMPORTANT: If the EEA event coincides with a severe weather event that resulted in the loss of residential load as well as the ERCOT directed shedding of firm load, COORDINATE load restoration with the appropriate Transmission Operator to insure lost residential load is given priority over the shed load. |  |  |
| --- | --- | --- |
| Time | Action | Comment |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - MIS messages posted |  |
|  | - SPP/CFE updated |  |
|  | - NXT System activated |  |
|  | - RCIS Posting |  |
|  | RESTORE FIRM LOAD | Sufficient Regulation exist to control to 60 Hz & PRC from generation >1354 MW |
|  | - Firm load restoration directed |  |
|  | - Notify QSEs of Firm load restoration |  |
|  | EEA LEVEL 3 TO EEA LEVEL 2B | Sufficient Regulation exist to control to 60 Hz & PRC from generation >1354 MW while Load Resources are being recalled |
|  | - Begin recalling Load Resources recalled (may also recall EILS) |  |
|  | - Distribution voltage reductions measures recalled |  |
|  | EEA Level 2B to EEA LEVEL 2A | Sufficient Regulation exist to control to 60 Hz & PRC > 1750 MW |
|  | - Verify with Manager that voluntary energy conservation is being terminated |  |
|  | - Begin recalling EILS if not already done |  |
|  | - Notify TO’s of Load Resource and EILS recall |  |
|  | EEA Level 2A TO EEA LEVEL 1 | PRC > 2300 MW & all Load Resources and EILS have been instructed to restore |
|  | - Block Load Transfers (if implemented) restoration has been directed |  |
|  | - EILS recalled if not already done |  |
|  | - Notify TO’s of EILS recall |  |
|  | EEA Level 1 TO EEA 0 | PRC > 2300 MW & all Load Resources and EILS have been instructed to restore |
|  | - End any emergency across DC Ties |  |
|  | - Release any RUC committed Resources |  |
|  | - See Administrative Tasks |  |

## 9.2	Monthly Test of Non-Routinely used Telecommunications Facilities

Procedure Purpose: To ensure backup communications are tested monthly.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1 R2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March, 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Primary Control Center |  |
| Phone Tests | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday: - Test the Control Room Cell Phone by calling the ERCOT Helpdesk Cell Phone. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Standalone Satellite phone. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to Section 8.7.4 in the Desktop Guide. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| SAT modem testing | Coordinate the following test with the DC Tie Operator at the alternate control center - Using the turret, call each programmed desk SAT Phone at the alternate control center - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| NXT Test | - Test NXT Communicator by activating the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log the results for each of the bulleted items above in the Shift Supervisors Operations Log. |
| Alternate Control Center |  |
| Phone Tests | - When working out of the alternate Control Room during the monthly scheduled dates: - Test Control Room Cell Phone with the ERCOT Helpdesk Cell Phone. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Satellite phone associated to the Operations Desk on each turret. It isn’t necessary to call a satellite number, just verify the phones are operational. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Standalone Satellite phone operation located in the Control Room. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to section 8.8.4 in the Desktop Guide. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| SAT modem testing | Coordinate the following test with the DC Tie Operator at the other control center - Using the turret, test call each programmed SAT Desk Phone at the other control center - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| NXT Test | - Log into the Austin ENS link when working out of the alternate Control Room in Austin, - Test NXT Communicator by activating the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log the results for each of the bulleted items above in the Shift Supervisors Operations Log. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |