## Power Operations Bulletin # 525

ERCOT has posted/revised the NODAL Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.3	Responding to Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.9.4.1 | 6.5.9.4(5) | 6.5.7.6.2.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.1(1) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002 R2.4 | EOP-001 R3.1 | EOP-002 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005-2 R1.4, R1.5, R4 |

| Version: 1 | Revision: 2 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at management’s discretion, may issue an appeal through the public news media for voluntary energy conservation at any time. - System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. - If Non-Spin Reserve Service is being deployed at any time other than the top of the hour (less than 12 consecutive 5-minute intervals), deselect any Resources whose COP Non-Spin Resource Responsibility is “ZERO” for subsequent hours. |
| ### Advisory |  |
| 1 | IF: - Physical Responsive Capability falls below 3000 MW; THEN: - Coordinate with the Real Time Operator, AND - Post on MIS Public using Notice Builder. Typical posting: “ERCOT is issuing an Advisory for Physical Responsive Capability less than 3000 MW.” |
| 2 | Make log entry. |
| ### Watch |  |
| 1 | IF: - Physical Responsive Capability falls below 2500 MW; THEN: - Coordinate with the Real Time Operator and Transmission Operator, AND - Utilize Non-Spin that can be deployed to increase the Physical Responsive Capability (see Section 6.2 in Desktop Guide), - Post on MIS Public using Notice Builder. Typical postings: “ERCOT is issuing a Watch for Physical Responsive Capability less than 2500 MW”. “ERCOT is deploying Non-Spin Reserve”. |
| 2 | Make log entry. |
| ### Cancelation |  |
| 1 | IF: - (HDL-GEN) ≥ deployed Non-Spin plus 500 MW, AND - Physical Responsive Capability is ≥ 3000 MW; THEN: - Coordinate with the Real Time Desk and recall Non-Spin by sending a Zero MW XML (Refer to Desktop Guide section 6.2 “Recall All Non-Spin or Partial Non-Spin Recall”), AND - End messages on MIS Public using Notice Builder. |

## 3.4	Responding to Capacity Shortages

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Capacity Shortages as requested by the Real-Time Operator.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 25 , 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If Non-Spin is being deployed at any time other than the top of the hour (less than 12 consecutive 5-minute intervals), deselect any Resources whose COP Non-Spin Resource Responsibility is “ZERO” for subsequent hours. (Refer to Desktop Guide section 6.2 “Non-Spin Deployment and Recall”) |
| Deployment | WHEN: - Notified by the Real-Time Operator to deploy Non-Spin for capacity shortages; THEN: - Coordinate with the Transmission Operator to verify the Non-Spin doesn’t create congestion, - Deploy Non-Spin, (Refer to Desktop Guide section 6.2 “Deploy All Non-Spin or Partial Non-Spin deployment”), - Notify the RUC Operator of the deployment, - Post as “Operational Information” message on MIS Public using Notice Builder. Typical posting: “ERCOT is deploying Non-Spin Reserve”. |
| Termination | WHEN: - Notified by the Real-Time Operator that the Non-Spin Reserve Service is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide section 6.2 “Recall All Non-Spin or Partial Non-Spin Recall”), AND - Cancel message on MIS Public using Notice Builder. |

## 3.7	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R2, R4.2 | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 |
|  | IRO-004 R3 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 4 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Deploy Non-Spin & Post | WHEN: - Notified by the Transmission Operator to deploy Non-Spin in the Houston area for the North-Houston Interface; THEN: - Deploy Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) (Refer to Desktop Guide section 6.2 “Partial Non-Spin deployment”) - Post on MIS Public using Notice Builder. Typical posting: “ERCOT is issuing a Watch for the North to Houston interface and deploying Non-Spin Reserve to specific resources”. |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| Deploy Load Resources & Post | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Deploy Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by XML (Refer to Desktop Guide section 6.1 “Deployment for Congestion/IROL”) - Post on MIS Public using Notice Builder. Typical posting: “ERCOT is issuing an Emergency Notice for the North to Houston interface and deploying specific Load Resources”. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Recall Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML (Refer to Desktop Guide section 6.1 “Recall (Full or Partial)”) - Cancel message on MIS Public using Notice Builder. |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Recall Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML, (Refer to Desktop Guide section 6.2 (“Partial Non-Spin Recall”) - Cancel message on MIS Public using Notice Builder. |
| Log | Log the actions taken. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 6.4.8.1 | 6.4.8.1.1 | 6.4.8.1.2 | 6.4.8.1.3 |
| --- | --- | --- | --- | --- |
|  | 3.16 (4) | 6.4.8.2 | 6.4.8.2.2 | 6.5.9(4) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - Once the notice is given, no further offers are eligible for that SASM. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services will have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify with the RUC Operator that the Hotline call notifying the Market that the DAM failed, - Make the following hotline notification before opening the SASM, - Procure all Ancillary Services for the next operating day through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.4 of the Desktop Guide: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx] ERCOT will be opening a SASM to procure all Ancillary Services for [operating day] due to the Day-Ahead Market failure. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline Notification and post message on MIS Public using Notice Builder, - Procure more Ancillary Services through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.3 of the Desktop Guide. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch due to the need to increase the system wide A/S requirement above what was procured in the Day-Ahead Market due to [state the reason]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | Once verified that all Ancillary Service has been procured, cancel the Watch: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace AS capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the Ancillary Service capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to section 6.7.1 in the Desktop Guide). |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Discuss with Shift Supervisor of the need to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| Replacement of Ancillary Services in Real Time |  |
| NOTE | When issuing a VDI to a Resource for Real Time A/S insufficiency, ensure the QSE understands the unit is being brought online to provide an A/S. Also verify the QSE’s COP is updated when the unit is online. |
| 1 | IF: - A Real Time A/S shortage exists, AND - It is determined to be a reliability issue; THEN: - Issue a VDI to commit an off-line Resource that is qualified to provide the insufficient A/S in the time frame needed (Refer to the SASM section 6.7.5 of the Desktop Guide). - Choose “COMMIT” as the Instruction Type from Resource Level - In text, state “commit for replacement of [A/S type]” |
| NOTE | The QSE will need to telemeter the Resource status as “ONREG”. |

## 7.1	Market Notices

Procedure Purpose:  Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - There is a Tropical Storm/Hurricane in the Gulf, either entering the Gulf or a newly formed storm projected to impact Texas. - A cold front is approaching with temperatures anticipated to be in mid to low 20o F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas. - Wet weather, such as a tropical storm making land fall. - Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Tropical Storm/Hurricane currently projected to impact Texas. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Hurricane in the Gulf with expected landfall in Texas affecting the grid reliability. - A cold front has arrived with temperatures anticipated to be in mid to low 20°F range and maximum temperature expected to remain near or below freezing impacting 50% or more of major metropolitan areas - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT varies from time-line for DRUC/HRUC. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT unable to approve DRUC/HRUC or failure of DRUC/HRUC/SCED. |
| ### Scripts |  |
| Hotline | Hotline calls are usually made by Real-Time Operator, the scripts below are for reference if needed: Notify QSEs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the only option is “public” - For “free form” messages, the “Notice priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added noteUpdated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |