## Power Operations Bulletin # 534

ERCOT has posted/revised the Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.8	Deploying Non-Spin for Local Congestion

Procedure Purpose:  Mitigating local congestion.

| Protocol Reference | 6.1 (3) | 6.5.1.2 (1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: May 11, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | WHEN: - Notified by the ERCOT Transmission and Security operator that specific Resources carrying Non-Spin are needed for local congestion; THEN: - Deploy specific Resources |
| POST | Post message on MIS public utilizing Notice Builder. Typical Posting: ERCOT is deploying Non-Spin Reserve for XXXX constraint. |
| CANCEL POSTING | WHEN: - Non-Spin is no longer needed to solve congestion, THEN: - Cancel the MIS message. |
| LOG | Log actions. |

## 3.9	Quick Start Generation Resource

Procedure Purpose:  Understanding Quick Start Generation Resources.

| Protocol Reference | 3.8.1 | 3.8.2 | 3.8.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: May 11, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| QSGR | A Generation Resource that while in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test which establishes the amount of capacity that can be deployed within a ten minute period. |
| COP | The QSE for a QSGR that is available for deployment by SCED shall set the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spin service, then the A/S Resource Responsibility for Non-Spin shall be set to the Resource’s Non-Spin obligation in the COP. If the Resource’s Non-Spin obligation is less than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP Resource Status to ON, otherwise it shall be set to OFFNS. |
| Telemeter | The QSGR shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED. |
| SCED | IF: - A QSGR requests a manual override within the first ten minutes after the SCED time stamp; THEN: - Manually override the Resources LDL to a level equal to the COP LSL, - Release after a couple of intervals. This should only be done until the Resource is operating at or above their COP LSL. |
| Log | Log all actions taken as necessary. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 6.4.8.1 | 6.4.8.1.1 | 6.4.8.1.2 | 6.4.8.1.3 |
| --- | --- | --- | --- | --- |
|  | 3.16 (4) | 6.4.8.2 | 6.4.8.2.2 | 6.5.9(4) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: May 11, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - Once the notice is given, no further offers are eligible for that SASM. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services will have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify with the RUC Operator that the Hotline call notifying the Market that the DAM failed, - Make the following hotline notification before opening the SASM, - Procure all Ancillary Services for the next operating day through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.4 of the Desktop Guide: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx] ERCOT will be opening a SASM to procure all Ancillary Services for [operating day] due to the Day-Ahead Market failure. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline Notification and post message on MIS Public using Notice Builder, - Procure more Ancillary Services through a Supplemental Ancillary Services Market (SASM). Refer to Section 6.7.3 of the Desktop Guide. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch due to the need to increase the system wide A/S requirement above what was procured in the Day-Ahead Market due to [state the reason]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | Once verified that all Ancillary Service has been procured, cancel the Watch: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace AS capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the Ancillary Service capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to section 6.7.1 in the Desktop Guide). |
| 2 | IF: - SASM did not procure the amount of AS requested; THEN: - Discuss with Shift Supervisor of the need to replace the remaining insufficiencies in the next HRUC. |
| 3 | IF: - A QSE is unable to provide their SASM awards; THEN: - Determine if there is time to open an additional SASM, AND - Send failure to provide notification. |
| 4 | Prepare email with the following information: - SASM ID - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 5 | Send information in an email to the following distribution list: - SASM |

## 8.1	Weekly Hotline Test

Procedure Purpose: To perform a weekly communication test of the ERCOT Hotline phone system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.1.3(3) |  |  |  |
| NERC Standard | COM-001-1.1 R2 | EOP-005-1 R5 |  |  |

| Version: 1 | Revision: 1 | Effective Date: May 11, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | In the event of a failure of the Forum Conference Client software, the most recent printout of the Hotline log may be used to perform a manual roll call of QSEs/ TOs. |
| 1 | Each Monday between 0630 and 1100 test the ERCOT Hotline |
| 2 | Using the Hotline, notify all QSEs/TOs of the purpose of the call. - When QSEs/TOs have answered the Hotline, print Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This is ERCOT Operator [first and last name]. ERCOT is conducting the weekly [QSE/TO] Hotline test. The following notices are currently in effect: - List OCNs, Advisories, Watches and/or Emergency Notices in effect. - State “None” if none are in effect. This ends the test of the ERCOT Hotline. That is all.” |
| 3 | Notify the Shift Supervisor of any QSE or TO that did not respond to the Hotline test. The Shift Supervisor and/or the Help Desk may notify the telecommunications department for repairs. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasability/Failure to Provide, deleted Replacment of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |