## Power Operations Bulletin # 535

ERCOT has posted/revised the DC Tie Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Approve E-Tags for the SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-2 R1.2 | INT-005-2 R1 | INT-006-2 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | TOP-002-2 R5, R9 |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - AEP TOP located in Ohio is the DC Tie Operator (AEP DCT) for the DC_E (East tie) and DC_N (North tie) - If either DC Tie is over-scheduled, contact SPP Tariff (SPP TAR) |
| NOTE | ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties. |
| NOTE | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria used to automatically validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCOT specified in the Physical Path If either of the above validations fail, the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSEs. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the OATI help desk. WebTrans Reference Display: Tag >Validation Summary Scheduling>QSE Summary |
| 1 | When a New or Updated E-Tag is received in WebTrans system: 1.1 Manually validate the following: - “ERCO” must not be listed as a PSE in Tag Information or Physical Path. - Time Zone should be CS (central standard) or CD (central daylight) - “Transaction type” must be “Energy or Normal” - “ERCOT-E” or “ERCOT-N” must be selected for the correct POR (Point-of-Receipt) or POD (Point of Delivery) in the Physical Path. - “CSWS” must be included as a Scheduling Entity on the SWPP TP row in the Physical Path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the Physical Path. (Note: If CSWS is listed in both the TP and GCA or LCA, this will cause double counting in the Tie Operators net-scheduled value so the “before the start of the hour” check out will not match. These type tags should be denied). - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section. - Start Time and Stop Time MUST NOT cross the midnight hour If any of the above information is incorrect, deny the E-Tag, otherwise go to Step 1.2. 1.2 If one or more E-Tags are submitted that will cause the DC Tie to be overscheduled: - Contact SPP Tariff (SPP TARF) approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule; they will take action to correct the over-schedule. If the correction is not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. - IF ERCOT curtails an E-Tag due to an over-schedule that was not corrected in time, contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| NOTE | If verification needs to be made in the current day HRUC will be used unless it is a current hour tag. If verification needs to be made for the next day DRUC will be used. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. OATI: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS by - going to the MI COP display and filter ‘ERCOT’ as the QSE name. |

## 3.2	Import and Export Limits for the CFE DC Ties

Procedure Purpose: To confirm the import and export limits of the CFE DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 8 , 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Daily import and export limits for the Railroad and Eagle Pass DC Ties, and Laredo VFT will be provided by the Operations Engineering Support Group on the “Transmission Limits to Be Monitored” sheet. MIS Secure>GRID>Transmission>Generic Transmission Limits If the limits are not posted, notify the ERCOT Shift Engineer. |
| 1 | Once the DC-Tie limits for next day are received, verify the sum of the E-Tags do NOT exceed the import/export limits on any DC-Tie. If so, contact the PSE of the last E-Tag received and request adjustments to be made. |
| 2 | Coordinate with the ERCOT Transmission & Security Operator to ensure the import and export limits are updated in RTMONI hourly. EMS>EMP Applications>RTMONI Constraints Monitoring>Monitor Displays>Real Time Monitoring Groups Dir>DC_Ties |

## 3.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-2 R1.2 | INT-005-2 R1 | INT-006-2 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | IRO-005-2 R2 | TOP-002-2 R5, R9 |  |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | AEP TO in Corpus Christi is the DC Tie Operator (AEP TDSP) for the DC_R (Railroad DC tie), DC_S (Eagle Pass DC tie), and the DC_L (Laredo VFT). All communications will be with the DC-Tie Operator and they will communicate with CFE. |
| NOTE | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC-Tie schedules are seen by our EMMS as a generator (import) or load (export). |
| NOTE | - ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties - The Railroad DC-Tie has a 15 MW minimum flow requirement, if E-Tags are scheduled - Approximately one hour before start of schedule, notify the ERCOT Transmission & Security Operator with scheduled MW, Tie and direction of flow and duration. |
| NOTE | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria ERCOT uses to validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCOT specified in the Physical Path If either of the above validations fail, the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the OATI help desk. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Summary Data>QSE Contracts |
| 1 | When a New or Updated E-Tag is received in the WebTrans system: - Manually validate the following: - “ERCO” must not be listed as a PSE in the Tag Information or Physical Path. - Time Zone should be CS (central standard) or CD (central daylight) - “Transaction type” must be “Energy or Normal” - AEPT must be included as a TP (Transmission Provider) in the Physical Path and ERCO as a Scheduling Entity on the AEPT TP row in the Physical Path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start Time and Stop Time must NOT cross the midnight hour If any of this information is incorrect on the E-Tag, deny the E-Tag, otherwise go to Step 1.2. - If one or more E-Tags are submitted that will cause the DC Tie to exceed the import/export limit for the tie: - Contact the DC Tie Operator approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule - Call the PSE to have the E-Tag modified, if modification is not done 20 minutes before the start of the ramp then; - Curtail the E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the import/export limit for the tie. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| 2 | The ramp rate for DC_R will be 50 MW per minute due to reactive issues on the CFE side. DC_L and DC_S will be ramped across a 10 minute window. - Ramp Duration should be filled out on DC_R E-Tags only - Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered - DC_L and DC_S ramp duration can remain blank |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. WebTrans: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS - by going to the MI COP display and filter ‘ERCOT’ as the QSE name |

## 3.4	Adjustment of SPP DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-Tags.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the Net Scheduled Interchange (NSI). |
| 1 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each SPP DC Tie (DC_E/DC_N) affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 3.5	Curtailment for the SPP DC Ties

Procedure Purpose: The process to curtail E-Tags for the SPP DC Ties

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | INT-005-2 R1.1 | INT-010-1 R2 | IRO-006-5 |  |

| Version: 1 | Revision: 2 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| 1 | IF: - A curtailment alarm is received in WebTrans, AND complying with the request will NOT put ERCOT in an unreliable state (such as EEA or IROL exceedance); THEN: - Approve the E-Tag curtailment. IF: - A curtailment alarm is received in WebTrans, AND complying with the request WILL put ERCOT in an unreliable state (such as EEA or IROL exceedance); THEN: - Deny the E-Tag, stating the reason on the tag, AND - Call SPP RC and provide reliability reason for denying the request. Webtrans Reference Displays: Tag Validation Summary Tag Approval Monitor |
| NOTE | IRO-006-5 R1 applies to requests from RCs, BAs, or TOPs from another Interconnection. If the request comes from one of those entities from another Interconnection, call the requesting entity and provide the reliability reason for not approving curtailment tag as well. |
| 2 | If a QSE or SPP Tariff desk requests an E-Tag be curtailed or adjusted for any reason, curtail the E-Tag to 0 (zero). |
| NOTE | E-Tag curtailments must be in an “Approved” or “Implemented” status to be calculated into the Net Scheduled Interchange (NSI). |
| 3 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each SPP DC Tie affected by E-Tag curtailments. WebTrans Reference Display: Realtime Summary |

## 3.6	Adjustment of CFE DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-Tags.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 |  |  |  |
| NERC Standard | INT-004-2 R1 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Imports |  |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the Net Scheduled Interchange (NSI). |
| 1 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |
| ### Exports |  |
| 1 | Notify the ERCOT Transmission & Security Operator when E-Tag Net Export adjustments are greater than 100 MW during the Adjustment Period. |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the Net Scheduled Interchange (NSI). |
| 2 | IF requested by the DC Tie Operator, checkout the Net Scheduled Interchange (NSI) value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 3.7	Curtailment for the CFE DC Ties

Procedure Purpose: The process to curtail E-Tags for the CFE Ties.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | INT-004-2 R1 | INT-005-2 R1.1 | INT-010-1 R2 |  |

| Version: 1 | Revision: 3 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE | Scheduling limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. After receiving the import/export limits for next day, it may be necessary to have the PSE adjust E-Tags. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific amount, only CFE needs to approve the change. Adjustments are done by the PSE which requires all parties to approve. If it is after hours, CFE cannot approve adjustments. Curtailments will be automatically approved by them. |
| ### DC-Tie Trips |  |
| 1 | If any of the CFE DC-Ties trip, ERCOT will have the responsibility to curtail the E-Tags. - Curtail the E-Tags, - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE if not already done. |
| 2 | Once the DC-Tie that tripped is operational, re-load the curtailed E-Tag(s), if applicable: - Re-load curtailed E-Tag(s), - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE to approve re-loads if not already done. |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| ### Transmission Issues Within ERCOT |  |
| 1 | Due to ERCOT transmission issues it may be necessary to curtail E-Tag(s) using the Last-in-First-Out (LIFO). If an E-tag needs to be cut immediately, ERCOT must declare a Transmission Watch: - Identify from ERCOT Transmission & Security Operator if at least 20 – 30 minute notice can be given for curtailment - Curtail the appropriate E-Tag(s) - Contact DC Tie Operator (AEP TDSP) with curtailment information - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE if not already done. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] DC-Tie starting at [xx:xx] due to transmission issues. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank You” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Once notified that transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s), - Ensure DC Tie Operator (AEP TDSP) sees the re-loaded E-Tags, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE to approve re-loads if not already done. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. At [xx:xx], the transmission issues within ERCOT have been resolved and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CFE to approve re-loads. Please repeat this back to me. That is correct. Thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. Repeat the steps above as necessary to get the tag(s) re-loaded. |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| ### Transmission Issues within CFE |  |
| 1 | Due to CFE transmission issues it may be necessary to curtail E-Tags using the Last-in-First-Out (LIFO). If notified by the DC Tie Operator or the ERCOT Transmission & Security Operator of CFE’s situation: - Identify if at least 20 – 30 minute notice can be given for curtailment - Curtail the appropriate E-tag(s) - Contact DC Tie Operator (AEP TDSP)with curtailment information - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE if not already done. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] DC-Tie starting at [xx:xx] due to issues within CFE. Please ramp the Tie accordingly. Please repeat this back to me. That is correct.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | If CFE curtails schedules for their transmission issues: - Once curtailment is received from Webtrans, approve AND - Notify DC Tie Operator (AEP TDSP) that they see the curtailment and will ramp the DC-Tie accordingly. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. At [xx:xx] CFE has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to transmission issues within CFE. Please ramp the Tie accordingly. Please repeat this back to me. That is correct. Thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Once notified that transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s), - Ensure DC Tie Operator (AEP TDSP) sees the re-loaded E-Tags, AND - Instruct the DC Tie Operator (AEP TDSP) to make notification to CFE to approve re-loads if not already done. Repeat the steps above as necessary to get the tag(s) re-loaded. |
| 4 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, - Call the DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |

## 3.8	Managing Daily Inadvertent Energy for the SPP DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.1b R12.1 | INT-003-2 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 2 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored frequently during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ERCOT-E or ERCOT-N). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| - NOTE | Due to the DC_N deadband issue, if the net schedule on the North DC-Tie is less than 25 MW, the DC-Tie Operator has the option of: - Automatically flow 25 MW in the default direction of the DC Tie, OR - Add MW flow in the direction of the schedule. IF: - The deadband is creating a transmission issue; THEN: - Contact AEP DC Tie Operator (AEP DCT) - Explain the problem - Request the deadband flow direction be changed to alleviate the problem. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP DCT). If there is a discrepancy, go over each. E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag cannot be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>Interchange>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP DCT) for each DC Tie: - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 10MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10MWH or more and the reason is known (database load, loss of ICCP, AEP automatically overriding the schedule on the North DC Tie, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Inadvertent>ATF |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator (AEP DCT): IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for both the DC_E and DC_N - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator - Click the “Apply Checkout” button. - If asked to change a scheduled value, log the appropriate information and email it to the Manager of System Operations. - If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_N and DC_E and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - aepcheckout-west@aep.com |

## 3.9	Managing Daily Inadvertent Energy for the CFE DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.1b R12.1 | INT-003-2 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 1 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ROAD_DC, EGPS_DC, or LAR_VFT). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| - 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP TDSP). If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP TDSP) for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 5 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Production Group to investigate problems with the meter information. WebTrans Reference Displays: Tie Data ATF |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator (AEP TDSP): IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_L, DC_R and DC_S - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_S, DC_R and DC_L DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

## 3.10	Managing Inadvertent Energy Payback

Procedure Purpose: To provide communication contacts and information prior to starting and ending inadvertent payback.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 (3) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Payback will only be planned when there is room on the DC Tie(s). Energy schedules of market participants will supersede any inadvertent payback bias. Payback plans are implemented by each of the DC Tie Operators. They will bias the DC Tie(s) and create inadvertent in the opposite direction. This will reduce the inadvertent values. |
| NOTE | When inadvertent needs to be paid back in either direction, the ERCOT Operator will receive the payback plan information from the Manager of System Operations or designee. |
| - 1 | - Prior to the start of the Payback plan, call the appropriate DC Tie Operator and confirm the start time, hourly MW amount, and direction of the payback plan. - If payback is planned across the DC_L, verify the transmission path (230kV or 138kV). |
| 2 | Prior to the Payback plan stopping, call the appropriate DC Tie Operator and confirm the agreed upon stop time. |

## 3.11	Loss of E-Tagging

Procedure Purpose: Contingency plan for loss of E-tagging capability

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | If the WebTrans system goes down for an unknown reason (i.e. maintenance), contact the ERCOT Operator at the primary control center to check on their connectivity. If their system is also down, contact the OATI helpdesk (OATI HELP) to see if the issue is on their end. If issue is not on the OATI end, contact the ERCOT helpdesk (HELP DESK). |
| 2 | Determine the estimated down time, if longer than 30 minutes, notify the SPP Tariff Operator (SPP TARF) and the DC-Tie Operators (AEP DCT/AEP TDSP). |
| 3 | Post message on MIS Public utilizing Notice Builder: Typical Posting: “ERCOT ISO E-tagging system is down; we are unable to accept new schedules across the DC-Ties at this time”. |
| 4 | No new E-tags will be accepted, only curtailments: - Coordinate with the SPP Tariff Operator (SPP TARF) and the appropriate DC-Tie Operator - Notify Real-Time Operator to determine if SCED needs to be manually executed for curtailments |
| NOTE | Before-the-fact and after-the-fact check outs will not be available |
| 5 | Once the WebTrans system is available, confirm SPP Tariff (SPP TARF) and the DC-Tie Operators availability. If available for all parties: - Update the MIS Public posting by sending a “Notice Cancellation” If curtailments were made while the WebTrans system was down, ensure E-tags are updated |

## 4.1	Emergency Energy from CFE

Procedure Purpose: Steps to secure emergency energy across the CFE DC Ties when ERCOT has declared a Transmission Watch, Emergency or EEA.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - The DC Tie operator for the CFE ties can be reached using the Turret phone button labeled (AEP TDSP) on page 2 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to. They can be reached using the Turret phone button labeled (AEP QSE) on page 2. |
| Transmission Issues | ERCOT must declare a Transmission Watch or a Transmission Emergency and make the proper posting/hotline calls when receiving emergency energy from CFE, whether it is for transmission issues or an EEA situation. This is done by the ERCOT Transmission/Real-Time Operators. Once notified of the emergency energy need, proceed with this procedure. |
| EEA | When notified by Hotline that ERCOT has implemented an EEA level, proceed with this procedure. |
| 1 | Verify each bullet (remembering 3-part communication): - Curtail any export E-tags to CFE (notify DC-Tie Operator) (see section 4.3 in Desktop Guide if needed) - Stop export inadvertent payback (contact DC-Tie Operator) - If there is import capacity room on any CFE DC-Tie(s), contact DC-Tie Operator and request that they contact CFE to see if emergency energy is available - If emergency energy is available, contact the ERCOT Transmission & Security Operator or review the CFE DC Tie Limits, determine the DC-Tie(s), MW amount, time and duration (when possible) and procure the appropriate MW amount available - Request DC-Tie Operator to ramp the appropriate DC-Tie with the emergency energy - Notify Shift Supervisor and Real-time Operator, SCED may need an off-scheduled run - Issue AEP QSE a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State which DC-Ties in Other Information - End time will be the same as initiation time (back office will take care of the rest) |
| Log | Log all actions taken. |

## 4.2	EEA 1 Schedule from SPP

Procedure Purpose: Steps to secure a schedule across the SPP DC tie(s) in an Energy Emergency Alert 1.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |
|  | IRO-006-5 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Met Center Turret Phone | - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC) on page 1 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP TAR) on page 1 - The DC Tie operator for the SPP DC-Ties can be reached using the Turret phone button labeled (AEP DCT) on page 6 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to. They can be reached using the Turret phone button labeled (AEP QSE) on page 2 |
| NOTE | For an EEA 1, only non-firm transmission service is available. For EEA 2 or 3, emergency transmission service is available. This is the reason for the two different procedures. |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. |
| 1 | IF: - There are export E-tags across the DC Ties, THEN: - Curtail (usually done one hour at a time) IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag, - Notify the Shift Supervisor |
| 2 | IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DCT). |
| 3 | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. We will inquire about the availability of transmission service, please transfer me to the Tariff desk.” |
| 4 | Notify the SPP Tariff desk (SPP TARF) to determine the availability of transmission service across the SPP DC-Ties for an EEA 1 schedule. Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie to start a schedule into ERCOT?” If no current hour transmission service is available, do not proceed and make log entry. If status changes from EEA 1 to EEA 2A, 2B, or 3 proceed to Section 4.3 Only continue to the next step if there is transmission service available |
| 5 | Notify AEP QSE (AEP QSE): Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” If no available capacity, do not proceed and make log entry. If there is available capacity (procure whatever amount is available), ask AEP QSE to arrange for the submission of the transmission request and the E-tag(s). |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 6 | If ERCOT will be receiving an EEA 1 schedule, notify the DC Tie Operator (AEP DCT): Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and the E-Tag (s) for an EEA 1 schedule. |
| 7 | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State which DC Ties in Other Information - End time will be the same as initiation time (back office will take care of the rest) |

## 4.3	EEA 2 or 3 Emergency Energy from SPP

Procedure Purpose: Steps to secure emergency energy across the SPP DC tie(s) in an Energy Emergency Alert 2 or 3.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |
|  | IRO-006-5 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Met Center Turret Phone | - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC) on page 1 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP TAR) on page 1 - The DC Tie operator for the SPP DC Ties can be reached using the Turret phone button labeled (AEP DCT) on page 6 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to. They can be reached using the Turret phone button labeled (AEP QSE) on page 2 |
| NOTE | - For an EEA 1, only non-firm transmission service is available. For EEA 2 or 3, emergency transmission service is available. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| EEA | If ERCOT goes directly to an EEA 2A, 2B or 3 OR if an EEA 1 schedule was unsuccessful, proceed with the steps below (only mention EEA 2, leave A/B off of communications) |
| 1 | IF: - There are export E-tags across the DC Ties; THEN: - Curtail (usually done one hour at a time). IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag, Notify the Shift Supervisor. |
| 2 | IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DCT). |
| 3 | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA status: Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. We will inquire about the availability of emergency transmission service, please transfer me to the Tariff desk.” |
| 4 | Notify the SPP Tariff desk (SPP TAR) to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” If not available, do not proceed and make log entry. If there is emergency transmission service available continues to step 4. |
| 5 | Notify AEP QSE (AEP QSE): Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” If no available capacity, do not proceed and make log entry. If there is available capacity, ask AEP QSE to arrange for the submission of the transmission request and the E-tag(s). |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 6 | If ERCOT will be receiving emergency energy, notify the DC-Tie Operator (AEP DCT): Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and if approved they will submit the E-Tag(s).” |
| 7 | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State which DC Ties in Other Information - End time will be the same as initiation time (back office will take care of the rest) |
| NOTE | Keep SPP RC informed of ERCOT’s change in EEA status. |

## 4.4	Backing out of EEAs and Termination

Procedure Purpose: Steps to back out of and terminate emergency energy across the SPP and CFE DC ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | When moving EEA status: Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s status change. Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]”. |
| 2 | This step only needs to be preformed if emergency energy is being received from SPP: Notify AEP QSE when emergency energy will end (usually at the top of the hour): Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA [3 or 2] to EEA [2 or 1]. We believe this emergency [will or will not] continue into the next hour. Thank you.” |
| 3 | This step only needs to be preformed if emergency energy is being received from CFE. Notify the DC Tie operator (AEP TDSP) when EEA status is 0 to end emergency energy from CFE. |
| NOTE | Repeat above steps as needed with the notifications until ERCOT’s status is EEA 0 (zero). |

## 4.5	Emergency Energy to CFE

Procedure Purpose: Provide Emergency Energy to CFE across the DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R1 | INT-010-1 R3 |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If CFE requests the emergency energy, no emergency notification needs to be declared by ERCOT. |
| NOTE | ERCOT maintains the authority to curtail energy schedules flowing into or out of the ERCOT System across the DC Ties in accordance with NERC scheduling guidelines. If there are E-tags that can be curtailed to alleviate the emergency situation, refer to Section 3.7. |
| 1 | The request for emergency energy will come from either the ERCOT Transmission & Security Operator or the DC Tie operator: - If there is export capacity room on the appropriate DC-Tie(s), coordinated with the ERCOT Transmission & Security Operator to ensure it will not cause transmission issues - With no issues, determine the DC-Tie(s), MW amount, time and duration (if possible) - Coordinate with Real-Time Operator - Notify DC-Tie Operator (AEP TDSP) to ramp DC-Tie(s) - Issue AEP QSE a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State Emergency Energy to CFE and which DC-Ties in Other Information - End time will be the same as initiation time (back office will take care of the rest) |
| Log | Log all actions taken. |

## 4.6	Emergency Energy to SPP

Procedure Purpose: Steps to provide emergency energy to Southwest Power Pool across the SPP DC ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP 001-0 R1 | INT-010-1 R3 |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | - SPP will notify ERCOT that emergency energy is needed - Verify that providing emergency energy will not put ERCOT in an insecure state. |
| 2 | - SPP will contact the DC Tie Operator and arrange to maximize the DC tie into SPP - AEP QSE will submit an E-Tag for the emergency energy. |
| 3 | Notify Real-time Operator, SCED may need an off-scheduled run. |
| 4 | Issue AEP QSE a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State Emergency Energy to SPP and which DC-Ties in Other Information - End time will be the same as initiation time (back office will take care of the rest). |

## 4.7	Loss of Primary Control Center Functionality

Procedure Purpose: To be performed by the Operator at the alternate Control Center (ACC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1.1 R5 | EOP-001-0 R4.4 | EOP-008-0 | IRO-005-2 R1.10 |

| Version: 1 | Revision: 5 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Contact Security | IF: - Unable to reach any Operator at the PCC (cell phone or PBX Bypass phones); THEN: - Check the Control Room video camera to determine the status of the PCC and personnel, - Contact Security at the ACC - Notify them of the situation AND - Have them attempt to make contact with Security at PCC. - Have them contact you with information acquired OR IF: - Notified by the PCC that they are evacuating and/or transferring sites; THEN: - Continue with procedure. |
| Constant Frequency | IF: - The loss of PCC involves the loss of EMS (LFC and RLC/SCED; THEN: - Determine which QSE has ample Capacity to place on Constant Frequency Control. (REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data) - Direct that QSE to go on “Constant Frequency”, by issuing an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into “Monitor” mode. |
| QSE Hotline Call | Hotline call for EMS (LFC and RLC/SCED) failure: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to loss of primary control center functionality, LFC and SCED failure. ERCOT has put a QSE on constant frequency. All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT. ERCOT may issue unit specific deployments to any Resources as required. Direct all urgent phone calls thru the [Austin][Taylor] OPX. [Select QSE], “Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call with systems functional: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center functionality and is transferring operations to the alternate control center. Direct all urgent phone calls thru the [Austin][Taylor] OPX. All ERCOT systems are functioning at this time. HRUC will be delayed until additional staffing arrives and Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| TO Hotline Call | Hotline call for EMS (LFC and RLC/SCED) failure and if Systems are functional: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center functionality and is transferring operations to the alternate control center. Please monitor your own service area and notify ERCOT if you exceed the normal rating of your transmission elements. Report West - North stability limit when power flows reach 70% and North – Houston stability limit power flows reaches 90% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any forced line operations. Direct all urgent phone calls thru the [Austin][Taylor] OPX. [Select TO], Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Nuclear Plants | If systems are NOT functional: Notify the appropriate Nuclear Plants QSE and inform them that they should notify the Resource that ERCOT has issued an Emergency Notice and RTCA and State Estimator is not functional. This is expected to last for approximately 1 hour. If systems are functional: Notify the appropriate Nuclear Plants QSE and inform them that they should notify the Resource that ERCOT has issued an Emergency Notice and is currently operating with one operator and RTCA results will not be viewed in a timely manner. This is expected to last for approximately 1 hour. |
| MIS Posting | As time permits, post the Emergency Notice in the Public MIS using Notice Builder. |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Austin. Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Manager of System Operations and/or designee will notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support These phone numbers are also programmed into the control room cell phone. |
| Monitor Critical Facilities | Potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the MIS. Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. |
| Respond to QSEs | If systems are NOT functional: IF: - The QSE that is put on constant frequency is having trouble controlling frequency; THEN: - Issue unit specific VDIs to other QSEs to help with Regulation, - Choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). If systems are functional: Monitor frequency and re-run SCED/use (manual offset) as needed. IF: - QSEs call in with questions about RUC; THEN: - Notify the QSE that the RUC functions will resume when additional staff arrive, - Document QSE calls to pass along the appropriate Operators as they arrive. |
| Respond to TOs | IF: - TOs call in to report the following: - Thermal limits have reached their continuous rating, - West-North stability limit has reached 70% of its limit, - North-Houston stability limit has reached 90% of its limit, THEN: - Take immediate action, as listed below, for thermal limits and stability limits, |
| Stability Limits (IROL) | IF: - The West-North stability limit is approaching 70% and is continuing to trend upward, - The North-Houston stability limit is approaching 90% and is continuing to trend upward; THEN: - Take immediate action to lower Wind Generation in the west by activating the west-north if systems are functional, OR - Issue unit specific VDIs as necessary to relieve the congestion, - Choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level - If VDIs are issued, monitor QSE on constant frequency |
| Thermal Limits Reached (SOL) | IF: - Thermal limits have reached their continuous rating and are continuing to trend upward, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - Issue unit specific VDIs as necessary, - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Log | - Make log entry of events. |

## 4.9	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - When cold weather is 5 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region - When severe cold weather is 5 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### ADVISORY |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When cold weather is 3 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 3 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### WATCH |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 1 days away - When cold weather is 1 day away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 1 day away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT varies from time-line for DAM/DRUC. |
| ### EMERGENCY NOTICE |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED). - When cold or severe cold weather is in the ERCOT Region and it is beginning to have an adverse impact on the ERCOT System. |
| ### Notifications |  |
| HOTLINE | Notify QSEs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| POST | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the only option is “public” - For “free form” messages, the “Notice priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| LOG | Make log entry. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 - / 1 - / 2 - / 2 - / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |