## Power Operations Bulletin # 539

ERCOT has posted/revised the Shift Supervisor Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 5.3	Notification of a Protective Relay or Equipment Failure Report

Procedure Purpose:  Notification to support groups.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 6.2.3 | 6.2.4 |  |  |
| NERC Standard | PRC-001 R2.2 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC | “If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible.” |
| 1 | Notify the shift engineer or the on-call engineer when notified that a protective relay or equipment failure reduces system reliability and there is no back-up protective relay available. A corrective action plan will need to be implemented to limit exposure to the BES. |
| 2 | - After notification from a TO or QSE, NOTIFY by e-mail: - OPS Support Engineering - Operations Analysis - Shift Supervisors - The subject line of the e-mail should read “Protective Relay or Equipment Failure.” - Include in the e-mail: - Entity Name - Brief description - Contact information - Any significant information |
| 3 | If a TO or QSE e-mails a “Mis-Operation Relay form”, forward to the above identified e-mail address. |
| 4 | Log information available in the Log as time permits. |

## 5.7	Market Participant Backup Control Center Transfer

Procedure Purpose:  To provide internal notification.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | If notified by a QSE or TO that they will be transferring to their backup control center, or from their backup to primary, - Send e-mail to 1 ERCOT System Operators - Make log entry. |
| 2 | - If experiencing issues with communications, ICCP, etc. contact the Help Desk. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Regional Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R4.1, R5 | EOP-002-2.1 R3, R6.3, R7.2 | EOP-004-1 R1, R3.1 | IRO-014-1 R1.1.2 |
|  | IRO-015-2 R15 | TOP-002-2 R4 | DOE OE-417 |  |

| Version: 1 | Revision: 4 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template around 0300 – 0400 and again around 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - Conditions change that required new notices to be issued or cancelled (e.g., OCN , Advisory, Watch, or Emergency Notice ) - A projected reserve capacity shortage develops - Local reliability concerns arise including actual overloads or loss of load - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas restrictions, not expected to cause reliability issues - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Send updated report when conditions have returned to normal. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2A - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EEA Level 2A in effect Potential for EEA Level 2B - N/A – No EIL available - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 2B in effect Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - EEA Level 2B in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 3 in effect |  |
| ### Texas RE Event Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, within one hour: - COMPLETE the form located in Section 2.5 of the Desktop Guide:“Texas RE Event Form” - E-MAIL the form to Manager, System Operations - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis process, events include the following: Category 1 Events: - Loss of bulk power system (BPS) elements caused by common mode failure ≥ 3 elements - Loss of generation station generators caused by common mode failure ≥ 3 aggregate 500 to 999 MW (Combine Cycle Train counts as one element) - Unplanned evacuation from BPS control center facility with BPS SCADA functionality ≥ 30 minutes - Failure, degradation or misoperation of SPS - Intended and controlled system separation by the proper operation of a SPS - System wide voltage reduction - Unintended system separation resulting in an island of 100 MW to 999 MW Category 2 Events: - Complete loss of all BPS control center voice communication system ≥ 30 minutes - Complete loss of SCADA, control or monitoring functionally ≥ 30 minutes - Loss of off-site power (LOOP) to a nuclear generating station - Unintended system separation resulting in an island of 1,000 MW to 4,999 MW - Unintended loss of Firm System Load ≥ 300 MW for more than ≥ 15 minutes - Voltage excursions ≥ ± 10 percent > 5 minutes Category 3 Events: - Loss of generation ≥ 1,000 MW - Unintended system separation resulting in an island of 5,000 MW to 10,000 MW - Loss of load ≥ 1,000 MW Category 4 Events: - Loss of generation > 5,0001 MW to 9,999 MW - Loss of Load 5,001 to 9,999 MW - Unintended system separation resulting in an island > 10,000 MW Category 5 Events: - Loss of generation ≥ 10,000 MW - Loss of Load ≥ 10,000 MW |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations or designee when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". |  |
| OE-417 Reporting Events | DOE OE-417 initial reports are to be completed within 1 hour, forms can be downloaded at: ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc. Electronic forms are preferred. OE-417 reports are required for the following events: - System wide voltage reduction ≥ 3 % - Public appeal to reduce the use of electricity for purposed of maintaining the continuity of the electric power system - Load shedding ≥ 100 MW implemented under emergency operational policy - Uncontrolled loss of Firm Load ≥ 300 MW for > 15 minutes - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Fuel supply emergencies that could impact system adequacy or reliability - Loss of electric service ≥ 50,000 for ≥ 1 hour - Compete operation failure of electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system |  |
| NERC IROL and Preliminary Disturbance Report EOP-004-1 | NERC Preliminary Disturbance reports are to be completed within 24 hours, forms can be downloaded at: http://www.nerc.com/page.php?cid=5¦66 NERC Disturbance reports are required for the following events: - Loss of bulk power transmission component that significantly affects the integrity of system operations, which resulted in actions such as: - Modification of operating procedures - Modification of equipment to prevent reoccurrence of event - Identification of valuable lessons learned - Identification of non-compliance with NERC standards or policies - Identification of a disturbance that is beyond recognized criteria (i.e. three-phase fault with breaker failure, etc) - Frequency or voltage going below the under-frequency or under-voltage load shed points - The occurrence of system separation or system islanding or both - Loss of generation ≥ 1,000 MW - IROL violation - Any action taken by a GOP, TOP, BA, or LSE that results in: - Sustained voltage excursions equal to or greater than ±10 percent - Major damage to power system components - Failure, degradation, or misoperation of system protection, SPS, RAPs, or other operating system that do not require operator intervention, which did result in, or could have resulted in, a system disturbance. - Firm load shedding of 100 MW or more to maintain the continuity of the BES - Loss of firm load demands totaling more than 200 MW or 50 percent of the total customers for ≥ 15 minutes |  |
| 1 | When required to file a report (If Manager or designee is unavailable): Forward the TO or QSE report or the Director of Cyber Security’s report to: - NERC (esisac@nerc.com, fax (609) 452-9550) - DOE (doehqeoc@oem.doe.gov, fax (202) 586-8485) - “NERC and DOE Disturbance Reporting” e-mail list. |  |
| ### RCIS Reporting |  |  |
| NOTE | Refer to Section 2.2 in Desktop Guide: Operating State Alert Levels. |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” (ERCOT EEA Level 2A or 2B) - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| TEA Postings | There are four levels of Transmission Emergency Alert (TEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “System Emergency”: - “ERCOT is declaring TEA 1 on the North-Houston interface” - “ERCOT is declaring TEA 2 on the North-Houston interface; Load Resources have been deployed in the Houston area”. - “ERCOT is declaring TEA 3 on the North-Houston interface; firm load is being curtailed in the Houston area”. - “ERCOT is in TEA 0 and back to normal operations” |  |
| SEA Postings | There are four levels of Security Emergency Alerts (SEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “CIP Free Form”: - “ERCOT is declaring SEA 1 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 2 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 3 for a [cyber or physical] attack on [control center, generating facility, substation, transmission line] located in [west, north, south, central] Texas”. - “ERCOT is in SEA0 and no longer under threat”. |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2A, THEN: - Select the “SO EEA Level 2A” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2B, THEN: - Select the “SO EEA Level 2B” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2B” Scenario and activate notification, WHEN: - EEA Level 2B is terminated, THEN: - Select the “SO EEA Level 2B to EEA Level 2A” Scenario and activate notification, WHEN: - EEA Level 2A is terminated, THEN: - Select the “SO EEA Level 2A to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed, THEN: - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 2.7.8 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on P:\SYSTEM OPERATIONS drive in the PUCT Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” - The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| 1 | Weather Information - Enter the High and Low temperature forecast from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Enter the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Enter the Previous Day Actual MW. |  |
| 3 | Interchange - Enter the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Enter the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals - Enter the Generation scheduled outage MW total. - Enter the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves - Enter the Responsive Reserve requirement at the Project Peak. - Enter the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity - No action needed |  |
| 8 | Comments - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically during the day, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | When alerts and warnings for GMDs are issued for K-7 or higher: - Notify the TOs and QSEs by posting message on MIS Public using Notice Builder, Log the information. |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability. |  |

## 7.1	Abnormal Events

Procedure Purpose:  To provide guidance for those events outside normal operating parameters.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.3 |  |  |  |
| NERC Standard | BAL-002-0 R6.2 | EOP-001-0 R4.4, R5 | EOP-004-1 R1, R3.1 | IRO-005-2 R1.7, R1.10, R6 |
|  | DOE OE-417 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - The ERCOT Shift Supervisor will act as the main contact and answer inquiries between the control room and other ERCOT operations groups during abnormal events - See Phone Book at Shift Supervisor’s Desk |
| ### System Disturbance |  |
| NERC | ERCOT ISO shall fully restore the minimum Contingency Reserve requirement of the ERCOT Region’s largest single contingency (1375 MW) as soon as practical. Within 90 minutes, ERCOT ISO will restore Responsive Reserves to 2300 MW or greater. This 90 minute restoration period begins at the end of the disturbance recovery period. |
| 1 | IF: - A system disturbance causes the ERCOT system to violate the Single Contingency Secure status, THEN: - VERIFY that the System Operators take all actions necessary as described in the ERCOT Operating Guides. |
| 2 | IF: - The system disturbance cannot be normalized with current on-shift staff, THEN: - IDENTIFY and ASSIGN additional System Operators, Operations Support, Operations Analysis, or Market Operations staff to assist in normalizing the system condition. |
| 3 | The ERCOT Shift Supervisor will ISSUE Emergency Communications & Notifications to ERCOT staff and management in accordance with Section 2.1 of the Desktop Guide. |
| ### Degraded Weather |  |
| 1 | WHEN degrading weather conditions are forecasted, VERIFY that the System Operators on the Transmission & Security and Real-Time desks issued corresponding OCN, Advisories, and Watches. |
| 2 | MONITOR ERCOT reserves and Ancillary Services capacities during degraded weather periods such as extreme heat, cold weather, severe cold weather, severe thunderstorms/tornado warnings and verify a SASM is initiated as necessary. |
| 3 | IF: - Forecasted weather conditions are extreme, and is deemed necessary, THEN: - IDENTIFY and ASSIGN additional System Operators, Operations Support, Operations Analysis, or Market Operations staff to assist in operating the system during degraded weather conditions |

## 7.4	Hurricane/Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov) |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Ensure OCN is issued. - Review the expected path of the hurricane/tropical storm and consult with the Operations Support Engineers to determine if multiple contingencies should be studied due to the possibility of transmission outages or loss of load. - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delay/return early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. Outages that could be critical are: - Getaways from power plants, in the affected areas, that need to remain on during the storm for reliability. - 345 KV transmission paths in the affected areas, OR - 345 KV transmission paths that will significantly impact the flow of power to and from the affected area. |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. - Ensure Advisory is issued. - If STP is in the path of the hurricane/tropical storm and the QSE is planning to take the unit offline, - Contact System Operations Support Engineers to run studies to determine the impact. - Discuss the study results with the Operations Support Engineers and evaluate the system conditions. - If necessary determine the generation needed to replace the loss of capacity from STP. - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delay/return early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. - Ensure Watch is issued - If necessary, instruct the RUC Operator to commit additional Resources as per Operations Support recommendations. - Determine with the Manager System Operations the need to have a conference call bridge open with the most affected TOs. - Determine with the Manager System Operations the need for additional support staff from EMMS Production, ANA, Operations Support, and Operators. - . - Report any fuel restrictions as per section 6.1 of this procedure. |
| Emergency Notice | When Hurricane/Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. - Ensure Emergency Notice is issued |

## 7.5	Cold Weather

Procedure Purpose: To ensure ERCOT is prepared for Severe Cold Weather Operations

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 0 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Cold weather notifications are called when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When approaching cold weather is approximately 5 days away. - Ensure OCN is issued. - Continue to monitor the expected path of the approaching cold front. - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delay/return early. - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market allows. - Review emergency operating procedures. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Advisory | When approaching cold weather is 3 days away. - Ensure Advisory is issued. - Continue to monitor the expected path of the cold front. - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delay/return early. - Contact Operations Support to run studies to determine the impact of current and future outages. - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market or if additional Ancillary Services will be needed. - Review emergency operating procedures. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Watch | When approaching cold weather is 1 day away. - Ensure Watch is issued. - Continue to monitor the expected path of the cold front. - Determine with the Manager System Operations the need for additional support staff. - Determine if additional Ancillary Services will be needed. - Continue to monitor the Ancillary Service and RUC Markets for shortages. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Emergency Notice | When cold weather is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. - Ensure Emergency Notice is issued. - Report any fuel restrictions as per section 6.1 of this procedure. |

## 7.6	Severe Cold Weather

Procedure Purpose: To ensure ERCOT is prepared for Severe Cold Weather Operations

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Severe cold weather notifications are called when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When approaching severe cold weather is approximately 5 days away. - Ensure OCN is issued. - Continue to monitor the expected path of the approaching severe cold front. - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delay/return early. - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market allows. - Review emergency operating procedures. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Advisory | When approaching severe cold weather is 3 days away. - Ensure Advisory is issued. - Continue to monitor the expected path of severe cold front. - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delay/return early. - Contact Operations Support to run studies to determine the impact of current and future outages. - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market or if additional Ancillary Services will be needed. - Review emergency operating procedures. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Watch | When approaching severe cold weather is 1 day away. - Ensure Watch is issued. - Continue to monitor the expected path of severe cold front. - Review emergency operating procedures. - Determine with the Manager System Operations the need for additional support staff. - Determine if additional Ancillary Services will be needed. - Continue to monitor the Ancillary Service and RUC Markets for shortages. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Emergency Notice | When severe cold weather is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. - Ensure Emergency Notice is issued. - Report any fuel restrictions as per section 6.1 of this procedure. |

## 8.3	Possible Protocol or Operating Guide Violations

Procedure Purpose: Provide instructions for reporting that a QSE or TO may have violated an ERCOT Protocol or Operating Guides requirement.

| Protocol Reference | 6.5.7.9 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.1.2 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - It appears that a QSE or TO is in violation of the ERCOT Protocols or Operating Guides, THEN: - Confirm the ERCOT System Operator’s finding of a possible violation and that an attempt was made to resolve issue with the QSE or TO personnel. - Attempt to resolve the issue. - Obtain information from Market Operations Support and/or Operations Support personnel, as needed. IF resolution is reached, then LOG the event and this procedure is complete. |
| 2 | IF: - No agreement can be reached; THEN: - Review the incident to establish confidence that there has been a possible violation. - Submit information to Manager System Operations or designee |
| 3 | Log the Incident Report in the Shift Supervisors log. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |