## Power Operations Bulletin # 540

ERCOT has posted/revised the Transmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	Site Failovers and Database Loads

Procedure Purpose: To provide notice to the Market Participants when ERCOT performs site failovers and database loads.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Database Load | Approximately 5 - 30 minutes before a database load, make the following Hotline call to TOs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a database load on its Energy & Market Management Systems. During this time, SCED Base Points will reflect accurate dispatch instructions. In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes. |
| Site Failover | Approximately 5 - 30 minutes before site failover, make the following Hotline call to TOs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 15 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. |
| Database Load With W-N Active | IF: - The West – North is active; Then: - Before database load, ensure W-N is constrained to ≤ 70%. |
| Site Failover With W-N Active | IF: - The West – North is active; Then: - Approximately 5-10 minutes before site failover, - Verify with Real-Time operator is aware constraint is active, - Ensure W-N is constrained to ≤ 70%. |
| Site Failover Posting | Verify with Real-Time operator that posting will be made. The site failover message is already built in Notice Builder under “EMS Site Failover”. |
| Site Failover Complete | Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], the site failover is complete. [TO] please repeat this back to me. That is correct, thank you.” |

## 3.3	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002 R8, R9 | NUC-001 | TOP-004 R4 |  |

| Version: 1 | Revision: 3 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT |
| 1 | IF: - RTCA or the State Estimator has not solved within the last 10 minutes, THEN: - Notify Shift Engineer, - Refer to Section 3.1 of the Desktop Guide and run through the checklist, - Request Shift Engineer to calculate limits manually if EMS will be unavailable for an extended period of time. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 15 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to issue an Advisory to the TOs: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], ERCOT’s RTCA and State Estimator have not solved in the last 15 minutes. Please monitor your own service area and notify ERCOT if you exceed the normal rating of your transmission elements. Report West - North and North – Houston stability limits if power flows reach 70% of their respective limits. Continue to monitor voltages in your area and notify ERCOT of any forced line operations.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Notify the appropriate Nuclear Plant’s QSEs and inform them that ERCOT’s RTCA is not function and is expected to be functional within approximately [# minutes]. |
| 4 | Post Advisory message on MIS Public using Notice Builder. |
| 5 | Once RTCA and State Estimator are operational: Make a Hotline call to cancel the Advisory to the TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT’s RTCA and State Estimator are functioning and we are back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 6 | Notify the appropriate Nuclear Plant’s QSEs to inform them that RTCA is now functional. |
| 7 | Cancel Advisory message on MIS Public using Notice Builder. |
| 8 | If VSAT has not solved within 1 hour: - Manually run VSAT, - If no results, notify Shift Engineer, - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |
| 9 | Make log entry of events. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-003 R1 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006 R1, R4 |
|  | IRO-002 R6, R8 | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |

| Version: 1 | Revision: 7 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. Error! Hyperlink reference not valid.A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) located in the Outage Notes - Unit specific dispatch instructions (Manual Dispatch or VDI) - If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - The electronic version is located at P:\System Operation\Remedial Action Plans, - A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congesting management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – mitigate local congestion and increase W/N transfers - Big Lake – mitigate local congestion and increase W/N transfers - Firerock ETT – mitigate local congestion and increase W/N transfers - Nelson Sharp – valley import during outages - Hamilton Road – control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – control Laredo import issues during outages |  |
| ### Review Planned Outage Notes |  |  |
| 1 | Review daily outage notes: IF: - Outage notes recommend slower moving Resources to be lowered to maintain system security; THEN: - Consider taking a real-time snap shot to determine where Resource(s) are needed before outage is taken - Use the manual override to step down Resource(s) - Once Resource(s) are down to where snap shot showed, release manual overrides, give approval for switching and activate SCED constraint. |  |
| Log | Log actions taken. |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - SE and/or RTCA is not solving; THEN: - Notify Shift Engineer, IF: - SE and/or RTCA has not solved for 15 minutes, THEN: - Refer to section 3.3 “Analysis Tool Outages” in this procedure. |  |
| 2 | IF: - RTCA has run within 10 minutes; THEN: - Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |  |
| 3 | IF: - A major change of Resource or Transmission Element Status; THEN: - Re-start RTCA and VSAT. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Determine if the SCADA is of similar magnitude to the Pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Shift Engineer. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP, - Refer to “Managing Binding and Exceeded Constraints” of this Procedure. |  |
| 4 | IF: - Post-contingency overloads greater than 100% exist without an SPS (identified as RAS in EMS), RAP, PCAP, or TOAP in place to relieve; THEN: - Activate constraints as necessary, - Lower the value in the % Rating column in RTCAM to tighten the constraint (minimum of 95%), - Increase the value in the % Rating column in RTCAM to loosen the constraint (maximum of 105%), - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 5 | IF: - There is an imminent threat to the reliability of the ERCOT system, caused by a Qualifying Facility (QF), and ERCOT decides to order the QF offline or to operate below its LSL; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 6 | IF: - Post-contingency overloads greater than 100% of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 7 | IF: - Any RTCA results predict a Facility Rating will exceed post-contingency loading of 125% or greater of the facility’s Emergency Rating, this is considered to be a potential IROL; THEN: - Refer to section 4.2 “Potential IROL’s”. |  |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |  |
| 9 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Shift Engineer, - If there are known reasons that the contingency is unsolved, notify the Shift Engineer to verify system conditions have not changed. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A Quick Start Resource is needed and not given SCED base points; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running), - Notify QSE as time permits. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| ### Transmission Issues in the Areas of the CFE DC-Ties |  |  |
| 1 | IF: - Contingencies or unsolved contingencies cannot be corrected with congestion management techniques and additional generation is not available to bring on; THEN: - Determine if there are export schedules over the CFE Ties that would help alleviate the situation if curtailed. |  |
| 2 | IF: - DC-Tie schedules can be curtailed; THEN: - Notify the ERCOT DC Tie Operator to curtail the schedule(s), specifying the time and amount, - Issue a Transmission Watch (if schedule needs to be cut immediately) - Make Hotline call - Make notification on MIS Public using Notice Builder - Notify Real-Time Desk to make Hotline call to QSEs - Notify Shift Engineer to update limit postings on MIS. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission Watch due to a post contingency loss of (name of contingency) overloads (name of overloaded element) resulting in curtailment(s) over the [name] DC-Tie.” [TO] please repeat this back to me. That is correct, thank you.” Edit script as needed to fit situation. |  |
| ### Managing Constraints in SCED |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for exceeded constraints). |  |
| 1 | IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk and control room staff. |  |
| 2 | Steps that may be taken to resolve congestion when a transmission constraint is exceeded in SCED: - Verify telemetry is correct, - Verify that the SCED executions are reducing the flows on the subject constraints, - Investigate units with large shift factors that are not being moved or are not following base points, - Create a “Suggestion Plan” for the constraint, - Redistribute A/S to increase the capacity available to SCED, - Instruct QSE to remove the appropriate A/S and to update telemetry, - Notify Resource Operator with undeliverable A/S type, amount and hours from the Resource(s), - Removing a unit from ONTEST, - Commit/decommit additional units, - Determine if there is a non-cascading constraint that is less severe and can be released to resolve this constraint, - Release the constraint if non-cascading and if the constraint prevents resolving a more severe insecure state, - Instruct Shift Engineer to formulate a mitigation plan which may include - Transmission reconfiguration (switching) - Load rollover to adjacent feeders - Load shed plans |  |
| 3 | Steps that may be taken to resolve insecure state by overriding HDL/LDL: - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - Notify QSE of override (this could exceed ramp rate) - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. |  |
| NOTE | Possible reasons for manually overriding HDL/LDL could be: - Manually dispatching slower moving Resources before an outage to better manage congestion caused by the outage - Manually overriding Resources which are not following Base Points and are affecting constraint management or frequency - Manually overriding Resources which are causing SPS to continuously trip in Real Time |  |
| Log | Log all action taken. |  |
| ### QSE Requests to Decommit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Initiate the Emergency Notice Hotline call, AND - Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 2 | Trouble Shooting: IF: - Transmission constraints are active, THEN: - Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |  |

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15 | 6.1.7 | 6.3.1 (1) | 6.3.2(2) |
| --- | --- | --- | --- | --- |
|  | 6.5.1.1(a)&(c) | 6.5.5.1(2) &(3) | 6.5.6 | 6.5.7 |
|  | 6.5.7.7 | 6.5.9.1(1)(c) | 6.6.7.1 | 6.7.6 |
| Guide Reference | 2.2.4 | 2.7.2(h)(ii) | 2.7.4.1(1) | 2.7.4.3 |
| NERC Standand | IRO-005-2 R1.2, R1.3, R1.4 | NUC-001-2 R4.2 | TOP-002-2 R8, R10 | VAR-001-1 R1, R2, R4, R6, R7, R8, R9, R10, R12 |
|  | VAR-002-1 R3.1 | IRO-002-1 R6, R8 | TOP-004-2 R6.2 | TOP-006-1 R2 |
|  | EOP-001-0 R4.2 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "normal" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS) Secure site. Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Voltage Tables | For Comanche Peak - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. For South Texas Project - System; - 345 kV. - Nominal Voltage; - 362.25 kV. - Tolerance; - +0% or -6.14%. - Maximum Voltage; - 362.25 kV. - Minimum Voltage; - 340 kV. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. When STP is in an alternate line up, the minimum voltage is 347 kV. When STP is in an alternate line up without the unit auxiliary transformer, the minimum voltage is 355 kV. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated in the voltage tables; THEN: - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate QSE. |
| ### Voltage Issues |  |
| NOTE | - Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Section 3.9 of the Desktop Guide. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damages is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implements and studies shall that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. |
| 1 | WHEN: - Indicated by SCADA alarms, OR - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. |
| 2 | WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct a QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| Exceed URL | For multi-generator busses, ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL until all On-Line Generation at the same transmission bus have been instructed to their respective CURLs or URLs. IF: - Instructing a QSE’s Generation Resource to exceed its Unit Reactive Limit (URL); THEN: - Issue a VDI to the QSE for exceeding the URL (Exceed URL VDI). The VDI must include the following: - Resource name - Specific voltage set point. - Start time - End time - Choose “HOLD X VOLTAGE LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| Reduce MW | IF: - MW output must be reduced to follow a voltage support instruction; THEN: - Issue a VDI to the QSE providing Voltage Support Service (VSS VDI). The VDI must include the following: - Resource name - MW level at time of instruction - MW level Resource needs to move to for Voltage Support - Start time - End time - Choose “STAY AT/ABOVE X MW/MVAR LEVEL” or “STAY AT/BELOW X MW/MVAR LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| NOTE | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure XX. |
| 1 | IF: - VSAT has not run in the last 80 minutes, OR - S-H or N-H 345kV circuit has a forced outage, OR - VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status; THEN: - Rerun the RTNET, RTCA, and RTDCP (VSA). If no change, then: - Notify the Shift Supervisor and Shift Engineer - As deemed necessary make the following Hotline call. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is experiencing problems with the Voltage Stability Analysis program. Maintain voltage levels as required by your procedures and notify ERCOT of any voltage issues within your system. [TO] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) more frequently than the periodic scheduled VSAT run. - Confirm VSAT indicates either “Normal” or “Pending”. Reliability Margin Table. Scenario Name; Safety Margin. O-CORP_L; 75MW. O-HOUS_L; 200MW. O-DFW_L; 200MW. S-H_G; 200MW. S-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. O-VALL_L; 75MW. HHGT_G-O; 0MW. |
| For HHGT_G-O | For HHGT_G-O: Instruction the QSE to raise or lower bus voltage: Typical script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specified bus] by (+ 1 or 2 kV or – 1 or 2 kV) for a target of [target kV] [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| 3 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the Extra-Interface Limit pre-contingency value is less than the Safety Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 4. |
| 4 | Determine the contingency status in RTCA (solved/unsolved).IF: - Solved, - Have Shift Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Shift Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct HRUC Operator to commit additional resources in the weak bus area that are available. |
| 5 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 6 | Determine if the Extra-Interface Limit pre-contingency value is greater than the Reliability Margin Value. IF: - The Extra-Interface Limit pre-contingency value is greater than the Reliability margin; THEN: - No further action is required. OR IF: - The Extra-Interface Limit pre-contingency value is less than the Reliability margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 4. If no additional generation is available, continue. |
| 7 | IF: - No additional generation is available; THEN: - Ensure that the OPS Support Engineering group has been contacted to devise a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT. |
| NOTE | Operations Support will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT SharePoint > Operations Support > AVR AND PSS Status |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, - Notify the appropriate TO of the change in status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “1 ERCOT System Operators” |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. To update the “real time values” spreadsheet when any PSS is forced offline in the West zone: - Open the Stability Limit tab to verify units, - Enter 0 = PSS is offline; 1 = PSS online for each resource change. It allows the Operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 5 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources - When cold weather is 5 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region - When severe cold weather is 5 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Unplanned Transmission Outages that may impact System reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When cold weather is 3 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 3 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 1 days away - When cold weather is 1 day away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 1 day away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - . - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. - ERCOT varies from time-line for DAM/DRUC. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - Loss of Primary Control Center Functionality. - Load Resource deployment for North-Houston voltage stability. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED). - When cold or severe cold weather is in the ERCOT Region and it is beginning to have an adverse impact on the ERCOT System. |
| ### Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on the MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| Version: 1 | Revision: 3 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted, QSEs should be notified via Hotline call (see 2b for typical script). - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC falls > 2300 MW; THEN: - Using the Hotline, notify all TOs to implement EEA 1. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is declaring EEA 1 due to Physical Responsive Capability is below 2300 MW. [TO] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | - Relax transmission constraints to provide additional generation at the expense of temporarily creating a security violation as long as the violation does not physically overload any single Transmission Element above its emergency rating, - Inquire about the availability of registered BLTs (see Section in Desktop Guide). |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2A |  |
| 1 | IF: - PRC falls > 1750MW; THEN: - Using the Hotline, notify all TOs to implement EEA 2A and any measures associated with EEA 1, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2A; - Load Resources providing RRS have been deployed, - Reduce customer loads by using distribution voltage reduction measures, if deemed beneficial. [TO] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | - Unless already in effect, verify with the shift supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify TOs, via Hotline, that a media appeal for conservation is in effect. Typical Script: “This is ERCOT Operator [first and last name]; this is a courtesy call to inform you that ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2B |  |
| NOTE | If no EILS exists, skip EEA 2B and proceed to EEA 3 if needed. If the amount of EILS available for deployment equals or exceeds 500 MW. EILS may be deployed as a single block or in two groups. |
| 1 | IF: - Unable to maintain system frequency at 60.00Hz AND Load Resources providing RRS have been deployed and EILS has been procured; THEN: - Using the Hotline, notify all TOs to implement EEA 2B and any measures associated with EEA 1 and 2A, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2B. EILS are being deployed. [TO] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Using the Hotline, notify all TOs to implement EEA 3 and any measures associated with EEA 1, 2A, and 2B, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3. ERCOT is instructing all Transmission Operators to shed their share of [amount] MW. Transmission Operators are to report to ERCOT when this is complete. [TO] please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R4.1, R4.4 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1375 MW; THEN: - Using the Hotline, notify all TOs of firm load restoration. Typical Script when only restoring a portion of the firm load: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is instructing all Transmission Operators to restore their share of [amount] MW leaving [amount] MW still off. Report to ERCOT when this task is complete. [TO] please repeat this back to me. “That is correct, thank you.” OR Typical Script when restoring all firm load: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is instructing all Transmission Operators to restore all firm load. Report to ERCOT when this task is complete. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 3 to EEA Level 2B |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1375 MW, AND - All firm load has been restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 3 to EEA 2B: - Notify the TOs that Load Resources are being restored - Rescind distribution voltage reduction measures as appropriate. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 3 to EEA 2B. All Load Resources are being recalled. Any TO that implemented distribution voltage reduction measures can return to normal operation”. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 2B to EEA Level 2A |  |
| 1 | IF: - The System can maintain PRC ≥ 1750 MW, AND - All Load Resources have been instructed to be recalled, AND - Sufficient Regulation Service exists to control to 60 Hz; THEN: - Using the hotline, notify all TOs of the reduction from EEA 2B to EEA 2A. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2B to EEA 2A. [TO] please repeat this back to me. That is correct, thank you.” |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 2A to EEA Level 1 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW AND - All Load Resources have been instructed to be restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 2A to EEA 1 and EILS have been instructed to restore, - If BLTs were implemented, restore. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2A to EEA 1, EILS are being restored. [If Block Load Transfers have been executed please coordinate with ERCOT to restore them as system conditions permit]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Using the hotline, notify all TOs of the reduction from EEA 1 to EEA 0. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 1 to EEA 0. A Watch still remains in effect. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Cancel Watch |  |
| 1 | WHEN: - PRC is ≥ 3000 MW, AND - Non-Spin has been recalled; THEN: - Cancel Watch Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. Physical Responsive Capability is now above 2500 MW. [TO] please repeat this back to me. That is correct, thank you.” |

## 7.4	Block Load Transfer

Procedure Purpose:  To transfer loads, located in ERCOT to a Non-ERCOT system or from a Non-ERCOT system to ERCOT during emergencies conditions.

| Protocol Reference | 6.5.9.5 | 6.5.9.5.1 | 6.5.9.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.4 |  |  |  |
| NERC Standard | EOP-001-0 R3.2, R4.2, R7.2, & R7.4 |  |  |  |

| Version: | 1 | Revision: | 2 | Effective Date: June 14, 2011 |
| --- | --- | --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Restoration of service to outage customers using BLT’s will be accomplished as quickly as possible if the transfers will not jeopardize the reliability of the ERCOT Interconnection. - BLTs that are comprised of looped systems may be tied to the non-ERCOT Control Area’s electrical system(s) through multiple interconnection points at the same time. Transfers of looped configurations are permitted only if all interconnection points are registered and netted under a single Electric Service Identifier (ESI ID) and represented by a single TSP or DSP or netted behind Non-Opt In Entity (NOIE) metering points. |
| ### ERCOT picks up Load for Non-ERCOT System |  |
| 1 | IF: - ERCOT is requested to pick up load for CFE or SPP; THEN: - Consult with Shift Engineer to ensure no reliability issue exists - If BLT is registered (refer to Desktop Guide): - Issue VDI to the QSE listed (if no QSE listed, no VDI needed) - If BLT is not registered, proceed to step 2 - Determine the amount of load being transferred into ERCOT - Issue VDI to QSE (if applicable) - Choose “OTHER For QSE” - In text, state “BLT from SPP/CFE to ERCOT” - Send e-mail to “BLT” distribution list with information - Include in e-mail weather BLT is modeled or not |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Shift Engineer to ensure no reliability issue exists - If no issues, allow the BLT - Determine the amount of load being transferred into ERCOT - Send e-mail to “BLT” distribution list with information - Include in e-mail that BLT is not registered - Include in e-mail weather BLT is modeled or not |
| 3 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Terminate the BLT. |
| ### Non-ERCOT System picks up Load for ERCOT |  |
| 1 | IF: - CFE or SPP picks up load for ERCOT; THEN: - Consult with Shift Engineer to ensure no reliability issue exists - If BLT is registered (refer to Desktop Guide): - Issue VDI to the QSE listed (if no QSE listed, no VDI needed) - If BLT is not registered, proceed to step 2 - Determine the amount of load being transferred out of ERCOT - Issue VDI to QSE if applicable (if applicable) - Choose “OTHER For QSE” - In text, state “BLT from ERCOT to SPP/CFE” - Send e-mail to “BLT” distribution list with information - Include in e-mail weather BLT is modeled or not |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Shift Engineer to ensure no reliability issue exists, - If no issues, allow the BLT, - Determine the amount of load being transferred out of ERCOT, - Send e-mail to “BLT” distribution list with information - Include in e-mail that BLT is not registered - Include in e-mail weather BLT is modeled or not |
| 3 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Terminate the BLT. |
| NOTE | If the Alamito Creek (ALMC) to Presidio (PRES) 69 kV transmission line trips, CFE will automatically pick up approximately 2 MW of load on the Presidio/Gonzales BLT. When AEP TO has informed you that this happened, follow step 1 above. |

## 8.1	Hurricane / Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov) |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. Coordinate with Outage Coordination for the review of planned and existing outages to be rejected and/or restored. Using the Hotline, issue an OCN to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a [Tropical Storm/Hurricane] [Name] due to a probability of making landfall in the ERCOT Region. TOs are instructed to: - Review planned and existing transmission outages to be withdrawn and/or restored - Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. Using the Hotline, issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is currently projected to impact the ERCOT Region. TOs are instructed to: - Review planned and existing transmission outages to be withdrawn and/or restored. - Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities. - Test communication with other TDSP's and QSEs prior to the hurricane making landfall. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. Using the Hotline, issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is expected to make landfall near [Place] at [time]. TOs are instructed to: - Be prepared to lose load and expect high voltage conditions - Keep ERCOT informed of transmission outages. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency | When Hurricane/Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to [Tropical Storm/Hurricane Name] having an adverse impact on the ERCOT System [specify condition]. TOs are instructed to: - Be prepared to lose load and expect high voltage conditions - Keep ERCOT informed of any issues ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public using Notice Builder. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

## 8.2	Cold Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for cold weather operations.

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 0 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Cold weather notifications are called when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. |
| OCN | When approaching cold weather is 5 days away. Using the Hotline, issue an OCN to all TO: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a cold weather system approaching in the next 5 days with temperatures anticipated to remain 32°F or below in three or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review planned and existing outages for the possibility of withdrawing or restoring equipment. - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory | When approaching cold weather is 3 days away. Using the Hotline, issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for a cold weather system approaching in the next 3 days with temperatures anticipated to remain 32°F or below in three or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch | When approaching cold weather is 1 day away. Using the Hotline, issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the cold weather system approaching tomorrow with temperatures anticipated to remain 32°F or below in three or more Weather Zones in the ERCOT Region. TOs are instructed to : - Review planned outages and existing outages for the possibility of withdrawing or restoring equipment. - Prepare for higher than usual loads. - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency Notice | When cold weather is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the cold weather system is in the ERCOT Region with temperatures 32°F or below in three or more Weather Zones in the ERCOT Region. The temperatures are beginning to have an adverse impact on the ERCOT System such as [state what the adverse impacts are]. TOs are instructed to: - Notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the severe cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Post | Issuance of an OCN, Advisory, Watch and Emergency Notice requires: Posting on MIS Public using Notice Builder. |
| Cancel Posting | Cancel postings on MIS Public using Notice Builder as required. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

## 8.3	Severe Cold Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for severe cold weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Severe cold weather notifications are called when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. |
| OCN |  | When approaching severe cold weather is approximately 5 days away. Using the Hotline, issue an OCN to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a severe cold weather system approaching in the next 5 days with temperatures anticipated to remain 32°F or below in three or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the severe cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory |  | When approaching severe cold weather is 3 days away. Using the Hotline, issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the severe cold weather system approaching in the next 3 with temperatures anticipated to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the severe cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch |  | When approaching severe cold weather is 1 day away. Using the Hotline, issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the severe cold weather system approaching tomorrow. Temperatures are expected to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Prepare for higher than usual loads, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the severe cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency Notice | When severe cold weather is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the severe cold weather system is in the ERCOT Region with temperatures between20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. The frigid temperatures are beginning to have adverse impact on the ERCOT System such as [state what the adverse impacts are]. - Prepare for higher than usual loads and the possibility of load shedding. - Review emergency operating procedures and immediately notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |  |
| Post | Coordinate with the Real-Time Operator for the posting of the notices on MIS Public using Notice Builder. |  |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on MIS Public. |  |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |  |

## 8.4	Other Significant Weather Events

Procedure Purpose:  Monitor severe weather conditions which can arise with little or no warning that can have an impact on the ERCOT grid.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: June 14, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight line winds - Hail - Severe lightening - Flooding |
| OCN/ Advisory/ Watch | When a significant weather event that could or does impact the ERCOT Region, make the proper notification. Using the Hotline, issue a notification to all TOs: Typical Script: “This call is requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [OCN/Advisory/Watch] due to [type of weather event] in the [location on the grid]. If you experience any issues as a direct result of the weather event, notify ERCOT. |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public using Notice Builder. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

## 9.1	Weekly Hotline Test

Procedure Purpose:  To perform a weekly communications test of the ERCOT Hotline phone system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.1.3(3) |  |  |  |
| NERC Standard | COM-001-1.1 R2 | EOP-005-1 R5 |  |  |

| Version: 1 | Revision: 1 | Effective Date: June 14, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | In the event of a failure of the Forum Conference Client software, the most recent printout of the Hotline log may be used to perform a manual roll call of TOs. |
| NOTE | Insure all Invalid Hotlines “Lost Souls” are cleared prior to the hotline call. |
| 1 | Each Monday between 0630 and 1100 test the ERCOT Hotline |
| 2 | Using the Hotline, notify all TOs of the purpose of the call. - When QSEs/TOs have answered the Hotline, print Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This is ERCOT Operator [first and last name]. ERCOT is conducting the weekly [TO] Hotline test. The following notices are currently in effect: - List OCNs, Advisories, Watches and/or Emergency Notices in effect. - State “None” if none are in effect. This ends the test of the ERCOT Hotline. That is all.” |
| 3 | Notify the Shift Supervisor of any TO that did not respond to the Hotline test. The Shift Supervisor and/or the Help Desk may notify the telecommunications department for repairs. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 - / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |