## Power Operations Bulletin # 541

ERCOT has posted/revised the DC Tie Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Approve E-Tags for the SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-2 R1.2 | INT-005-2 R1 | INT-006-2 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | TOP-002-2 R5, R9 |  |  |

| Version: 1 | Revision: 5 | Effective Date: June 17, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - AEP TOP located in Ohio is the DC Tie Operator (AEP DCT) for the DC_E (East tie) and DC_N (North tie) - If either DC Tie is over-scheduled, contact SPP Tariff (SPP TAR) |
| NOTE | ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties. |
| 1 | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria used to automatically validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCOT specified in the Physical Path IF: - Either of the above validations fail; THEN: - The E-Tag will be automatically denied. IF: - You feel an E-Tag failed validation erroneously; THEN: - Go to the list of approved ERCOT Registered QSE’s at the following website: http://www.ercot.com/mktparticipants/ - Select the “List of Market Participants in ERCOT Region”, - Select the DC Tie Scheduling List tab to view the ERCOT Registered QSEs. IF: - The QSE name is on the list but was denied by WebTrans; THEN: - Approve the E-Tag and inform the OATI help desk. WebTrans Reference Display: Tag >Validation Summary Scheduling>QSE Summary |
| 2 | When a New or Updated E-Tag is received in WebTrans system: Manually validate the following: - “ERCO” must not be listed as a PSE in Tag Information or Physical Path. - Time Zone should be CS (central standard) or CD (central daylight) - “Transaction type” must be “Energy or Normal” - “ERCOT-E” or “ERCOT-N” must be selected for the correct POR (Point-of-Receipt) or POD (Point of Delivery) in the Physical Path. - “CSWS” must be included as a Scheduling Entity on the SWPP TP row in the Physical Path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the Physical Path. (Note: If CSWS is listed in both the TP and GCA or LCA, this will cause double counting in the Tie Operators net-scheduled value so the “before the start of the hour” check out will not match. These type tags should be denied). - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section. - Start Time and Stop Time MUST NOT cross the midnight hour IF: - Any of the above information is incorrect; THEN: - Deny the E-Tag, otherwise proceed below. IF: - One or more E-Tags are submitted that will cause the DC Tie to be overscheduled; THEN: - Contact SPP Tariff (SPP TARF) approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule; they will take action to correct the over-schedule. If the correction is not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. IF: - ERCOT curtails an E-Tag due to an over-schedule that was not corrected in time; THEN: - Contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| NOTE | If verification needs to be made in the current day HRUC will be used unless it is a current hour tag. If verification needs to be made for the next day DRUC will be used. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. OATI: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name. |

## 3.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-2 R1.2 | INT-005-2 R1 | INT-006-2 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | IRO-005-2 R2 | TOP-002-2 R5, R9 |  |

| Version: 1 | Revision: 5 | Effective Date: June 17, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | AEP TO in Corpus Christi is the DC Tie Operator (AEP TDSP) for the DC_R (Railroad DC tie), DC_S (Eagle Pass DC tie), and the DC_L (Laredo VFT). All communications will be with the DC-Tie Operator and they will communicate with CFE. |
| NOTE | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC-Tie schedules are seen by our EMMS as a generator (import) or load (export). |
| NOTE | - ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties - The Railroad DC-Tie has a 15 MW minimum flow requirement, if E-Tags are scheduled - Approximately one hour before start of schedule, notify the ERCOT Transmission & Security Operator with scheduled MW, Tie and direction of flow and duration. |
| NOTE | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria ERCOT uses to validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCOT specified in the Physical Path If either of the above validations fail, the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the OATI help desk. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Summary Data>QSE Contracts |
| 1 | When a New or Updated E-Tag is received in the WebTrans system: Manually validate the following: - “ERCO” must not be listed as a PSE in the Tag Information or Physical Path. - Time Zone should be CS (central standard) or CD (central daylight) - “Transaction type” must be “Energy or Normal” - AEPT must be included as a TP (Transmission Provider) in the Physical Path and ERCO as a Scheduling Entity on the AEPT TP row in the Physical Path. - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section. - Start Time and Stop Time must NOT cross the midnight hour IF: - Any of this information is incorrect on the E-Tag; THEN: - Deny the E-Tag, otherwise proceed below. IF: One or more E-Tags are submitted that will cause the DC Tie to exceed the import/export limit for the tie; THEN: - Contact the DC Tie Operator approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule, - Call the PSE to have the E-Tag modified, if modification is not done 20 minutes before the start of the ramp then, - Curtail the E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the import/export limit for the tie. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| 2 | The ramp rate for DC_R will be 50 MW per minute due to reactive issues on the CFE side. DC_L and DC_S will be ramped across a 10 minute window. - Ramp Duration should be filled out on DC_R E-Tags only - Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered - DC_L and DC_S ramp duration can remain blank |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. WebTrans: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name |

## 3.7	Curtailment for the CFE DC Ties

Procedure Purpose: The process to curtail E-Tags for the CFE Ties.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | INT-004-2 R1 | INT-005-2 R1.1 | INT-010-1 R2 |  |

| Version: 1 | Revision: 4 | Effective Date: June 17, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE | Scheduling limits for the CFE DC Ties can change due to changes in generation, transmission configuration, and other system conditions. After receiving the import/export limits for next day, it may be necessary to have the PSE adjust E-Tags. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific amount, only CFE needs to approve the change. Adjustments are done by the PSE which requires all parties to approve. If it is after hours, CFE cannot approve adjustments. Curtailments will be automatically approved by them. |
| ### DC-Tie Trips |  |
| 1 | IF: - Any of the CFE DC-Ties trip, THEN: - ERCOT will have the responsibility to curtail the E-Tags. - Curtail the E-Tags, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE if not already done. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] due to [DC-Tie name] tripped. Please notify CFE. Please repeat this back to me. That is correct. Thank You.” |
| 2 | Once the DC-Tie that tripped is operational, re-load the curtailed E-Tag(s), if applicable: - Re-load curtailed E-Tag(s), - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE to approve re-loads if not already done. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. ERCOT has re-loaded curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name]. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank You” |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| ### Transmission Issues Within ERCOT |  |
| 1 | Due to ERCOT transmission issues it may be necessary to curtail E-Tag(s) using the Last-in-First-Out (LIFO). IF: - An E-tag needs to be cut immediately, THEN: - ERCOT must declare a Transmission Watch: - Identify from ERCOT Transmission & Security Operator if at least 20 – 30 minute notice can be given for curtailment, - Curtail the appropriate E-Tag(s), - Contact DC Tie Operator (AEP TDSP) with curtailment information, - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] DC-Tie starting at [xx:xx] due to transmission issues. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank You” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Once notified that transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s), - Ensure DC Tie Operator (AEP TDSP) sees the re-loaded E-Tags, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE to approve re-loads if not already done. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. At [xx:xx], the transmission issues within ERCOT have been resolved and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CFE to approve re-loads. Please repeat this back to me. That is correct. Thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. Repeat the steps above as necessary to get the tag(s) re-loaded. |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| ### Transmission Issues within CFE |  |
| 1 | Due to CFE transmission issues it may be necessary to curtail E-Tags using the Last-in-First-Out (LIFO). IF: - Notified by the DC Tie Operator or the ERCOT Transmission & Security Operator of CFE’s situation; THEN: - Identify if at least 20 – 30 minute notice can be given for curtailment, - Curtail the appropriate E-tag(s), - Contact DC Tie Operator (AEP TDSP) with curtailment information, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] DC-Tie starting at [xx:xx] due to issues within CFE. Please ramp the Tie accordingly. Please repeat this back to me. That is correct.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | IF: - CFE curtails schedules for their transmission issues; THEN: - Once curtailment is received from Webtrans, approve, AND - Notify DC Tie Operator (AEP TDSP) that they see the curtailment and will ramp the DC-Tie accordingly. Typical script to AEP TDSP: This is ERCOT operator [first and last name]. At [xx:xx] CFE has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to transmission issues within CFE. Please ramp the Tie accordingly. Please repeat this back to me. That is correct. Thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Once notified that transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s), - Ensure DC Tie Operator (AEP TDSP) sees the re-loaded E-Tags, AND - Instruct the DC Tie Operator (AEP TDSP) to make notification to CFE to approve re-loads if not already done. Repeat the steps above as necessary to get the tag(s) re-loaded. |
| 4 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, - Call the DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |

## 3.9	Managing Daily Inadvertent Energy for the CFE DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.1b R12.1 | INT-003-2 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 2 | Effective Date: June 17, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ROAD_DC, EGPS_DC, or LAR_VFT). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP TDSP). If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP TDSP) for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 5 MWH, overwrite the actual value in the WebTrans system. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Production Group to investigate problems with the meter information. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Ubtercgabge>ATF Checkout |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator (AEP TDSP): IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_L, DC_R and DC_S - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF Checkout |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Checkout Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_S, DC_R and DC_L DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

## 4.2	EEA 1 Schedule from SPP

Procedure Purpose: Steps to secure a schedule across the SPP DC tie(s) in an Energy Emergency Alert 1.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |
|  | IRO-006-5 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: June 17, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Met Center Turret Phone | - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC) on page 1 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP TAR) on page 1 - The DC Tie operator for the SPP DC-Ties can be reached using the Turret phone button labeled (AEP DCT) on page 6 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to. They can be reached using the Turret phone button labeled (AEP QSE) on page 2 |
| NOTE | For an EEA 1, only non-firm transmission service is available. For EEA 2 or 3, emergency transmission service is available. This is the reason for the two different procedures. |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. |
| 1 | IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag), THEN: - Curtail (usually done one hour at a time) IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag - Notify the Shift Supervisor |
| 2 | IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DCT). |
| 3 | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. We will inquire about the availability of transmission service, please transfer me to the Tariff desk.” |
| 4 | Notify the SPP Tariff desk (SPP TARF) to determine the availability of transmission service across the SPP DC-Ties for an EEA 1 schedule. Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie to start a schedule into ERCOT?” If no current hour transmission service is available, do not proceed and make log entry. If status changes from EEA 1 to EEA 2A, 2B, or 3 proceed to Section 4.3 Only continue to the next step if there is transmission service available |
| 5 | Notify AEP QSE (AEP QSE): Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” If no available capacity, do not proceed and make log entry. If there is available capacity (procure whatever amount is available), ask AEP QSE to arrange for the submission of the transmission request and the E-tag(s). |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 6 | If ERCOT will be receiving an EEA 1 schedule, notify the DC Tie Operator (AEP DCT): Typical Script: “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and the E-Tag (s) for an EEA 1 schedule. |
| 7 | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State which DC Ties in Other Information - End time will be the same as initiation time (back office will take care of the rest) |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 - / 1 - / 2 - / 2 - / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans referrences Updated step 1 | June 17, 2011 |