## Power Operations Bulletin # 542

ERCOT has posted/revised the DC Tie Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Approve E-Tags for the SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-2 R1.2 | INT-005-2 R1 | INT-006-2 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | TOP-002-2 R5, R9 |  |  |

| Version: 1 | Revision: 6 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - AEP TOP located in Ohio is the DC Tie Operator (AEP DCT) for the DC_E (East tie) and DC_N (North tie) - If either DC Tie is over-scheduled, contact SPP Tariff (SPP Tariff) |
| NOTE | ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties. |
| 1 | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria used to automatically validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCO specified in the Physical Path IF: - Either of the above validations fail; THEN: - The E-Tag will be automatically denied. IF: - You feel an E-Tag failed validation erroneously; THEN: - Go to the list of approved ERCOT Registered QSE’s at the following website: http://www.ercot.com/mktparticipants/ - Select the “List of Market Participants in ERCOT Region”, - Select the DC Tie Scheduling List tab to view the ERCOT Registered QSEs. IF: - The QSE name is on the list but was denied by WebTrans; THEN: - Approve the E-Tag and inform the OATI help desk. WebTrans Reference Display: Validation > Tag Validation Monitor |
| 2 | When a New or Updated E-Tag is received in WebTrans system: Manually validate the following: - “ERCO” must not be listed as a PSE in Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard) or CD (central daylight) - “Transaction type” must be “Energy or Normal” - “ERCOT-E” or “ERCOT-N” must be selected for the correct POR (Point-of-Receipt) or POD (Point of Delivery) in the Physical Path - “CSWS” must be included as a Scheduling Entity on the SWPP TP row in the Physical Path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the Physical Path. (Note: If CSWS is listed in both the TP and GCA or LCA, this will cause double counting in the Tie Operators net-scheduled value so the “before the start of the hour” check out will not match. These type tags should be denied) - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section - Multi day tags are acceptable but the Start Time and Stop Time MUST NOT cross the midnight hour (Separate tag for each day) IF: - Any of the above information is incorrect; THEN: - Deny the E-Tag, otherwise proceed below. IF: - One or more E-Tags are submitted that will cause the DC Tie to be overscheduled; THEN: - Contact SPP Tariff (SPP Tariff) approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule; they will take action to correct the over-schedule. If the correction is not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. IF: - ERCOT curtails an E-Tag due to an over-schedule that was not corrected in time; THEN: - Contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| NOTE | If verification needs to be made in the current day HRUC will be used unless it is a current hour tag. If verification needs to be made for the next day DRUC will be used. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. OATI: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name. |

## 3.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-2 R1.2 | INT-005-2 R1 | INT-006-2 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | IRO-005-2 R2 | TOP-002-2 R5, R9 |  |

| Version: 1 | Revision: 6 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | AEP TO in Corpus Christi is the DC Tie Operator (AEP TDSP) for the DC_R (Railroad DC tie), DC_S (Eagle Pass DC tie), and the DC_L (Laredo VFT). All communications will be with the DC-Tie Operator and they will communicate with CFE. |
| NOTE | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC-Tie schedules are seen by our EMMS as a generator (import) or load (export). |
| NOTE | - ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties - The Railroad DC-Tie has a 15 MW minimum flow requirement, if E-Tags are scheduled - Approximately one hour before start of schedule, notify the ERCOT Transmission & Security Operator with scheduled MW, Tie and direction of flow and duration. |
| NOTE | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria ERCOT uses to validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCOT specified in the Physical Path If either of the above validations fail, the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the OATI help desk. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Summary Data>QSE Contracts |
| 1 | When a New or Updated E-Tag is received in the WebTrans system: Manually validate the following: - “ERCO” must not be listed as a PSE in the Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard) or CD (central daylight) - “Transaction type” must be “Energy or Normal” - AEPT must be included as a TP (Transmission Provider) in the Physical Path and ERCO as a Scheduling Entity on the AEPT TP row in the Physical Path - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section - Multi day tags are acceptable but the Start Time and Stop Time must NOT cross the midnight hour (Separate tag for each day) IF: - Any of this information is incorrect on the E-Tag; THEN: - Deny the E-Tag, otherwise proceed below. IF: One or more E-Tags are submitted that will cause the DC Tie to exceed the import/export limit for the tie; THEN: - Contact the DC Tie Operator approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule, - Call the PSE to have the E-Tag modified, if modification is not done 20 minutes before the start of the ramp then, - Curtail the E-Tag(s) to the amount needed based on Last-in-first-out (LIFO) until under the import/export limit for the tie. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| 2 | The ramp rate for DC_R will be 50 MW per minute due to reactive issues on the CFE side. DC_L and DC_S will be ramped across a 10 minute window. - Ramp Duration should be filled out on DC_R E-Tags only - Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered - DC_L and DC_S ramp duration can remain blank |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. WebTrans: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name |

## 3.6	Adjustment of CFE DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-Tags.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 |  |  |  |
| NERC Standard | INT-004-2 R1 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Imports |  |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the Net Scheduled Interchange (NSI). |
| 1 | IF requested by the DC Tie Operator (AEP TDSP), checkout the Net Scheduled Interchange (NSI) value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |
| ### Exports |  |
| 1 | Notify the ERCOT Transmission Operator when E-Tag Net Export adjustments are greater than 100 MW during the Adjustment Period. |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the Net Scheduled Interchange (NSI). |
| 2 | IF requested by the DC Tie Operator (AEP TDSP), checkout the Net Scheduled Interchange (NSI) value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 3.7	DC-Tie Trips

Procedure Purpose: The process when DC-Ties trip.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | INT-004-2 R1 | INT-005-2 R1.1 | INT-010-1 R2 |  |

| Version: 1 | Revision: 5 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### CFE DC-Ties |  |
| 1 | IF: - Any of the CFE DC-Ties trip, THEN: - ERCOT will have the responsibility to curtail the E-Tags. - Curtail the E-Tags for the Tie that tripped (see Desktop Guide if needed), AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] due to [DC-Tie name] tripped. Please notify CFE. Please repeat this back to me. That is correct. Thank You.” |
| 2 | Once the DC-Tie that tripped is operational, re-load the curtailed E-Tag(s), if applicable: - Re-load curtailed E-Tag(s) (see Desktop Guide if needed), - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE to approve re-loads. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. ERCOT has re-loaded curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name]. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank You” |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| ### SPP DC-TIES |  |
| 1 | IF: - Any of the SPP DC-Ties trip, THEN: - SPP has the responsibility to curtail the E-Tags. |

## 3.9	Managing Daily Inadvertent Energy for the CFE DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.1b R12.1 | INT-003-2 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 3 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored frequently enough during the day to ensure that large inadvertent flows don’t accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ROAD_DC, EGPS_DC, or LAR_VFT). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP TDSP). If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP TDSP) for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 5 MWH, overwrite the actual value in the WebTrans system with a whole number. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 5 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Production Group to investigate problems with the meter information. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Interchange>ATF Checkout |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator (AEP TDSP): IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_L, DC_R and DC_S - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF Checkout |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and email it to the Manager of System Operations. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Checkout Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_S, DC_R and DC_L DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

## 3.11	Loss of E-Tagging

Procedure Purpose: Contingency plan for loss of E-tagging capability

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | If the WebTrans system goes down for an unknown reason (i.e. maintenance), contact the ERCOT Operator at the primary control center to check on their connectivity. If their system is also down, contact the OATI helpdesk (OATI HELP) to see if the issue is on their end. If issue is not on the OATI end, contact the ERCOT helpdesk (HELP DESK). |
| 2 | Determine the estimated down time, if longer than 30 minutes, notify the SPP Tariff Operator (SPP Tariff) and the DC-Tie Operators (AEP DCT/AEP TDSP). |
| 3 | Post message on MIS Public utilizing Notice Builder: Typical MIS Posting: “ERCOT ISO E-tagging system is down; we are unable to accept new schedules across the DC-Ties at this time”. |
| 4 | No new E-tags will be accepted, only curtailments: - Coordinate with the SPP Tariff Operator (SPP Tariff) and the appropriate DC-Tie Operator - Notify Real-Time Operator to determine if SCED needs to be manually executed for curtailments |
| NOTE | Before-the-fact and after-the-fact check outs will not be available |
| 5 | Once the WebTrans system is available, confirm SPP Tariff (SPP Tariff) and the DC-Tie Operators availability. If available for all parties: - Update the MIS Public posting by sending a “Notice Cancellation” If curtailments were made while the WebTrans system was down, ensure E-tags are updated |

## 4.1	ERCOT Declares EEA 1

Procedure Purpose: Steps to perform when ERCOT declares an Energy Emergency Alert (EEA) 1.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |
|  | IRO-006-5 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE DC-Ties can be reached using the Turret phone button labeled (AEP TDSP) - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC) - SPP Tariff operator can be reached using the Turret phone button labeled (SPP Tariff) - The DC Tie operator for the SPP DC-Ties can be reached using the Turret phone button labeled (AEP DCT) - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to. They can be reached using the Turret phone button labeled (AEP QSE) |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC-Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC-Ties. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. |
| Comision Federal de Electricidad (CFE) |  |
| 1a | IF: - There are export schedules on any CFE DC-Tie; THEN: - Curtail (see Desktop Guide if needed) - Contact DC Tie Operator (AEP TDSP) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | IF: - There is export inadvertent payback flowing to CFE; THEN: - Stop inadvertent payback by contacting the DC-Tie Operator (AEP TDSP) Typical Script to DC Tie Operator (AEP TDSP): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC-Tie] be ramped to zero. Please notify CFE.” |
| 3a | Contact DC-Tie Operator (AEP TDSP) and request them to contact CFE to inquire about the availability of emergency energy on all available CFE DC-Ties. IF: - Emergency energy is available; THEN: - Request the DC-Tie Operator to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP QSE (AEP QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| 4a | IF: - CFE can not supply ERCOT with emergency energy; THEN: - Make log entry with information. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1”. |
| 2b | IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide if needed) Typical script to DC Tie Operator (AEP DCT): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag (see Desktop Guide if needed) - Notify the Shift Supervisor |
| 3b | IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DCT). Typical Script to DC Tie Operator (AEP DCT): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1 and is requesting the inadvertent payback on [name DC-Tie] go to zero.” |
| 4b | IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC-Tie Operator (AEP DCT) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DCT): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | IF: - The SPP DC-Ties are not at maximum import into ERCOT; THEN: - Notify the SPP Tariff desk (SPP Tariff) to determine the availability of transmission service for an EEA 1 schedule. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie to start a schedule into ERCOT?” IF: - No current hour transmission service is available; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor IF: - Status changes from EEA 1 to EEA 2A, 2B, or 3; THEN: - Proceed to Section 4.2 |
| 6b | IF: - Transmission service is available; THEN: - Notify AEP QSE (AEP QSE): Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” IF: - No available capacity; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor. IF: - Capacity is available; THEN: - Request - AEP QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you” NOTIFY: - DC Tie Operator (AEP DCT): Typical Script for DC Tie Operator (AEP DCT): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and the E-Tag (s) for an EEA 1 schedule. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency into ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 1 to EEA 2. Thank you”. If moved to EEA 2 or 3 proceed to section 4.2, ERCOT Declares EEA 2 or 3. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide if needed) - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all actions taken. |

## 4.2	ERCOT Declares EEA 2 or 3

Procedure Purpose: Steps to secure emergency energy across the DC tie(s) in an Energy Emergency Alert (EEA) 2 or 3.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |
|  | IRO-006-5 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE ties can be reached using the Turret phone button labeled (AEP TDSP) - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC) - SPP Tariff operator can be reached using the Turret phone button labeled (SPP Tariff) - The DC Tie operator for the SPP DC Ties can be reached using the Turret phone button labeled (AEP DCT) - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to. They can be reached using the Turret phone button labeled (AEP QSE) |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC-Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC-Ties. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| EEA | When notified by Hotline that ERCOT has declared EEA 2 or 3, proceed with this procedure. |
| Comision Federal de Electricidad (CFE) |  |
| 1a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There are export schedules on any CFE DC-Tie; THEN: - Curtail (see Desktop Guide if needed) - Contact DC Tie Operator (AEP TDSP) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback flowing to CFE; THEN: - Stop inadvertent payback by contacting the DC-Tie Operator (AEP TDSP) Typical Script to DC Tie Operator (AEP TDSP): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC-Tie] be ramped to zero. Please notify CFE.” |
| 3a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. Contact DC-Tie Operator (AEP TDSP) and request them to contact CFE to inquire about the availability of emergency energy on all available CFE DC-Ties. IF: - Emergency energy is available; THEN: - Request the DC-Tie Operator to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP QSE (AEP QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| 4a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - CFE can not supply ERCOT with emergency energy; THEN: - Make log entry with information. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Thank you.” |
| 2b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide if needed). Typical script to DC Tie Operator (AEP DCT): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag, - Notify the Shift Supervisor. |
| 3b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DCT). Typical Script to DC Tie Operator (AEP DCT): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3] and is requesting the inadvertent payback on [name DC-Tie] go to zero.” |
| 4b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC-Tie Operator (AEP DCT) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DCT): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | Complete this step if in EEA 1 there was no non-firm transmission service available or EEA 1 was skipped. Notify the SPP Tariff desk (SPP Tariff) to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” IF: - No emergency transmission service is available, THEN: - Do NOT proceed and make log entry. - Notify Shift Supervisor |
| 6b | IF: - Emergency transmission service is available; THEN: - Request emergency energy from AEP QSE (AEP QSE) Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” IF: - No available capacity, THEN: - Do NOT proceed and make log entry. IF: - Capacity is available; THEN: - Request - If there is available capacity (procure whatever amount is available), askAEP QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you.” NOTIFY: - DC Tie Operator (AEP DCT): Typical Script for DC Tie Operator (AEP DCT): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and the E-Tag (s) for emergency energy into ERCOT. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 2 to EEA 3. Thank you”. IF EEA 1 has ended continue with this procedure. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC); Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide if needed), - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all action taken |

4.3	Emergency Energy to CFE

Procedure Purpose: Provide Emergency Energy to CFE across the DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R1 | INT-010-1 R3 |  |  |

| Version: 1 | Revision: 5 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If CFE requests the emergency energy, no emergency notification needs to be declared by ERCOT. |
| 1 | IF: - Notified by the ERCOT Transmission Operator or the DC Tie Operator (AEP TDSP) of CFEs emergency situation; THEN: - Identify if CFE has export schedule(s) that can be curtailed, if CFE has no exports, proceed to step 2, - Curtail the appropriate E-Tag(s) (see Desktop Guide if needed), - Contact the DC Tie Operator (AEP TDSP) when curtailment is complete and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to CFEs emergency situation. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | IF: - CFE has export inadvertent payback flowing into ERCOT; THEN: - Notify DC Tie Operator (AEP TDSP) to stop inadvertent payback Typical Script to DC Tie Operator (AEP TDSP): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting the inadvertent payback being imported to ERCOT on [name DC-Tie] go to zero due to CFEs emergency situation. Please repeat this back to me. That is correct. Thank you.” |
| 3 | IF: - Notified by the ERCOT Transmission Operator or the DC Tie Operator (AEP TDSP) that CFE is requesting emergency energy; THEN: - Verify with the ERCOT Transmission Operator that sending emergency energy to CFE would not put ERCOT in an insecure state, IF: - ERCOT is able to send CFE emergency energy; THEN: - Request the DC-Tie Operator (AEP TDSP) to ramp the appropriate DC-Tie with the amount of emergency energy that ERCOT is able to send, Typical script to DC-Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT will send [amount] of emergency energy on [DC-Tie(s)] Please ramp Ties accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” - Notify Shift Supervisor - Issue AEP QSE (AEP QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to CFE” and which DC-Ties in “Other Information” - End time will be the same as initiation time. - Notify AEP QSE (AEP QSE) to acknowledge the VDI. |
| 4 | WHEN: - Notified that CFEs emergency has ended; THEN: - Perform/verify the following: - End Emergency Energy, if appropriate - Re-load E-Tag(s), if appropriate (see Desktop guide if needed) - Restart import inadvertent payback, if appropriate |
| Log | Log all actions taken. |

## 4.4	Emergency Energy to SPP

Procedure Purpose: Steps to provide emergency energy to Southwest Power Pool across the SPP DC ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP 001-0 R1 | INT-010-1 R3 |  |  |

| Version: 1 | Revision: 5 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - Notified by SPP that emergency energy is needed; THEN: - Verify with the ERCOT Transmission Operator that providing emergency energy will not put ERCOT in an insecure state. |
| 2 | IF: - ERCOT is able to send SPP emergency energy; THEN: - Inform SPP of the amount - An E-Tag will be submitted - Issue AEP QSE a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State Emergency Energy to SPP and which DC-Ties in Other Information - End time will be the same as initiation time (back office will take care of the rest). - Notify AEP QSE (AEP QSE) to acknowledge VDI. |

## 4.5	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose: The process to curtail E-Tags for the CFE Ties and request emergency energy is needed.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001 R3.1, R4.2 | INT-004-2 R1 | INT-005-2 R1.1 | INT-010-1 R2 |

| Version: 1 | Revision: 5 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific amount, only CFE needs to approve the change. Curtailments will be automatically approved by them. Adjustments are done by the PSE which requires all parties to approve. |
| ### Transmission Issues within ERCOT |  |
| 1 | Due to ERCOT transmission issues it may be necessary to curtail export E-Tag(s) using the Last-in-First-Out (LIFO). IF: - Notified by the ERCOT Transmission Operator of the need to curtail exports on a specific DC-Tie; THEN: - Ask if E-tag(s) needs to be cut immediately or if at least 30 minute notice can be given; IF: - Curtailment needs to take place immediately, proceed with this step. If at least 30 minutes can be given proceed to step 2. THEN: - Verify with ERCOT Transmission Operator that a Transmission Watch or Emergency has been declared, - Curtail the appropriate E-Tag(s) (see Desktop Guide if needed), - Contact DC Tie Operator (AEP TDSP) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] starting at [xx:xx] due to transmission issues within ERCOT. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | IF: - At least 30 minute notice can be given (Issuance of Watch/Emergency is not needed), THEN: - Curtail the appropriate E-Tag(s), - Contact DC Tie Operator (AEP TDSP) with curtailment information and instruct them to make notification to CFE Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] starting at [xx:xx] due to transmission issues within ERCOT. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank You” . |
| 3 | Once notified by the ERCOT Transmission Operator that the transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s) (see Desktop Guide if needed), - Ensure DC Tie Operator (AEP TDSP) sees the re-loaded E-Tags, and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. At [xx:xx], the transmission issues within ERCOT have been resolved and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CFE to approve re-loads. Please repeat this back to me. That is correct. Thank you.” |
| 4 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 5 | IF: - Notified by the ERCOT Transmission Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.1 Emergency Energy from CFE. |
| LOG | Log all actions taken. |
| ### Transmission Issues within CFE |  |
| 1 | Due to CFE transmission issues it may be necessary to curtail import E-Tag(s) for them. IF: - Notified by the ERCOT Transmission Operator or the DC Tie Operator (AEP TDSP) of a need to curtail imports on specific CFE DC-Tie(s); THEN: - Curtail the appropriate E-Tag(s) (see Desktop Guide if needed), - Contact the DC Tie Operator (AEP TDSP) when curtailment is complete and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TDSP): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to transmission issues within CFE. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified that transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s) (see Desktop Guide if needed), - Ensure DC Tie Operator (AEP TDSP) sees the re-loaded E-Tags, and instruct them to make notification to CFE. |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, - Call the DC Tie Operator (AEP TDSP) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.4, Emergency Energy to CFE. |
| LOG | Log all actions taken. |

## 4.6	Loss of Primary Control Center Functionality

Procedure Purpose: To be performed by the Operator at the alternate Control Center (ACC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1.1 R5 | EOP-001-0 R4.4 | EOP-008-0 | IRO-005-2 R1.10 |

| Version: 1 | Revision: 5 | Effective Date: June 8, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Contact Security | IF: - Unable to reach any Operator at the PCC (cell phone or PBX Bypass phones); THEN: - Check the Control Room video camera to determine the status of the PCC and personnel, - Contact Security at the ACC - Notify them of the situation AND - Have them attempt to make contact with Security at PCC. - Have them contact you with information acquired OR IF: - Notified by the PCC that they are evacuating and/or transferring sites; THEN: - Continue with procedure. |
| Constant Frequency | IF: - The loss of PCC involves the loss of EMS (LFC and RLC/SCED; THEN: - Determine which QSE has ample Capacity to place on Constant Frequency Control. (REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data) - Direct that QSE to go on “Constant Frequency”, by issuing an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into “Monitor” mode. |
| QSE Hotline Call | Hotline call for EMS (LFC and RLC/SCED) failure: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to loss of primary control center functionality, LFC and SCED failure. ERCOT has put a QSE on constant frequency. All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT. ERCOT may issue unit specific deployments to any Resources as required. Direct all urgent phone calls thru the [Austin][Taylor] OPX. [Select QSE], “Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Hotline call with systems functional: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center functionality and is transferring operations to the alternate control center. Direct all urgent phone calls thru the [Austin][Taylor] OPX. All ERCOT systems are functioning at this time. HRUC will be delayed until additional staffing arrives and Day-Ahead Market functions may be delayed” [Select QSE], “Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| TO Hotline Call | Hotline call for EMS (LFC and RLC/SCED) failure and if Systems are functional: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center functionality and is transferring operations to the alternate control center. Please monitor your own service area and notify ERCOT if you exceed the normal rating of your transmission elements. Report West - North stability limit when power flows reach 70% and North – Houston stability limit power flows reaches 90% of the last posted limit. Continue to monitor voltages in your area and notify ERCOT of any forced line operations. Direct all urgent phone calls thru the [Austin][Taylor] OPX. [Select TO], Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| Nuclear Plants | If systems are NOT functional: Notify the appropriate Nuclear Plants QSE and inform them that they should notify the Resource that ERCOT has issued an Emergency Notice and RTCA and State Estimator is not functional. This is expected to last for approximately 1 hour. If systems are functional: Notify the appropriate Nuclear Plants QSE and inform them that they should notify the Resource that ERCOT has issued an Emergency Notice and is currently operating with one operator and RTCA results will not be viewed in a timely manner. This is expected to last for approximately 1 hour. |
| MIS Posting | As time permits, post the Emergency Notice in the Public MIS using Notice Builder. |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Austin. Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| Additional Notifications | Manager of System Operations and/or designee will notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support These phone numbers are also programmed into the control room cell phone. |
| Monitor Critical Facilities | Potential critical facilities will be apparent to the Operator by notification from TOs based on the information ERCOT has requested within the Hotline Call instructions. Critical facilities will be those that show up in RTCA. ERCOT considers the list of critical facilities to be the contingencies posted on the MIS. Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. |
| Respond to QSEs | If systems are NOT functional: IF: - The QSE that is put on constant frequency is having trouble controlling frequency; THEN: - Issue unit specific VDIs to other QSEs to help with Regulation, - Choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). If systems are functional: Monitor frequency and re-run SCED/use (manual offset) as needed. IF: - QSEs call in with questions about RUC; THEN: - Notify the QSE that the RUC functions will resume when additional staff arrive, - Document QSE calls to pass along the appropriate Operators as they arrive. |
| Respond to TOs | IF: - TOs call in to report the following: - Thermal limits have reached their continuous rating, - West-North stability limit has reached 70% of its limit, - North-Houston stability limit has reached 90% of its limit, THEN: - Take immediate action, as listed below, for thermal limits and stability limits, |
| Stability Limits (IROL) | IF: - The West-North stability limit is approaching 70% and is continuing to trend upward, - The North-Houston stability limit is approaching 90% and is continuing to trend upward; THEN: - Take immediate action to lower Wind Generation in the west by activating the west-north if systems are functional, OR - Issue unit specific VDIs as necessary to relieve the congestion, - Choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level - If VDIs are issued, monitor QSE on constant frequency |
| Thermal Limits Reached (SOL) | IF: - Thermal limits have reached their continuous rating and are continuing to trend upward, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - Issue unit specific VDIs as necessary, - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Log | - Make log entry of events. |

## 4.7	Restoration of Primary Control Center Functionality

Procedure Purpose: To be performed once additional staff has reported to the alternate Control Center and Grid can return to normal operations.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: March 25, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE: | As additional Operators arrive, communicate any pertinent information that will assist them in getting their specific functions ready for normal operation. |
| Additional Operators | When a Real-Time Operator has arrived, turn over frequency control to that Operator and assist with other needs such as approve any E-Tags waiting. |
| Notification of Additional Operators | WHEN: - Fully staffed; THEN: - Make notification using the NXT - SO Loss of CC Operations Resumed. |
| Help Desk | Make notification to Help Desk that the Control Room is now back to normal operations from the alternate. |
| Contact Security | Notify Security that the transition of Operations to the ACC has been completed. |
| Log | Make log entries as needed. |

## 4.8	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 5 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - When cold weather is 5 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region - When severe cold weather is 5 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### ADVISORY |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When cold weather is 3 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 3 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### WATCH |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When cold weather is 1 day away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 1 day away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT varies from time-line for DAM/DRUC. |
| ### EMERGENCY NOTICE |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED). - When cold or severe cold weather is in the ERCOT Region and it is beginning to have an adverse impact on the ERCOT System. |
| ### Notifications |  |
| HOTLINE | Notify QSEs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| POST | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the only option is “public” - For “free form” messages, the “Notice priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| LOG | Make log entry. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 - / 1 - / 2 - / 2 - / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 - / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |