## Power Operations Bulletin # 543

ERCOT has posted/revised the Real Time Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.6	Site Failovers and Database Loads

Procedure Purpose: To provide notice to the Market Participants when ERCOT performs site failovers and database loads.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Database Load | Approximately 5 - 30 minutes before database load, make the following Hotline call to QSEs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a database load on its Energy & Market Management Systems. During this time, SCED Base Points will reflect accurate dispatch instructions. In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes. |
| Site Failover | Approximately 5 - 30 minutes before site failover, make the following Hotline call to QSEs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 15 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. |
| Site Failover with W-N Active | IF: - The West – North is active; Then: - MP’s base points should remain the same during the failover, however to ensure the management of WGR’s is sustained, use the following script: Approximately 5 minutes before the site failover, make the following Hotline call to QSEs: Typical Script: At [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 15 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. The West to North constraint is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output during this failover. A call will be made when we have completed the site failover. |
| Site Failover Posting | The site failover message is already built in Notice Builder under “EMS Site Failover”. |
| If EBPs are needed | IF: - Site Failover is taking longer than expected and EBPs are needed; Then: - Make the following hotline call to QSEs: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. The site failover is taking longer than expected; Emergency Base Points will be issued. ERCOT will make another hotline call when the site failover is complete. [QSE] please repeat this back to me. That is correct, thank you.” |
| If EBPs are needed and W-N was Active before Site Failover started | IF: - Site Failover is taking longer than expected and EBPs are needed, AND - The West – North was active before the start of the Site Failover; Then: - Make the following hotline call to QSEs: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. The site failover is taking longer than expected; Emergency Base Points will be issued. WGRs which were required to follow their Base Point instruction before the site failover are required to continue to stay at their current output. ERCOT will make another hotline call when the site failover is complete. [QSE] please repeat this back to me. That is correct, thank you.” |
| Site Failover Complete | Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [XX:XX], the site failover is complete. All QSEs should continue normal operations. [QSE] please repeat this back to me. That is correct, thank you.” |

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.3.2(2) | 6.5.7.6.2.2 | 6.5.9.1(1)(b) | 8.2 (2)(b)(vii) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.3.1.2 |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6, R7, R8 | BAL-005-0.b R8 | BAL-007 (Field Trial) | EOP-002-2.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 587 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -587 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, - Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) |
| Base Point Deviation | IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) - If unit trip: - Time of unit trip, - Name of unit, - Approximate net MW on unit, - Approximate lowest frequency, - Amount of RRS deployed (if any), AND - Approximate ERCOT load. |
| Automatic SCED Runs | LFC triggers automatically when one of the following occurs: - Frequency reaches 59.91 Hz or below, SCED runs within a minute of LFC trigger - If frequency stays below 59.95 for more than 50 seconds, LFC triggers SCED to run |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: - QSE will request VDI(s) - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time - A VDI will be needed for each Resource IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per deployment for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency is above 60.05 Hz and continuing to climb or exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - CHECK the (Gen-LDL) to ensure there is adequate down room, - Manually run SCED. IF: - Frequency is above 60.05 Hz and continuing to climb or exceeds 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the (GEN-LDL) to ensure there is adequate down room, - Enter manual offset (the offset will continue until removed). IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| 10 MINUTES | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points (GEN-LDL), - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points (GEN-LDL), - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Shift Engineer to send an event notification to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.75 Hz - Load Resource providing RRS – 59.7 Hz |
| Monitor/ Deploy | IF: - Frequency is below 59.95 Hz and continuing to drop or is below 59.95, AND - Regulation Up service remains and is deploying; THEN: - Check the (GTBD_TO_HDL) on the OpsMon SCED GEN ONLINE Dashboard, and enter appropriate manual offset - Do Not enter an offset > than (GTBD_TO_HDL) - Manually run SCED (do not run SCED more than once between SCED runs). IF: - Frequency is below 59.95 Hz and continuing to drop or is below 59.95, AND - Out of Up Regulation; THEN: - Check the GTBD_TO_HDL on the OpsMon SCED GEN ONLINE Dashboard and enter appropriate manual offset - Do Not enter an offset > than (GTBD_TO_HDL) - If the OpsMon Dashboard is not available, check the EMS and enter appropriate manual offset (the offset will continue until removed) - Do Not enter an offset > than (HDL-GEN) IF: - Frequency is below 59.95 Hz, AND - (GTBD_TO_HDL) on the OpsMon SCED GEN ONLINE Dashboard does not have adequate up room; THEN: - Manually deploy Responsive Reserve using the “ERCOT Nodal Summary” display on the EMS - Check the “Manual RRS” to activate box, - Enter the “Desired RRS MW”, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - Do Not enter an offset > than (HDL-GEN) - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Notify the Shift Supervisor of the need to possibly commit additional Resources: - Resource Operator will issue a VDI for intra-hour - Notify RUC Operator for the next HRUC run. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED, - Log the event and notify Shift Engineer to send notification of the event to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED. |
| Stable | IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Austin) |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Contact the Help Desk. |

## 5.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 6 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Projected Reserve Capacity Shortage that could affect System Reliability and may require more Resources. - When cold weather is 5 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region - When severe cold weather is 5 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Unplanned Transmission Outages that may impact System Reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse Reliability impacts and Contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When cold weather is 3 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 3 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term Operating Reliability. - In such circumstances ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market (DAM) in accordance with ERCOT Procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission System conditions are such that operations within first contingency criteria are not likely or possible due to Forced Outages or other conditions. - Loss of communications or a control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from the Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 1 day away. - When cold weather is 1 day away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 1 day away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - A Transmission condition has been identified that requires Emergency Energy from any of the CFE DC-Ties. - Conditions have developed that require additional Ancillary Services in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based Congestion Management techniques embedded in SCED will not be adequate to resolve Transmission Violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require Operations with active Transmission Violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the Reliability of the ERCOT System. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. - ERCOT varies from time-line for DAM/DRUC. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum Reliability Standards during the Operating Period utilizing every Resource practically obtainable from the Market - ERCOT forecasts an inability to meet applicable Reliability Standards and has exercised all other reasonable options - A Transmission condition has been identified causing unreliable Operation or overloaded elements - A Single Severe Contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements for which no practicable Resource solution exists - ERCOT has determined a fuel shortage exists that would affect Reliability - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED) - When cold or severe cold weather is in the ERCOT Region and it is beginning to have an adverse impact on the ERCOT System. |
| ### Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify QSEs: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public utilizing Notice Builder. - For “free form” messages, the “Notice Priority” will be specified as follows: - OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Log all actions taken. |

## 5.2	Responding to Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for the purpose of providing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.9.4.1 | 6.5.9.4(5) | 6.5.7.6.2.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.1(1) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002 R2.4 | EOP-001 R3.1 | EOP-002 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005-2 R1.4, R1.5, R4 |

| Version: 1 | Revision: 4 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at Management’s discretion, may issue an appeal through the Public News Media for voluntary energy conservation at any time. - System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. |
| ### Advisory |  |
| 1 | IF: - PRC < 3000 MW; THEN: - Using the Hotline, issue an Advisory, AND - Instruct the Resource Desk Operator to post a message on MIS Public utilizing Notice Builder. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory due to Physical Responsive Capability falling below 3000 MW. Please ensure you are telemetering correct HSL values. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure that all actions taken have been logged. |
| ### Watch |  |
| 1 | IF: - PRC < 2500 MW, THEN: - Coordinate with the Resource Operator to deploy Non-Spin Reserve Service, - Using the Hotline, issue a Watch, AND - Instruct the Resource Desk Operator to post a message on MIS Public utilizing Notice Builder. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to Physical Responsive Capability falling below 2500 MW. Please ensure you are telemetering correct HSL values. Suspend all Resource testing and update telemetered Resource Status Codes. ERCOT is reminding you, that you can schedule available interchange into ERCOT across the DC Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Ensure that all actions taken have been logged. |
| ### Cancelation |  |
| 1 | IF: - (HDL-GEN) ≥ 500 MW, - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Resource Operator to recall half of the Non-Spin IF: - (HDL-GEN) ≥ 1000 MW, - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Resource Operator to recall all Non-Spin, AND - Using the Hotline cancel the Watch. Typical script: “This is ERCOT Operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. At this time, the Advisory is still in effect. Resource testing may resume. [QSE] please repeat this back to me. That is correct, thank you.” Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Advisory for Physical Responsive Capability. Physical Responsive Capability is now above 3000 MW. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| ### Version: 1 | Revision: 4 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls < 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls < 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA. When a media appeal for voluntary energy conservation is enacted, QSEs should be notified via Hotline call (see EEA 2A for typical script). - Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore Reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Select the activate EEA flag in EMS, - Using the Hotline, notify all QSEs to implement EEA 1. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is declaring EEA 1, QSEs are to ensure: - COPs and HSLs are current, - Resource are not to be taken off-line while ERCOT is in emergency operations unless it is due to a forced outage, - Suspend any Resource testing, AND - ERCOT is reminding you, that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2A |  |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Typical Script: “This is ERCOT Operator [first and last name]; this is a courtesy call to inform you that ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. |
| 1 | IF: - PRC < 1750 MW; THEN: - Once the Resource Desk has completed the deployment of the Load Resources (XML deployments must be made before the Hotline call) providing RRS as follows: - Less than 1750 MW, deploy Group 1. - As system conditions require, deploy remaining load resources. - Less than 1375 MW deploy both Groups 1 and 2 simultaneously. - Using the Hotline, notify all QSEs to implement EEA 2A and any measures associated with EEA 1, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2A and has deployed [Group 1/Group 1 & 2] Load Resources. Also: - Implement all measures associated with EEA 1, if not already implemented. - Do not take units off-line while ERCOT is in Emergency Operations unless it is due to a forced outage. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2B |  |
| NOTE | If no EILS exists, skip EEA 2B and proceed to EEA 3. |
| 1 | Deploy all EILS as a single block. IF: - No EILS exists; THEN: - Skip EEA 2B and proceed to EEA 3 if needed. |
| 2 | IF: - Unable to maintain system frequency at 60.00Hz AND Load Resources providing RRS have been deployed and EILS have been procured; THEN: - Using the Hotline, notify all QSEs to implement EEA 2B and any measures associated with EEA 1 and 2A, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2B. ERCOT is issuing Verbal Dispatch Instruction to deploy contracted EILS Resources in the current time period until further notice. Implement all measures associated with EEA 1 and 2A, if not already implemented. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain System Frequency at 59.80 Hz; THEN: - Using the Hotline, notify all QSEs to implement EEA 3 and any measures associated with EEA 1, 2A, and 2B, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3, [MW Amount] of firm load is being shed. Implement all measures associated with EEA 1, 2A, and 2B if not already implemented. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 5.4	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - Physical Responsive Capability supplied from generation is greater than 1375 MW; THEN: - Using the Hotline, notify all QSEs of firm load restoration. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is restoring firm load. [QSE] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Maintain Physical Responsive Capability supplied from generation equal to 1375 MW while restoring firm load. |
| ### Move From EEA Level 3 to EEA Level 2B |  |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - PRC is ≥ 1375 MW, AND - All firm load has been restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 3 to EEA 2B: - Coordinate with the Resource Desk and begin recalling Load Resources - Maintain a minimum of 1375 MW of Physical Responsive Capability supplied from Generation Resources while Load Resources are being recalled. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 3 to EEA 2B. QSEs are to recall their Load Resources at this time. [QSE] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move From EEA Level 2B to EEA Level 2A |  |
| 1 | IF: - The System can maintain PRC ≥ 1750 MW, AND - All Load Resources have been instructed to be recalled, AND - Sufficient Regulation Service exists to control to 60 Hz. THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 2B to EEA 2A. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2B to EEA 2A. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Appeals through the public news media for voluntary energy conservation may be terminated, after conferring with the Shift Supervisor |
| 3 | Verify and log that all measures have been implemented. |
| ### Move From EEA Level 2A to EEA Level 1 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 2A to EEA 1 and the recalling of EILS. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2A to EEA 1. QSE’s are to recall their EILS at this time. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Move From EEA Level 1 to EEA 0 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Uncheck the EEA flag in EMS and make inactive, - Using the hotline, notify all QSEs of the termination of EEA. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is terminating EEA 1. A Watch still remains in effect. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Cancel Watch |  |
| 1 | WHEN: - PRC is ≥ 3000 MW, AND - Non-Spin has been recalled; THEN: - Cancel Watch Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. At this time, Resource testing may resume. [QSE] please repeat this back to me. That is correct, thank you.” |

## 8.1	Responding to Market Participant Issues

Procedure Purpose:  Responding to Market Participant issues regarding website questions, SCED Deployments, LMPs, etc.

| Protocol Reference | 6.5.7.1.13(4) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: July 20, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Market Participant Backup Control Center Transfer |  |
| 1 | If notified by a QSE that they will be transferring to their backup control center, or from their backup to primary, - Send e-mail to 1 ERCOT System Operators - Make log entry. |
| ### Market Participant Issues |  |
| 1 | If the MPs are not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |
| 2 | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |
| 3 | If the MPs are having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |
| 4 | As time permits, log and notify the Shift Supervisor of any actions taken and unresolved issues. |
| ### Missing Data from MIS Postings |  |
| 1 | IF: - A call is received about data missing or data being incorrect, THEN: - Transfer the call to the Help Desk, and - Notify the Shift Engineer. |
| Log | Log the information. |
| ### Requests to Decommit Self-committed Resource in Operating Period |  |
| 1 | IF: - A request is made by a QSE to decommit a self-committed Resource in the Operating Period; THEN: - Transfer the call to the Resource Desk Operator. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |