## Power Operations Bulletin # 555

ERCOT has posted/revised the Shift Supervisor Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.2	Unannounced Resource Testing

Procedure Purpose: This procedure provides direction and guidelines for conducting unannounced testing of resources.

| Protocol Reference | 8.1.1.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.3.1 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: September 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Unannounced Resource Testing |  |
| NOTE | - Operations Analysis will provide the list of resources to be tested. - The list of units [Season] is located on P:\SYSTEM OPERATIONS drive in the Performing Unannounced Unit Testing folder. - In addition, the Shift Supervisor may request at his discretion an unannounced test of any resource, other than Hydro, Wind and Nuclear-fueled Generation Resources. - Tests may be conducted as they best fit within the activities of the ERCOT Control Room, a minimum of 4 resources per week. - The resource to be tested must be on-line before beginning the test. - To identify potential congestion it may be necessary to conduct a Security Analysis Study using a Powerflow Base Case or Real-time Snap shot of the System. - Operations Analysis will complete the following items: - Current Seasonal HSL(Net MW) - 30 Min Avg Real Time Telemetry (MW) - Additional Comments - Overall Test Results |
| Caution | - DO NOT perform an unannounced Generation Resource test during a Watch for PRC or EEA event. - If an unannounced Generation Resource test is underway when a Watch or EEA event commences, the test may be cancelled. |
| VDI | When performing a test, use the Electronic VDI tool: ISSUE: - VDI to QSE - Choose “UNANNOUNCED CAPACITY TEST (NOTE IF RETEST)” as the Instruction Type from Resource level - Instruct QSE to telemeter the Resource “ONTEST” - In text, state “RETEST” if applicable |
| Testing Rules | ISSUE a VDI instructing the resource to the HSL it has reported in its Resource Plan. If conducting a re-test, make sure “Re-test” is on the VDI. The QSE has the following time to reach its HSL, depending on its output when the test begins: - At LSL – 60 minutes to reach 90% of HSL, and an additional 20 minutes to reach HSL - Between LSL and 50 % of HSL – 60 minutes to reach HSL - Above 50 % of HSL – 30 minutes to reach HSL Typical script: “This is ERCOT operator [first and last name]. ERCOT is issuing a VDI at [time] to perform an Unannounced Unit Test. Increase [Resource] to the current QSE’s telemetry HSL as shown. The [Resource] will have [XXX] amount of time to reach the reported HSL. Once the [Resource] has met the time requirement or reached its HSL, HOLD [Resource] at its HSL for at least 30 minutes. [QSE] please repeat this back to me. That is correct, thank you.” The QSE will release all Ancillary Service obligations carried by the unit to be tested and change the Resource status to “ONTEST.” When the resource reaches its HSL, HOLD that resource at its HSL for at least 30 minutes. NOTIFY the QSE that the test is complete, and RELEASE the resource from its VDI. If the resource fails to reach its HSL within the time frame, CONTINUE TO HOLD the resource for at least 30 minutes, and LOG this in the ERCOT logs. NOTIFY the QSE that the test is complete, and RELEASE the resource from its VDI. Typical script: “This is ERCOT operator [first and last name]. ERCOT is releasing VDI [number] at [time]. The Unannounced Unit Test is complete for [Resource]. Submit the results from the test within 2 business days. [QSE] please repeat this back to me. That is correct, thank you.” COMPLETE the ERCOT values on the Unannounced Seasonal Generation Verification Test via the NDCRC application on the ERCOT MIS in a reasonable timeframe. MIS>Applications>NDCRC |
| Retest | QSE can request a retest up to two times per month: - If approved, a QSE-requested retest will take place either: - Within the first twenty-four (24) operating hours of the designated Generation Resource after the request for retest, OR - Three (3) Business Days after the request for retest - Any VDI issued as a result of a QSE-requested retest will be considered as an instructed deviation only for compliance purposes. ISSUE: - VDI to QSE - Choose “UNANNOUNCED CAPACITY TEST (NOTE IF RETEST)” as the Instruction Type from Resource level - Instruct QSE to telemeter the Resource “ONTEST” - In text, state “RETEST” |
| Completion | INSTRUCT: - QSE - That the VDI issued has ended - Instruct QSE to telemeter the proper Resource status |
| Notify | Notify test completion by e-mail (include resource(s), date and time) - Operations Analysis - Shift Supervisors |

## 5.5	Supervise Coordination with SPP and CFE

Procedure Purpose:  To ensure proper notification and coordination takes place.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R4.2, R4.3 | IRO-005-2 R1.9 | IRO-014 R1.1 | TOP-002 R4 |

| Version: 1 | Revision: 2 | Effective Date: September 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The ERCOT ISO is only connected to another RC through asynchronous ties. The coordination and communication that must take place with SPP and CFE is outlined below. It is the responsibility of the Shift Supervisor to ensure this coordination takes place. - DC-Tie Tagging Activities - EEA Levels - Outages on DC-Ties - BLT’s - Arming of the Monticello SPS - ERCOT System Blackout Communications with CFE will be coordinated through AEP Corpus (Turret phone button labeled AEP TO). |
| 1 | Confirm that the DC Tie schedules and E-Tags were properly verified. Ensure that the “after-the-fact checkout” is performed each night and e-mailed to the appropriate entities as outlined in the DC-Tie Procedures. |
| 2 | ERCOT’s EEA status must be communicated to the SPP Reliability Coordinator (Turret phone button labeled SPP RC) as outlined in the DC-Tie procedures. |
| 3 | All planned and forced outages that affect the DC-Ties shall be coordinated with the Tie Operator(s) and SPP (if SPP DC-Ties affected). A message must also be posted on the MIS Public using Notice Builder for planned outages on any commercial DC-Ties. |
| 4 | Notify the SPP Reliability Coordinator when a BLT is initiated between ERCOT and SPP, as outlined in the Transmission & Security procedures. |
| 5 | Notify the SPP Reliability Coordinator when the Monticello SPS arms. If the SPS activates, the DC-E will trip. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Regional Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R4.1, R5 | EOP-002-2.1 R3, R6.3, R7.2 | EOP-004-1 R1, R3.1 | IRO-014-1 R1.1.2 |
|  | IRO-015-2 R15 | TOP-002-2 R4 | DOE OE-417 |  |

| Version: 1 | Revision: 6 | Effective Date: September 1, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template around 0300 – 0400 and again around 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - Conditions change that required new notices to be issued or cancelled (e.g., OCN , Advisory, Watch, or Emergency Notice ) - A projected reserve capacity shortage develops - Local reliability concerns arise including actual overloads or loss of load - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas restrictions, not expected to cause reliability issues - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Send updated report when conditions have returned to normal. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2A - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Adjusted Responsive Reserve ≤ 2000 MW and trending downward - Critical - EEA Level 2A in effect Potential for EEA Level 2B - N/A – No EIL available - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 2B in effect Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - Medium - EEA Level 2A in effect - High - EEA Level 2B in effect - Adjusted Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.9 Hz - Critical - EEA Level 3 in effect |  |
| ### Texas RE Event Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations or designee - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis process, events include the following: Category 1 Events: - Loss of bulk power system (BPS) elements caused by common mode failure ≥ 3 elements - Loss of generation station generators caused by common mode failure ≥ 3 aggregate 500 to 999 MW (Combine Cycle Train counts as one element) - Unplanned evacuation from BPS control center facility with BPS SCADA functionality ≥ 30 minutes - Failure, degradation or misoperation of SPS - Intended and controlled system separation by the proper operation of a SPS - System wide voltage reduction - Unintended system separation resulting in an island of 100 MW to 999 MW Category 2 Events: - Complete loss of all BPS control center voice communication system ≥ 30 minutes - Complete loss of SCADA, control or monitoring functionally ≥ 30 minutes - Loss of off-site power (LOOP) to a nuclear generating station - Unintended system separation resulting in an island of 1,000 MW to 4,999 MW - Unintended loss of Firm System Load ≥ 300 MW for more than ≥ 15 minutes - Voltage excursions ≥ ± 10 percent > 5 minutes Category 3 Events: - Loss of generation ≥ 1,000 MW - Unintended system separation resulting in an island of 5,000 MW to 10,000 MW - Loss of load ≥ 1,000 MW Category 4 Events: - Loss of generation > 5,001 MW to 9,999 MW - Loss of Load 5,001 to 9,999 MW - Unintended system separation resulting in an island > 10,000 MW Category 5 Events: - Loss of generation ≥ 10,000 MW - Loss of Load ≥ 10,000 MW |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations or designee when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". |  |
| OE-417 Reporting Events | DOE OE-417 initial reports are to be completed within 1 hour, forms can be downloaded at: ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc. Electronic forms are preferred. OE-417 reports are required for the following events: - System wide voltage reduction ≥ 3 % - Public appeal to reduce the use of electricity for purposed of maintaining the continuity of the electric power system - Load shedding ≥ 100 MW implemented under emergency operational policy - Uncontrolled loss of Firm Load ≥ 300 MW for > 15 minutes - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Fuel supply emergencies that could impact system adequacy or reliability - Loss of electric service ≥ 50,000 for ≥ 1 hour - Compete operation failure of electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system |  |
| NERC IROL and Preliminary Disturbance Report EOP-004-1 | NERC Preliminary Disturbance reports are to be completed within 24 hours, forms can be downloaded at: http://www.nerc.com/page.php?cid=5¦66 NERC Disturbance reports are required for the following events: - Loss of bulk power transmission component that significantly affects the integrity of system operations, which resulted in actions such as: - Modification of operating procedures - Modification of equipment to prevent reoccurrence of event - Identification of valuable lessons learned - Identification of non-compliance with NERC standards or policies - Identification of a disturbance that is beyond recognized criteria (i.e. three-phase fault with breaker failure, etc) - Frequency or voltage going below the under-frequency or under-voltage load shed points - The occurrence of system separation or system islanding or both - Loss of generation ≥ 1,000 MW - IROL violation - Any action taken by a GOP, TOP, BA, or LSE that results in: - Sustained voltage excursions equal to or greater than ±10 percent - Major damage to power system components - Failure, degradation, or misoperation of system protection, SPS, RAPs, or other operating system that do not require operator intervention, which did result in, or could have resulted in, a system disturbance. - Firm load shedding of 100 MW or more to maintain the continuity of the BES - Loss of firm load demands totaling more than 200 MW or 50 percent of the total customers for ≥ 15 minutes |  |
| 1 | When required to file a report (If Manager or designee is unavailable): Forward the TO or QSE report or the Director of Cyber Security’s report to: - NERC (esisac@nerc.com, fax (609) 452-9550) - DOE (doehqeoc@oem.doe.gov, fax (202) 586-8485) - “NERC and DOE Disturbance Reporting” e-mail list. |  |
| ### RCIS Reporting |  |  |
| NOTE | Refer to Section 2.2 in Desktop Guide: Operating State Alert Levels. |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” (ERCOT EEA Level 2A or 2B) - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| TEA Postings | There are four levels of Transmission Emergency Alert (TEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “System Emergency”: - “ERCOT is declaring TEA 1 on the North-Houston interface” - “ERCOT is declaring TEA 2 on the North-Houston interface; Load Resources have been deployed in the Houston area”. - “ERCOT is declaring TEA 3 on the North-Houston interface; firm load is being curtailed in the Houston area”. - “ERCOT is in TEA 0 and back to normal operations” |  |
| SEA Postings | There are four levels of Security Emergency Alerts (SEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “CIP Free Form”: - “ERCOT is declaring SEA 1 for a [cyber or physical] attack on [control center, generating facility, substation, and transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 2 for a [cyber or physical] attack on [control center, generating facility, substation, and transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 3 for a [cyber or physical] attack on [control center, generating facility, substation, and transmission line] located in [west, north, south, central] Texas”. - “ERCOT is in SEA0 and no longer under threat”. |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2A, THEN: - Select the “SO EEA Level 2A” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2B, THEN: - Select the “SO EEA Level 2B” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2B” Scenario and activate notification, WHEN: - EEA Level 2B is terminated, THEN: - Select the “SO EEA Level 2B to EEA Level 2A” Scenario and activate notification, WHEN: - EEA Level 2A is terminated, THEN: - Select the “SO EEA Level 2A to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed, THEN: - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on P:\SYSTEM OPERATIONS drive in the PUCT Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” - The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| 1 | Weather Information - Enter the High and Low temperature forecast from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Enter the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Enter the Previous Day Actual MW. |  |
| 3 | Interchange - Enter the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Enter the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals - Enter the Generation scheduled outage MW total. - Enter the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves - Enter the Responsive Reserve requirement at the Project Peak. - Enter the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity - No action needed |  |
| 8 | Comments - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically during the day, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | When alerts and warnings for GMDs are issued for K-7 or higher: - Notify the TOs and QSEs by posting message on MIS Public using Notice Builder, Log the information. |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability. |  |

## 7.2	EEA Implementation Checklist

shift Supervisor – EEA IMPLEMENTATION Check List

| Time | Action | Comment |
| --- | --- | --- |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - Phone calls made to Executive Team |  |
|  | - MIS message posted |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posting |  |
|  | EEA Level 1 Implementation | PRC <2300 MW |
|  | - Non-Spin deployed |  |
|  | - Resource testing suspended |  |
|  | - Online RMRs loaded to full output |  |
|  | - Emergency Energy Procedures implemented across CFE DC-Ties |  |
|  | - EEA 1 Schedule requested across SPP DC-Ties |  |
|  | - Verbal RUC VDIs issued, as appropriate |  |
|  | EEA Level 2A Implementation | PRC <1750MW |
|  | - Load Resources deployed - Block 1 (<1750MW) - Block 2 (as needed) - Both (<1375MW) - Settlements VDI issued |  |
|  | - Emergency Energy Procedures implemented across SPP DC-Ties |  |
|  | - Notify TO’s of Load Resource deployment |  |
|  | - Distribution voltage reduction as appropriate |  |
|  | - Verify with Manager that appeals for voluntary energy conservation through the public news media are enacted |  |
|  | - Verbal RUC VDIs issued, as appropriate |  |
|  | EEA Level 2B Implementation | Load Resources-RRS deployed & EILS procured & unable to maintain Freq at 60.00 Hz |
|  | - EILS deployed (if procured) |  |
|  | - Notify TO’s of EILS deployment |  |
|  | EEA Level 3 Implemention | Unable to maintain Freq at 59.8 Hz. |
|  | - Firm Load shed ordered (100 MW blocks) |  |
|  | - Notify QSE’s of Firm Load shed |  |
|  | - Load shed achieved |  |

## 7.3	EEA Restoration Checklist

Shift Supervisor – EEA Restoration Check List

| IMPORTANT: If the EEA event coincides with a severe weather event that resulted in the loss of residential load as well as the ERCOT directed shedding of firm load, COORDINATE load restoration with the appropriate Transmission Operator to insure lost residential load is given priority over the shed load. |  |  |
| --- | --- | --- |
| Time | Action | Comment |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - MIS message updated |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posting |  |
|  | RESTORE FIRM LOAD | Sufficient Regulation exist to control to 60 Hz & PRC from generation >1354 MW |
|  | - Firm load restoration directed |  |
|  | - Notify QSEs of Firm load restoration |  |
|  | EEA LEVEL 3 TO EEA LEVEL 2B | Sufficient Regulation exist to control to 60 Hz & PRC from generation >1375 MW while Load Resources are being recalled |
|  | - Begin recalling Load Resources |  |
|  | - Notify TO’s of Load Resource |  |
|  | EEA Level 2B to EEA LEVEL 2A | Sufficient Regulation exist to control to 60 Hz & PRC > 1750 MW |
|  | - Verify with Manager that voluntary energy conservation is being terminated |  |
|  | - Distribution voltage reductions measures recalled |  |
|  | - May begin recalling EILS |  |
|  | - Notify TO’s of Load Resource and EILS recall |  |
|  | EEA Level 2A TO EEA LEVEL 1 | PRC > 2300 MW & all Load Resources and EILS have been instructed to restore |
|  | - EILS recalled if not already done |  |
|  | - Notify TO’s of EILS recall |  |
|  | EEA Level 1 TO EEA 0 | PRC > 2300 MW & all Load Resources and EILS have been instructed to restore |
|  | - End any emergency across DC Ties |  |
|  | - Release any RUC committed Resources |  |
|  | - See Administrative Tasks |  |

## 7.7	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for Extreme Hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 1 | Effective Date: September 1, 2011 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| Watch |  | When Extreme Hot weather is projected. - Ensure Watch is issued. - Continue to monitor the weather. - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delay/return early. - Contact Operations Support to run studies to determine the impact of current and future outages. - Review emergency operating procedures. |
| Log | Log all information in the Operator log and notify the ERCOT Manager, System Operations or designee of any issues. |  |

## 9.2	Monthly Test of Non-Routinely used Telecommunications Facilities

Procedure Purpose: To ensure backup communications are tested monthly.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1 R2 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: September 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Primary Control Center |  |
| Phone Tests | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday: - Test the Control Room Cell Phone by calling the ERCOT Helpdesk Cell Phone. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Standalone Satellite phone. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to Section 8.7.4 in the Desktop Guide. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| SAT modem testing | Coordinate the following test with the DC Tie Operator at the alternate control center - Using the turret, call each programmed desk SAT Phone at the alternate control center - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| NXT Test | - Test NXT Communicator by activating the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Notice Builder | - Test Notice Builder and Twitter postings by selecting the “Test Message on Notice Builder/Twitter” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log the results for each of the bulleted items above in the Shift Supervisors Operations Log. |
| Alternate Control Center |  |
| Phone Tests | - When working out of the alternate Control Room during the monthly scheduled dates: - Test Control Room Cell Phone with the ERCOT Helpdesk Cell Phone. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Satellite phone associated to the Operations Desk on each turret. It isn’t necessary to call a satellite number, just verify the phones are operational. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Standalone Satellite phone operation located in the Control Room. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to section 8.8.4 in the Desktop Guide. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| SAT modem testing | Coordinate the following test with the DC Tie Operator at the other control center - Using the turret, test call each programmed SAT Desk Phone at the other control center - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| NXT Test | - Log into the Bastrop ENS link when working out of the alternate Control Room in Bastrop, - Test NXT Communicator by activating the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log the results for each of the bulleted items above in the Shift Supervisors Operations Log. |

## 10.1		Loss of Primary Control Center Functionality

Procedure Purpose: Provide instructions for responding to conditions that cause the primary control center to become inoperable or uninhabitable and ensuring the safety of control room personnel.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Stanard | COM-001 R5 | EOP-008 R1.4 |  |  |

| Version: 1 | Revision: 1 | Effective Date: September 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | It will be the responsibility of the Shift Supervisor to determine the risk and ensure the safety of Control Center personnel. |
| 2 | Upon confirmation of imminent danger to Control Center personnel immediately evacuate the Control Center to a secure area, taking the Control Center cell phone and a copy of this procedure with you. |
| NOTE | - After the Control Center has been evacuated the Shift Supervisor may: - Re-locate the entire shift to the Alternate Control Center (ACC). - Send a partial shift or contact extra personnel to report to the ACC. - Remain in the secure area in anticipation of a quick return to the Primary Control Center (PCC). - The Shift Supervisor may choose another course of action that will best maintain grid security depending on the circumstances causing the evacuation. |
| 3 | - The Shift Supervisor is responsible for the following notifications in the event of a Control Center evacuation. Information and instructions conveyed will be based on the Shift Supervisor’s decision regarding relocation to the ACC. - DC Tie Desk Operator at the ACC - ERCOT Security TCC1 – Ext. 3000 - ERCOT Security TCC2 – Ext. 6400 - ERCOT Security ACC (Bastrop) – Ext. 5000 - ERCOT Security MET – Ext. 7000 - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations - Engineering Support These phone numbers have been programmed into the control room cell phone |
| NOTE | - The DC Tie Desk Operator at the ACC will be responsible for all notifications if there is a loss of the PCC and he/she has not been contacted by the Shift Supervisor. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |