## Power Operations Bulletin # 565

ERCOT has posted/revised the Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	Compliance Monitoring

Procedure Purpose: To monitor QSE performance

| Protocol Reference | 3.9.1(7) & (8) | 6.3.2(2) | 6.4.2.5 (2) | 6.4.2.5(3)(b) |
| --- | --- | --- | --- | --- |
|  | 6.4.8.1(1) | 6.5.7.5(2) | 6.5.9(3) | 8.1.1.3(3) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### Monitor Resource Status for Discrepancies |  |  |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instructions under normal conditions and Emergency Conditions. During Emergency Conditions, ERCOT may verbally request QSEs to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |  |
| Monitor COP | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>COP Monitor Periodically: - Review the COP changes utilizing the Date/Time of Submission column as a reference; IF: - A QSE has changed a resource status code, resource parameter, or ancillary service on a specific resource; THEN: - Review the change in the COP Monitor, AND - Notify the QSE representing the resource if the change is unacceptable to ERCOT. |  |
| Telemetered Status | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>Consistency Checks IF: - Discrepancy is identified between a COP and telemetered Resource Status; THEN: - Call the QSE representing Resource to determine the correct resource status and have them make the necessary correction. NOTE: It is not necessary to make calls for inconsistent telemetry/COP for quick start units. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Area Status>Nodal Operational Status>Resource Limit Data>Unit Tab WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) |  |
| ON TEST | - If the ONTEST Resource Status Code is used to indicate that a Generation Resource is performing a test, the QSE should notify ERCOT by 1800 in the Day-Ahead, - Review the list of approved Resources to be ONTEST, - ONTEST can be used by the QSE when in the start-up and shut-down mode. |  |
| Control Block Up/Down | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details>Unit tab - Control Block Current UP/DN are telemetry points that a QSE can use in emergency situations to communicate that a resources ability to adjust its output has been unexpectedly impaired. - If a QSE has a Control Block set for greater than 5 minutes, the system will set the corresponding (UP/DN) Too Long flag to indicate this to the operator. |  |
| ### Manual Override Checks |  |  |
| 1 | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL and LDL Periodically: - Review the Manual HDL and LDL overrides to ensure they are still needed. IF: - Override exists; THEN: - Coordinate with the Transmission Operator to determine if override is still needed. |  |
| ### Dynamically Scheduled Resource |  |  |
| NOTE | Each QSE may not have more than one DSR Load. |  |
| DSR | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Analyst Displays>Gen Monitoring Displays>Dynamic Schedules>Load Based IF: - A DSR load signal fails for any reason for > than one 15 minute Settlement Interval; THEN: - Notify the QSE and notify the Helpdesk to suspend validation of DSR Output Schedule. IF: - A DSR load signal fails for more than 10 consecutive hours; THEN: - Notify the Helpdesk to have DSR suspended until the signal is reliably restored. |  |
| NOTE | IF: - The signal failure is identified to be an ERCOT communication problem; THEN: - ERCOT will not suspend the QSE’s ability to use DSR. |  |
| ### Monitor QSE Ancillary Services Obligation |  |  |
| Monitor |  | Monitor the Regulation A/S details, RRS details and Non-Spin details displays. |
| NOTE |  | If any A/S insufficiencies are identified in the HRUC solution, refer to the “Replacement of Ancillary Service Due to Undeliverable/Failure to Provide” section of the “Supplemental Ancillary Services Market” procedure. |
| Real-Time A/S Shortage |  | WHEN: - A QSE shows a Real-Time A/S shortage; NOTIFY: - The effected QSE of their QSEs Resources’ telemetered value and their A/S Resource Responsibility; THEN: - Within ten minutes, the QSE must: - Correct the telemetered A/S Resource Responsibility to provide sufficient capacity, OR - Provide both appropriate justification for not satisfying their A/S Obligation AND a plan to correct the shortfall that is acceptable. IF: - The QSE is unable to replace their A/S Obligation; THEN: - Notify the Shift Supervisor and determine if A/S shortage amount and reliability need is sufficient enough for ERCOT to replace from existing offers. |
| A/S Difference in COP |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Participation>Physical Market>SASM Market>Failure To Provide IF: - A/S Difference (MW) column displays negative values in RED; THEN: - Verify that the Notification Flag column displays a “Y” (should automatically default). Change the “Y” to “No” for past hours and next day hours. Commit to database, - Press the “Send Notification” button and acknowledge the pop-up box indicating the notifications were sent, - Navigate to the Failure To Provide display and call the Market Participants that are displayed with a Failure MW, IF: - The QSE states that they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened. IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Failure To Provide section 6.8.2 of the Desktop Guide. |
| Infeasible A/S Capacity from RUC |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market> AS Replacement IF: - The Infeasible MW column is displaying MW values; THEN: - Change the Notification Flag to “Y” and commit to database, - Press the “Send Notification” button and acknowledge the pop-up box indicating the notifications were sent, - Navigate to the AS Replacement display and call the Market Participants that are displayed with an Infeasible MW. IF: - The QSE states that they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened; IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Undeliverable section 6.8.1 of the Desktop Guide. |
| NOTE |  | A QSE that has one or more of its Resources RUC-committed to provide Ancillary Services must increase its Ancillary Service Supply Responsibility by the total amount of RUC-committed Ancillary Service quantities. The QSE may only use a RUC-committed Resource to meet its Ancillary Service Supply Responsibility during that Resource’s RUC-Committed Interval if the Resource has been committed by the RUC process to provide Ancillary Service. The QSE shall indicate the exact amount and type of Ancillary Service for which it was committed as the Resource’s Ancillary Service Resource Responsibility and Ancillary Services Schedule for the RUC-Committed Intervals for both telemetry and COP information provided to ERCOT. Upon deployment of the Ancillary Services, the QSE shall adjust its Ancillary Services Schedule to reflect the amounts requested in the deployment. |

## 3.4	Responding to Capacity Shortages

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Capacity Shortages as requested by the Real-Time Operator.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R3.1 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If Non-Spin is being deployed 20 minutes past the top of the hour, deselect any Resources whose COP Non-Spin Resource Responsibility is “ZERO” for next hour. (Refer to Desktop Guide section 6.2 Non-Spin Deployment and Recall) |
| Deployment | WHEN: - Notified by the Real-Time Operator to deploy Non-Spin for capacity shortages; THEN: - Coordinate with the Transmission Operator to verify the Non-Spin doesn’t create congestion, - Deploy Non-Spin, (Refer to Desktop Guide section 6.2 “Deploy All Non-Spin or Partial Non-Spin deployment”), - Post as “Operational Information” message on MIS Public using Notice Builder. Typical MIS posting: “ERCOT is deploying all Non-Spin Reserve”, OR “ERCOT is deploying half of the Non-Spin Reserve. |
| Additional Deployment | IF: - Additional Non-Spin becomes available going into next hour; THEN: - Determine if the additional Non-Spin is needed, - Deploy if needed (Refer to Desktop Guide section 6.2 Non-Spin Deployment and Recall) |
| Commit | IF: - Notified by a QSE that their Off-line Non-Spin obligation has ended, AND - PRC is below 2500 MW, OR HDL-GEN is ≤ 200; THEN: - Request that the Resource stay On-line, - Issue an electronic VDI (see Desktop guide 8.3) - Choose Resource tab - Choose Commit as the Instruction Type - State Capacity in Other Information |
| Termination | WHEN: - Notified by the Real-Time Operator that the Non-Spin Reserve Service is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide section 6.2 “Recall All Non-Spin or Partial Non-Spin Recall”), AND - Cancel message on MIS Public using Notice Builder. |

## 3.6	System Failures

Procedure Purpose: To ensure Market Participants are notified via MIS Public using Notice Builder of any SCED/RLC/LFC(AGC) failures.

| Protocol Reference | 6.5.9.2 | 6.5.9.1(2) | 6.5.9.2(3) | 6.5.9.2(4) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | WHEN: - Notified by the Real-Time Operator of a SCED/RLC/LFC(AGC) failure; THEN: - Post the following message on MIS Public using Notice Builder: Typical MIS posting: “ERCOT has issued an Emergency Notice due to the failure of [SCED/RLC Failure], and/or [LFC].” |
| 2 | WHEN: - Notified by the Real-Time Operator that SCED/RLC/LFC(AGC) has been restored; THEN: - Cancel message on MIS Public using Notice Builder. |
| Log | Make log entry of actions taken. |

## 3.8	Deploying Non-Spin for Local Congestion

Procedure Purpose:  Mitigating local congestion.

| Protocol Reference | 6.1 (3) | 6.5.1.2 (1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - Notified by the ERCOT Transmission and Security operator that specific Resources carrying Non-Spin are needed for local congestion; THEN: - Deploy specific Resources |
| POST | Post message on MIS public utilizing Notice Builder. Typical MIS Posting: ERCOT is deploying Non-Spin Reserve for [XXXX] constraint. |
| 2 | IF: - The Non-Spin obligation ends for the Resource deployed, AND - The Resource is still needed; THEN: - Issue an electronic VDI (see Desktop guide 8.3) - Choose Resource tab - Choose Commit as the Instruction Type - State Local Congestion in Other Information |
| Termination | IF: - Notified by the ERCOT Transmission and Security Operator that Non-Spin is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide section 6.2 “Recall All Non-Spin or Partial Non-Spin Recall. |
| CANCEL POSTING | Cancel the MIS message. |
| LOG | Log actions. |

## 4.1	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve or reject Resource decommitments in the Operating Period.

| Protocol Reference | 6.4.6 | 6.4.6.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Operating Period |  |
| NOTE | - The Operating Period is the two-hour period comprised of the Operating Hour and the clock hour preceding the Operating Hour - A QSE may request to decommit a Resource other than a QSGR for any interval that is not a RUC-Committed Interval by verbally requesting ERCOT to consider its request - A QSE may decommit a QSGR without any request for any interval that is neither a RUC-Committed Interval nor an interval in which a manual override by the ERCOT Operator. |
| NOTE | If a combined cycle train (CCT) is transitioning from one configuration to another, this is not a QSE requested de-commit. |
| 1 | IF: - A QSE requests to de-commit a Resource that has been Self-Committed (other than a QSGR); THEN: - Determine if the Resource has an Ancillary Service responsibility. If yes, inquire how this AS will be replaced, - Notify the Transmission Operator to make determination if needed for congestion management, - Notify the Shift Supervisor to ensure that requests will not have a reliability impact. NOTIFY: - The QSE of ERCOT’s decision. |
| 2 | IF: - Request is granted; THEN: - Issue an electronic VDI - Choose “Resource” tab - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type tab |
| 3 | Log actions taken. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 6.4.8.1 | 6.4.8.1.1 | 6.4.8.1.2 | 6.4.8.1.3 |
| --- | --- | --- | --- | --- |
|  | 3.16 (4) | 6.4.8.2 | 6.4.8.2.2 | 6.5.9(4) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - Once the notice is given, no further offers are eligible for that SASM. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. - See Desktop Guide 8.15 if the savecase function fails when running a SASM |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services will have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify that the RUC Operator has issued an Emergency Notice by making a Hotline call to the QSEs, - Procure all Ancillary Services for the next operating day through a SASM, (Refer to Section 6.8.4 of the Desktop Guide) |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in RUC. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline Notification and post message on MIS Public using Notice Builder, - Procure more Ancillary Services through a SASM(Refer to Section 6.8.3 of the Desktop Guide). Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reason]. At [xx:xx] ERCOT will open a SASM to procure the additional Ancillary Services for hours [hours] for operating day [day]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the RUC Operator to replace the remaining insufficiencies in the next HRUC. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | Once verified that all Ancillary Service has been procured, cancel the Watch: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace A/S capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the A/S capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to section 6.8.1 or 6.8.2 in the Desktop Guide). |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Discuss with Shift Supervisor of the need to replace the remaining insufficiencies in the next HRUC. |
| 3 | IF: - A QSE is unable to provide their SASM awards; THEN: - Determine if there is time to open an additional SASM, AND - Send failure to provide notification. |
| 4 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE Name you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - PVT transferred |
| 5 | Send information in an email to the following distribution list: - SASM |

## 8.1	Weekly Hotline Test

Procedure Purpose: To perform a weekly communication test of the ERCOT Hotline phone system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.1.3(3) |  |  |  |
| NERC Standard | COM-001-1.1 R2 | EOP-005-1 R5 |  |  |

| Version: 1 | Revision: 3 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | In the event of a failure of the Forum Conference Client software, the most recent printout of the Hotline log may be used to perform a manual roll call of QSEs/ TOs. |
| NOTE | Insure all Invalid Hotlines “Lost Souls” are cleared prior to the hotline call. |
| NOTE | Confirm with Shift Supervisor the threat alert level, which can be viewed at the following links: http://www.esisac.com/SitePages/Home.aspx, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert level are listed in the Security Alert Plan. |
| 1 | Each Monday between 0630 and 1100 test the ERCOT Hotline |
| 2 | Using the Hotline, notify all QSEs/TOs of the purpose of the call. - When QSEs/TOs have answered the Hotline, print Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This is ERCOT Operator [first and last name]. ERCOT is conducting the weekly [QSE/TO] Hotline test. ERCOT is currently at threat alert level [state alert level]. The following notices are currently in effect: - List OCNs, Advisories, Watches and/or Emergency Notices in effect. - State “None” if none are in effect. This ends the test of the ERCOT Hotline. That is all.” |
| 3 | Notify the Shift Supervisor of any QSE or TO that did not respond to the Hotline test. The Shift Supervisor and/or the Help Desk may notify the telecommunications department for repairs. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |