## Power Operations Bulletin # 566

ERCOT has posted/revised the Reliability Unit Commitment Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	Publish A/S Requirements and Review System Conditions

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

| Protocol Reference | 4.2.1.1 | 4.2.1.2 | 4.2.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1, R5 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Review and update A/S Requirements must be completed prior to 0500. - The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month. |
| ### Review Weather Data Information |  |
| 1 | REVIEW the Weather Data for the next operating day in the EMS. |
| 2 | REVIEW REFERENCE DISPLAY: EMS Applications>Weather Details>Real Time Displays>Weather Forecast Directory The Meterlogix phone number is (952) 882-4312. IF: - The Last Weather Source Update or Last Weather Read is less than one (1) hour old; THEN: - Using the usual sources, review the weather forecast for at least two days out. IF: - The data update or read is more than one (1) hour old; THEN: - Notify the Shift Supervisor and the Help Desk. |
| 3 | Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems. The trigger will usually be an extreme weather event which will cause temperatures to be below freezing for an extended period of time, though there could be other reasons. |
| ### Review and Select Load Forecast |  |
| 1 | - Review and Select load forecast for next day (Refer to Section 7.17 Select Day-Ahead MTLF in Desktop Guide). |
| NOTE | The Net Error Subtracted from the Load Forecast is scheduled based on the 2010 AS methodology. If ERCOT subtracts a MW value from the load forecast during the month additional Non-Spin will be procured. |
| ### Publish A/S Requirements |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| ### Increasing A/S Requirements before A/S Obligations Publish |  |
| NOTE | This procedure would be performed when it has been determined that additional A/S is needed, such as to support a weather event. |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, increase the hourly ERCOT system total A/S requirements for each requirement needed for each hour of the next operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| 3 | IF: - The A/S requirements were increased, THEN: - The next day will copy the new A/S requirements unless you return the A/S requirements to the A/S Plan requirements for the month. REFERENCE DISPLAY: - Market Participation > Physical Market > AS Market > AS Plan Before 04:00 update the A/S requirements. |
| NOTE | Refer to the A/S requirements for the current month’s A/S Plan if no changes are required. |
| ### Invalid SPS/RAP due to Outage |  |
| 1 | Review outages notes and coordinate with Outage Coordinator and/or Shift Engineer to determine if an outage will have an effect on SPS/RAP/PCAPs. Market Participation > Physical Market > AS Market > AS Plan IF: - An SPS/RAP will be disabled next day due to an outage; THEN: - Notify the DAM operator to deactivate the invalid SPS/RAP. |
| ### Priority Outages |  |
| 1 | A Priority Outage is one that affects generation. Prior to 1200: - From a review of the Outage Notes for the next Operating Day, make lists of Priority Outages, sorted by affected Transmission Operator, - The file is located in P:\DAY AHEAD – TDSP PRIORITY OUTAGE NOTIFICATION, - Print copies, - Fax the lists to the respective TOs accompanied by a request that within 30 minutes of the Actual Start and Actual End times of these Priority Outages, they enter the Actual Start and Actual End times in the Outage Scheduler, - Place in Daily Log File. |
| ### Verification of Published A/S Requirements |  |
| NOTE | This step may be completed after 0600. |
| 1 | VERIFY by spot-checking the following information posted to the ERCOT Market Information System (MIS) for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - MIS; Grid; Transmission; Transmission Outages; Approved and Accepted Transmission Outages - Weather assumptions used to provide the system conditions forecast. - MIS; Markets; Day-Ahead Market; Operating Day System Conditions; Weather assumptions - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, and Non-spinning Reserve – NSPIN. - MIS; Markets; Day-Ahead Market; Ancillary Service Plans; DAM Ancillary Service Plan. |
| Log | LOG any significant problems including any action taken. |

## 2.4	RMR Resource Commitment

Procedure Purpose: This task is performed to notify ERCOT Market Operations of RMR resources that are required, in the Day-Ahead, to maintain system security/stability of the ERCOT Interconnection.

| Protocol Reference | 4.3(2) | 4.4.8 | 6.5.1.1(d) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT does not currently have RMR contracts. |

## 3.1	Tasks prior to Execution of HRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit/de-commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.1 | 5.5.2(5) |
| --- | --- | --- | --- | --- |
|  | 5.5.2(9)(b) | 5.3(3) | 6.3.1(1) | 6.3.2(2) |
|  | 6.3.2(3)(a) | 6.4.1 | 6.4.2.5(3)(b) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 & R11 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Tasks prior to execution of HRUC |  |
| NOTE | The RUC Study Period for DRUC is the next Operating Day. The RUC Study Period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the Operating Day has been solved or after 18:00 if DRUC did not solve. |
| Continuous Monitoring | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow IF: - The EMSI Workflow Parameters does not indicate EMSI has run in the last hour and Load Forecast are NOT running (should be continuous); THEN: - Open EMSI Workflow, select “Start up”. When start up is complete, select “Run”. IF: - EMSI Workflow does not complete; THEN: - Notify Helpdesk and Control Room staff. |
| Load Forecast | Periodically monitor the Load Forecast to ensure it is accurate: IF: - Adjustments need to be made, they will be done in the EMS and updated to the MMS; THEN: - Adjust (Refer to Section 7.17 of the Desktop Guide). |
| Wind Forecast Updates | Periodically monitor the Wind Forecast and verify data is updating: IF: - Wind forecast is not updating; THEN: - Notify Supply Integration & Grid Application group, - Be aware that this could skew HRUC results. |
| RMR Consideration | IF: - An RMR unit needs to be considered in HRUC; THEN: - Ensure COP status is “OFF”. IF: - An RMR unit is needed but is not to be considered in HRUC; THEN: - Commit unit before HRUC is executed. |
| COP Validation | REVIEW REFERENCE DISPLAY: Market Participation>Monitoring>Event Manager>Events>filter Event Name for COP Validation IF: - A Resource Forced Outage has occurred and the QSE has not update their COP, OR - COP Validation ERROR; THEN: - Select “START-NOW" in the Status column, - Be aware that the results may be skewed and determine the need for procuring equivalent MW capacity elsewhere. |
| Review AS Differences | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>SASM Market>AS Responsibility – QSE Market Participation>Monitoring>Event Manager>Events IF: - AS Differences exist; THEN: - Notify the Resource Operator. |
| Bad/Suspect Telemetry | Periodically monitor: IF: - Notified of bad/suspect telemetry; THEN: - Determine if issues will be resolved for next HRUC run, - Discuss with Shift Supervisor if the HRUC should be run or delayed until the issues can be resolved, - Consider requesting Shift Engineer to manual over-ride SCADA values (be aware that this could skew the results), - If it is determined to delay HRUC, follow the “HRUC Failure/Timeline Deviation” procedure. |
| E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS: IF: - Individual schedules need to be reviewed; THEN: - Go to the MI COP display and filter ‘ERCOT’ as the QSE name. |
| Verify | REVIEW REFERENCE DISPLAYS: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>HRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” |
| DSI | EXECUTE: - The DSI sequence; VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact Help Desk immediately to determine the cause and expected time of resolution. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes> DSI Operator Manual Commitment Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data> MF Generator Parameter IF: - An RMR unit is needed but was not picked up in DAM, OR - Is not to be considered in HRUC; THEN: - Commit unit before HRUC is executed. IF: - Additional resources are needed to solve for transmission congestion; THEN: - Consult with the Shift Engineer and/or the Transmission and Security Desk Operator to determine which resources should be committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods; THEN: - Change ‘blank’ to ‘Commit’, - List reason. |
| Deselect Contingencies | IF: - It has been determined with the help of Engineering Support that a contingency known to cause errors or that otherwise result in inconclusive study output in RUC; THEN: - After the Shift Engineer has deselected the contingency, - Post to the MIS Secure Area contingency that was deselected with the reason and no later than one hour after deselection. |
| NOTE | If a RMR unit was committed in DSI Operator Manual Commitment and it is the only change since the DSI was last run the next step is not necessary. |
| Verify | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the HRUC input data; CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No”, OR - “Use Save case set to “Yes” |
| ### Verify HRUC executed at XX: 03 |  |
| 1 | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages Verify execution of the HRUC sequence. |

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 3.9(7) | 3.9.2(4)&(5) | 5.1 (7)&(9) | 5.3(3) |
| --- | --- | --- | --- | --- |
|  | 5.5.1(11) | 5.5.2 | 5.5.3 | 6.3(1) |
|  | 6.3.1(1) | 6.3.2(2) | 6.4.8.1.2 | 6.4.8.1.3 |
|  | 6.5.9(2) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 & R11 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide 8.15 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages - Monitor the HRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published. IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for HRUC are invalid, - Notify the Manager or designee immediately, - ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: - The load forecast is not reasonable for each hour; THEN: - Be aware that this could skew the HRUC results, IF: - Any under/over generation exists that HRUC could not resolve; THEN: - Notify Control Room staff. |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on WGR’s or Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue an electronic VDI (priority should be given to WGRs and Resources that resolve congestion - Choose “DECOMMIT” as the Instruction Type from Resource tab - Enter “ERCOT requested decommit/capacity surplus” in Other Information. |
| QSE’s Request to Change Resource supplying A/S | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: - Undeliverable Ancillary Service are indicated; THEN: - Notify the Resource Desk Operator. |
| A/S Insufficiency from SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - A/S Insufficiency; THEN - If deemed necessary, commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, - Refer to Section 7.18 of the Desktop Guide. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints; THEN: - Notify the Resource Desk. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Shift Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Shift Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually commit resources as needed Refer to Section 7.14 of the Desktop Guide. |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: - HRUC recommends the commitment of any unit; THEN: - Determine the validity, - Determine the temporal constraints for each of the units. IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason (evaluate later), IF: - There is a reliability reason requiring the resource commitment decision to be made immediately; - Resources returning from outages - Congestion or Capacity deficiencies that are creating HRUC performance issues THEN: - Log the reason for not de-selecting the resource. |
| RMR Resources | QSEs will show a COP status of OFF when Resources are available. RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| RMR Commitment | WHEN: - HRUC recommends a RMR unit, AND - A capacity reserve shortage is projected and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; THEN: - Determine if an RMR Resource will need to be considered in HRUC Study Period; ISSUE: - Watch for projected reserve capacity shortage with no market solution; THEN: - Ensure COP status is “OFF” and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event; SELECT: - Commit Resource before HRUC is approved - Commit Resource, - List reason (RMR for Capacity). |
| Hotline | Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed during a HRUC study. [QSE] please repeat this back to me. That is correct, thank you.” Ask Transmission Operator to make Hotline call to TOs. |
| Post | Typical MIS posting: ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. |
| Cancel | Cancel Watch once RMRs are off-line by making hotline call to QSEs and cancelling the posting. Ask Transmission Operator to make hotline call to TOs. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: - Additional resources are needed to solve for transmission issues (such as for voltage issues) and were not picked up in the HRUC run; THEN: - Commit unit before HRUC is approved - Change ‘blank’ to ‘Commit’, - List reason (contingency name or voltage issue). |
| NOTE | - Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. - ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. - If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. - QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If HRUC recommends decommitments; Determine if: - Outage related, - Possible Network Model error/ Normal Breaker status variances, - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort, THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |
| ### VSAT and RUC perform full AC analysis of all contingencies |  |
| NOTE | IF: - RUC cannot complete the process; THEN: - Notify the Transmission & Security Desk Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - External Input data - UC Displays - Input Display Menu - System TCG Data & System Load |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The HRUC results are reasonable and after all necessary modifications have been made; THEN: - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button, AND - Follow the Manage HRUC Timeline Failure in the next section. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| Log | Log actions taken. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 5.1 (9)&(11) | 5.3.(3) | 5.5.1(9) | 5.5.2 |
| --- | --- | --- | --- | --- |
|  | 5.5.3(2) | 6.3.1(1) | 6.4.6(4) | 6.4.8.1(3) |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide 8.15 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with the Market Operations and Shift Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published, IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for DRUC are invalid, - Notify the Manager or designee immediately, - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “Manage Capacity Insufficiency” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to “Use Suggestion Plan to Resolve Violated Constraints in DRUC” in Section 7.6, step 5 of the Desktop Guide. |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour, - Any under/over generation; THEN: - Be aware of these when running HRUC. |
| NOTE | The RUC process may not be used to buy A/S unless the A/S Offers submitted in the DAM are insufficient to meet the requirements of the A/S Plan. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Notified from Market Operations of A/S Insufficiency from DAM; THEN - Call the Market Participant and confirm that the unit can be started as required to supply the A/S Insufficiency, - Commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, entering the A/S amount in the reason column, - Refer to Section 7.1 of the Desktop Guide. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Shift Engineer to determine the validity; IF: - Invalid, no further action is required, - Valid; THEN - Locate the constraint on the DSP Constraint Summary display, - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, - Commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit; THEN - Determine the validity, - Determine the temporal constraints for each of the units, IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason (evaluate later). IF: - There is reliability reason requiring the resource commitment decision to be made immediately; - Resources with long start-up times - Resources returning from outages - Congestion or Capacity deficiencies that may create HRUC performance issues THEN: - Log the reason for not de-selecting the resource. |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS folder: - “6 DRUC Capacity” which is based on the last ran DRUC VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision can be made in the future, THEN: - Post an OCN and make Hotline call for Excess Reserve Capacity for hours projected. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess Reserve Capacity for [hours]. [QSE] please repeat this back to me. That is correct, thank you.” |
| DRUC Committed For Capacity Shortage | IF: - DRUC recommends Resource(s)s for capacity; THEN - Determine if start-up time allows enough time to re-evaluate, and - De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: - Post an OCN and make Hotline call for projected Reserve Capacity shortage for hours short. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [hours]. [QSE] please repeat this back to me. That is correct, thank you.” |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Additional resources are needed to solve for transmission issues (such as voltage issues) and were not picked up in the DRUC run, AND - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period; THEN: - Change ‘blank’ to ‘Commit’ - List reason (contingency name or voltage issue). |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments; DETERMINE IF: - Outage related’ - Possible Network Model error’ - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort; THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - External Input data - UC Displays - Input Display Menu - System TCG Data & System Load |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made; THEN: - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button - Follow the Manage DRUC Failure/Timeline Deviation procedure. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed and needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |

## 4.4	DAM/DRUC Timeline Deviation

Procedure Purpose: To address situations in which the DAM/DRUC process has deviated from its timeline.

| Protocol Reference | 4.1.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 | IRO-001 R9 |  |  |

| Version: 1 | Revision: 6 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
|  | 2 |
| DAM Timeline Deviation |  |
| DAM Timeline Deviation | IF: - Notified by Market Operations that the DAM Market timeline is deviated; THEN: - Notify Shift Supervisor, - Issue a Watch by making a Hotline call (Market Operations will post message on the MIS): Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch for the timeline deviation of the Day Ahead Market; the start of DRUC will be delayed. Another hotline call will be made when DAM completes. [QSE] please repeat this back to me. That is correct, thank you.” WHEN: - DAM completes; THEN: - Make Hotline call to QSE’s and give one hour notice to update COPs - Post message on MIS Public utilizing Notice Builder (Operational Information with low priority) Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the delay of DAM. DAM is now complete; DRUC will begin at [time]. [QSE] please repeat this back to me. That is correct, thank you.” Typical MIS Posting: DAM is complete, DRUC will begin at [xx:xx]. |
| ### Delay of DRUC |  |
| DRUC Delay | By 16:00 IF: - DRUC is delayed; THEN: - Notify Shift Supervisor, - Issue a Watch by making a Hotline call - Post message on the MIS Public using Notice Builder: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch for the timeline deviation of DRUC for [effected date] due to [state issue]. DRUC will now start at [time]. [QSE] please repeat this back to me. That is correct, thank you.” Note: This step may have already been done if DAM did not met its timeline in “DAM Timeline Deviation” |
| Timeline Not Met | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow By 18:00 IF: - DRUC completed and the results cannot be approved; THEN: - No need to abort DRUC Process, just don’t approve. IF: - DRUC can’t complete (software issues); THEN: - Abort DRUC Process. |
| 1 | IF: - DRUC software fails without expectation of timely repair, or due to time constraints due to not completing in a timely manner; THEN: - Notify the Help Desk and control room staff, - Issue an Emergency Notice by making a Hotline call - Posting message on the MIS Public using Notice Builder Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to DRUC not completing by 1800 due to [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” |
| NOTE | After 1800, HRUC will run for the rest of the current day and the next day even if DRUC has not run successfully. |

## 4.5	A/S Insufficiency in DAM

Procedure Purpose:  When there is an insufficiency in A/S offers in DAM.

| Protocol Reference | 4.5.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| A/S Insufficiency Offers | IF: - Notified by Market Operations of an insufficiency in A/S offers in DAM; THEN: - Determine which A/S offers are needed, AND - Issue a Watch by making a Hotline (Market Operations will post message on the MIS): Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to an insufficiency in Ancillary Service offers in the Day Ahead Market. ERCOT is requesting additional Ancillary Service Offers for [Up/Down Regulation, Responsive Reserve, Non-Spin]. [QSE] please repeat this back to me. That is correct, thank you.” |
| NOTE | Market Operations will not begin executing the second DAM sooner than 30 minutes after issuing a Watch. |
| DAM Complete with A/S | WHEN: - The second DAM is complete, AND - Was successful in procuring all required A/S; THEN: - Cancel the Watch by making a Hotline call, and - Cancel the MIS posting (if not already done by Market Operations). Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is canceling the Watch for insufficient Ancillary Services offers in the Day Ahead Market. [QSE] please repeat this back to me. That is correct, thank you.” |
| A/S Still Insufficient | IF: - Notified by Market Operations that A/S offers in DAM are still insufficient; THEN: - The difference will be procured in DRUC from Resources that are qualified to provide the needed A/S, - See Desktop Guide 7.1 for instructions. |
| Cancel Watch | WHEN: - DRUC is complete, AND - The needed A/S has been procured; THEN: - Cancel the Watch by making a Hotline call, and - Cancel the MIS posting (if not already done by Market Operations). Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is canceling the Watch for insufficient Ancillary Services offers in the Day Ahead Market. [QSE] please repeat this back to me. That is correct, thank you.” |

## 4.6	DAM Failure

Procedure Purpose:  When DAM has failed.

| Protocol Reference | 5.2.2.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| DAM Failure | IF: - Notified by Market Operations that the DAM Market has failed and A/S will need to be procured through SASM; THEN: - Notify Shift Supervisor and Resource Desk - Issue an Emergency Notice by making a Hotline call (Market Operations will post message on the MIS) Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing an Emergency Notice due to the failure of the Day Ahead Market for [effected date] due to [state issue]. At [xx:xx] ERCOT will open a SASM to procure Ancillary Services for tomorrow’s operating day. [QSE] please repeat this back to me. That is correct, thank you.” |
| SASM not able to Procure all A/S Requested | IF: - Notified by the Resource Operators that SASM did not procure all A/S required; THEN: - Procure Resources in RUC that are qualified to provide the needed A/S, - See Desktop Guide 7.1 for instructions. |
| Cancel Emergency Notice | WHEN: - Notified by Resource Operator that SASM procured the needed A/S, OR - Resourcres were commit in RUC to provide the A/S insufficiency; THEN: - Cancel Emergency Notice by making a Hotline call, - Cancel MIS message Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is canceling the Emergency Notice for the failure of the Day Ahead Market for [effected date]. All Ancillary Services have been procured for tomorrow’s operating day. [QSE] please repeat this back to me. That is correct, thank you.” |

|  | - the service needed and amounts. |
| --- | --- |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |