## Power Operations Bulletin # 568

ERCOT has posted/revised the Transmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.3	Analysis Tool Outages

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002 R8, R9 | IRO-008-1 R2 | NUC-001 | TOP-004 R4 |

| Version: 1 | Revision: 5 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT Real-Time Assessments must be performed at least once every 30 minutes to determine if any IROLs are exceeding or are expected to exceed its limit |
| 1 | IF: - RTCA or the State Estimator has not solved within the last 10 minutes, THEN: - Notify Shift Engineer, - Refer to Section 3.1 of the Desktop Guide and run through the checklist, - Request Shift Engineer to calculate limits manually if EMS will be unavailable for an extended period of time. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 15 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to issue an Advisory to the TOs: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory due to ERCOT’s RTCA and State Estimator have not solved in the last 15 minutes. Please monitor your own service area and notify ERCOT if you exceed the normal rating of your transmission elements. Report West - North and North – Houston stability limits if power flows reach 70% of their respective limits. Continue to monitor voltages in your area and notify ERCOT of any forced line operations.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Notify the appropriate Nuclear Plant’s QSEs and inform them that ERCOT’s RTCA is not function and is expected to be functional within approximately [# minutes]. |
| 4 | Post Advisory message on MIS Public using Notice Builder. |
| 5 | Once RTCA and State Estimator are operational: Make a Hotline call to cancel the Advisory to the TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory, ERCOT’s RTCA and State Estimator are functioning and we are back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 6 | Notify the appropriate Nuclear Plant’s QSEs to inform them that RTCA is now functional. |
| 7 | Cancel Advisory message on MIS Public using Notice Builder. |
| 8 | If VSAT has not solved within 1 hour: - Manually run VSAT, - If no results, notify Shift Engineer, - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |
| 9 | Make log entry of events. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-003 R1 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006 R1, R4 |
|  | IRO-002 R6, R8 | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |

| Version: 1 | Revision: 11 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. Error! Hyperlink reference not valid.A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) located in the Outage Notes - Unit specific dispatch instructions (Manual Dispatch or VDI) - If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP , - A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congesting management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – Mitigate local congestion and increase W/N transfers - Big Lake – Mitigate local congestion and increase W/N transfers - Firerock ETT – Mitigate local congestion and increase W/N transfers - Nelson Sharp – Valley import during outages and flow in/out of Corpus Christi - Hamilton Road – Control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – Control Laredo import issues during outages - Thomaston – Control flow into Cuero, Yoakum and Victoria Areas |  |
| ### Review Planned Outage Notes |  |  |
| 1 | Review daily outage notes: IF: - Outage notes recommend slower moving Resources to be lowered to maintain system security; THEN: - Consider taking a real-time snap shot to determine where Resource(s) are needed before outage is taken - Use the manual override to step down Resource(s) - Once Resource(s) are down to where snap shot showed, release manual overrides, give approval for switching and activate SCED constraint. |  |
| Log | Log actions taken. |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - SE and/or RTCA is not solving; THEN: - Notify Shift Engineer, IF: - SE and/or RTCA has not solved for 15 minutes, THEN: - Refer to section 3.3 “Analysis Tool Outages” in this procedure. |  |
| 2 | IF: - RTCA has run within 10 minutes; THEN: - Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |  |
| 3 | IF: - A major change of Resource or Transmission Element Status; THEN: - Re-start RTCA and VSAT. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Determine if the SCADA is of similar magnitude to the Pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Shift Engineer. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP, - Refer to “Managing Constraints in SCED” of this Procedure. |  |
| 4 | IF: - Post-contingency overloads greater than 100% exist without an SPS (identified as RAS in EMS), RAP, PCAP, or TOAP in place to relieve; THEN: - Activate constraints as necessary, - Lower the value in the % Rating column in RTCAM to tighten the constraint (minimum of 95%), - Increase the value in the % Rating column in RTCAM to loosen the constraint (maximum of 100%), - If “%Rating” is placed below 95% or above 100%, make log entry with reasoning. - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 5 | IF: - A Qualifying Facility (QF) needs to operate below its LSL, or be ordered off line to solve congestion; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 6 | IF: - Post-contingency overloads greater than 100% of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 7 | IF: - Congestion can not be fully resolved and does not have a MP or RAP; THEN: - REQUEST the Shift Engineer investigate the development of a MP or correct errors in the current plan. |  |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |  |
| 9 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Shift Engineer, - If there are known reasons that the contingency is unsolved, notify the Shift Engineer to verify system conditions have not changed. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A Quick Start Resource is needed and not given SCED base points; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running), - Notify QSE as time permits. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| ### Managing Constraints in SCED |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for exceeded constraints). |  |
| 1 | IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk and control room staff. |  |
| 2 | Steps that may be taken to resolve congestion when a transmission constraint is exceeded in SCED: - Verify telemetry is correct, - Verify that the SCED executions are reducing the flows on the subject constraints, - Investigate units with large shift factors that are not being moved or are not following base points, - Create a “Suggestion Plan” for the constraint, - Redistribute A/S to increase the capacity available to SCED, - Instruct QSE to remove the appropriate A/S and to update telemetry, - Notify Resource Operator with undeliverable A/S type, amount and hours from the Resource(s), - If Non-Spin is deployed for congestion, the telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Removing a unit from ONTEST, - Commit/decommit additional units, - Determine if there is a non-cascading constraint that is less severe and can be released to resolve this constraint, - Release the constraint if non-cascading and if the constraint prevents resolving a more severe insecure state, - Instruct Shift Engineer to formulate a mitigation plan which may include - Transmission reconfiguration (switching) - Load rollover to adjacent feeders - Load shed plans |  |
| 3 | Steps that may be taken to resolve insecure state by overriding HDL/LDL: - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - DO NOT override a Resource ONRR - Notify QSE of override (this could exceed ramp rate) - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. |  |
| NOTE | Possible reasons for manually overriding HDL/LDL could be: - Manually dispatching slower moving Resources before an outage to better manage congestion caused by the outage - Manually overriding Resources which are not following Base Points and are affecting constraint management or frequency - Manually overriding Resources which are causing SPS to continuously trip in Real Time |  |
| Log | Log all action taken (including reason for doing a manual override). |  |
| ### QSE Requests to Decommit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Initiate the Emergency Notice Hotline call, AND - Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 2 | Trouble Shooting: IF: - Transmission constraints are active, THEN: - Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |  |

## 4.3	West-North Stability Limit

Procedure Purpose: Maintain Transmission stability between the West and North.

| Protocol Reference | 3.10.7.6(3) | 6.5.9.1(1)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Refernce |  |  |  |  |
| NERC Standard | EOP-001 R4.2 | IRO-002 R6, R8 | IRO-003 R1 | IRO-004 R3 |
|  | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | IRO-008-1 R2 | IRO-009 R4 |
|  | TOP-002 R10 | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 |
|  | TOP-008 R1 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| NOTE | If unexpected changes to system conditions occur between 1700 – 0900 that result in a large limit change from the day-ahead GTL posting: - Declare a Watch by posting on MIS - Make Hotline call to TOs - Notify Real-Time operator to make hotline call - Ensure Shift Engineer posts new GTL Typical Message Script: “ERCOT has updated the posted West-North GTL limit on the MIS due to an unexpected change on the system.” |
| 1 | IF: - The West-North stability limit calculated on the spreadsheet changes value or color; THEN: - Verify the value is accurate and update limit on RTMONI to give transparency to Market Participants, - Monitor as needed to the value shown on the spreadsheet. |
| NOTE | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. - To update the spreadsheet when any PSS is forced offline in the West zone. - Open the Summary tab to verify units - Enter 0 = PSS is offline, 1 = PSS online for each resource change. It allows the operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |
| 2 | IF: - The monitored flow on the Stability-WN monitor is approaching 80%; THEN: - Activate the West-North constraint, - Post message on MIS Public using Notice Builder, Typical Message Script: “ERCOT is constraining for the West-North stability limit.” |
| 3 | Once wind output is controlled, keep constrained around 86% – 92% IF: - West – North reaches 100%; THEN: - Continue to tighten constraint, - Call QSEs with the largest WGR base point deviations |
| 4 | IF: - West – North exceeds 100% for 10 minutes; THEN: - Instruct QSEs with the largest WGR base point deviation to zero immediately (violate ramp rate), - Issue electronic VDI as time permits, - Notify the control room staff. Typical Script: “This is ERCOT operator [first and last name]. The West to North flow is exceeding the stability limit; At [xx:xx] ERCOT is instructing you to take [unit name] to zero effective immediately, which means you may violate your ramp rate. I will be sending you an electronic VDI shortly. [QSE] please repeat this back to me. That is correct, thank you.” |
| 5 | IF: - Congestion management techniques fail to control the flow within 20 minutes; THEN: - Issue directive to TO to open WGR breaker with the largest WGR base point deviation (refer to Real-Time spreadsheet tab “West Wind”), - Issue electronic VDI as time permits, - Notify the control room staff. |
| Log | Log all actions taken. |

## 4.6	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security.

| Protocol Reference | 6.3.2(2) | 6.5.7.1.10(3) | 6.5.7.8 | 6.5.7.9(7) |
| --- | --- | --- | --- | --- |
|  | 6.5.9 (3) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R6 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: November 1, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The order of steps in this procedure is a recommendation. The System Operator will determine the sequence of steps, or any additional actions necessary to ensure system security. |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instruction under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |
| ### Manual Dispatch Instruction to take a Unit Off-Line |  |
| 1 | This step DOES NOT apply to Qualifying Facilities (QF). For QF’s, refer to Transmission Congestion Management/Post-Contingency Overloads/step 5. IF: - A manual dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue a VDI taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Ensure QSE updates telemetry. |
| ### Taking One CT of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one CT of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and determine which CT should receive the dispatch instruction, - Obtain the MW output impact the CT’s dispatch instruction will have on the steam unit, - Issue VDI to dispatch the CT off-line and instruct the QSE to adjust their CC configuration. - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” |
| ### Manual Commit of a Resource |  |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition; THEN: - Issue a VDI to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name or capacity in “other information” - See Desktop Guide Section 8.3 for additional information to submit a correct VDI. |
| 2 | Log information. |
| ### Canceling RUC Commitments |  |
| 1 | IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information |
| 2 | Log information. |
| ### Posting Manual Actions |  |
| 1 | IF: - Any manual action is taken (manual override or VDI); THEN: - Post message on MIS Public using Notice Builder. Typical Posting Script: ERCOT is taking manual actions for XXXX constraint. |
| 2 | Log information. |

## 9.1	Weekly Hotline Test

Procedure Purpose:  To perform a weekly communications test of the ERCOT Hotline phone system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.1.3(3) |  |  |  |
| NERC Standard | COM-001-1.1 R2 | EOP-005-1 R5 |  |  |

| Version: 1 | Revision: 3 | Effective Date: November 1, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | In the event of a failure of the Forum Conference Client software, the most recent printout of the Hotline log may be used to perform a manual roll call of TOs. |
| NOTE | Insure all Invalid Hotlines “Lost Souls” are cleared prior to the hotline call. |
| NOTE | Confirm with Shift Supervisor the threat alert level, which can be viewed at the following links: http://www.esisac.com/SitePages/Home.aspx, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert level are listed in the Security Alert Plan. |
| 1 | Each Monday between 0630 and 1100 test the ERCOT Hotline |
| 2 | Using the Hotline, notify all TOs of the purpose of the call. - When QSEs/TOs have answered the Hotline, print Hotline participants and log any issues. If necessary call participants individually. Typical Script: “This is ERCOT Operator [first and last name]. ERCOT is conducting the weekly [TO] Hotline test. ERCOT is currently at threat alert level [state alert level]. The following notices are currently in effect: - List OCNs, Advisories, Watches and/or Emergency Notices in effect. - State “None” if none are in effect. This ends the test of the ERCOT Hotline. That is all.” |
| 3 | Notify the Shift Supervisor of any TO that did not respond to the Hotline test. The Shift Supervisor and/or the Help Desk may notify the telecommunications department for repairs. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 - / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.47.5 7.6 10.1 | - / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |