## Power Operations Bulletin # 574

ERCOT has posted/revised the Transmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	Site Failovers and Database Loads

Procedure Purpose: To provide notice to the Market Participants when ERCOT performs site failovers and database loads.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Database Load | Approximately 5 - 30 minutes before a database load, make the following Hotline call to TOs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a database load on its Energy & Market Management Systems. During this time, SCED Base Points will reflect accurate dispatch instructions. In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes. |
| Site Failover | Approximately 5 - 30 minutes before site failover, make the following Hotline call to TOs: Typical Script: This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 30 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. |
| Database Load With W-N Active | IF: - The West – North is active; THEN: - Before database load, ensure W-N is constrained to ≤ 70%. |
| Site Failover With W-N Active | IF: - The West – North is active; THEN: - Approximately 5-10 minutes before site failover, - Verify with Real-Time operator is aware constraint is active, - Ensure W-N is constrained to ≤ 70%. |
| Site Failover Posting | Verify with Real-Time operator that posting will be made. The site failover message is already built in Notice Builder under “EMS Site Failover”. |
| Site Failover Complete | Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], the site failover is complete. [TO] please repeat this back to me. That is correct, thank you.” |

## 3.1	System Overview

Procedure Purpose: Analyze data to maintain system security.

| Protocol Reference | 6.3.2(3)(a) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-1 R6, R8 | IRO-005-2 R1.1, R1.2, R1.3 | NUC-001-1 | PRC-001-1 R2.2 |
|  | TOP-006-1 R2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: December 15, 2010 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Review | REVIEW each of the following as necessary to confirm system reliability status: - Alarms - State Estimator (SE) - Real Time Contingency Analysis (RTCA) - Transmission Constraint Manager (TCM) - Approved and Forced Outages - Load Forecast - Daily Transmission Limits - Voltage and Stability Limits - Real Time Monitoring (RTMONI) - Security Constrained Economic Dispatch (SCED) - Real Time Reserve Monitoring |
| Gap Study | Run a gap study for the peak hour to ensure all contingencies can be solved. If necessary, request the Shift Engineer to review results and make suggestions. If both CPSES units are offline, the Auxiliary load will need to be manually adjusted to 45 MW at both units. Make a log entry with your results. |
| STP Lines | A minimum of two transmission lines should be in service at all times. The in-service lines should be from at least two of the groups in the table below: Independent Groups of STP Transmission Lines Group 1; Group 2; Group 3. STPZWP39; STPELM18; DOWSTP18. STPELM27; DOWSTP27. STPWAP39. Note: The 3 Transmission lines, STP – Blessing (BLESSING), STP – HILLJE (HLJSTP64), STP – HILLJE (CKT_3124) (EMS naming convention) are not included in this table because these circuits are not part of STP’s credited offsite sources. If a minimum of two lines are not in service, notify the QSE. |
| Protective Relay or Equipment Failure | When notified by a TO that a protective relay or equipment failure reduces system reliability: - Ask the TO how it reduces ERCOT Grid system reliability and if any corrective actions have been taken, - Notify the Shift Engineer to verify that system reliability has been affected. If so, a corrective action must be taken within 30 minutes, - Determine if other TOs are affected by this failure and make notification by phone, - Make log entry of events. |
| Dynamic Transmission Limits | IF: - Any changes in the system that could affect the security and dynamic transmission limits; THEN: - Post message on MIS Public using Notice Builder. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-003 R1 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006-5 R1, R4 |
|  | IRO-002 R6, R8 | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |

| Version: 1 | Revision: 12 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to ensure system security. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. Error! Hyperlink reference not valid.A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) located in the Outage Notes - Unit specific dispatch instructions (Manual Dispatch or VDI) - If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP , - A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congesting management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – Mitigate local congestion and increase W/N transfers - Big Lake – Mitigate local congestion and increase W/N transfers - Firerock ETT – Mitigate local congestion and increase W/N transfers - Nelson Sharp – Valley import during outages and flow in/out of Corpus Christi - Hamilton Road – Control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – Control Laredo import issues during outages - Thomaston – Control flow into Cuero, Yoakum and Victoria Areas |  |
| ### Review Planned Outage Notes |  |  |
| 1 | Review daily outage notes: IF: - Outage notes recommend slower moving Resources to be lowered to maintain system security; THEN: - Consider taking a real-time snap shot to determine where Resource(s) are needed before outage is taken - Use the manual override to step down Resource(s) - Once Resource(s) are down to where snap shot showed, release manual overrides, give approval for switching and activate SCED constraint. |  |
| Log | Log actions taken. |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - SE and/or RTCA is not solving; THEN: - Notify Shift Engineer, IF: - SE and/or RTCA has not solved for 15 minutes, THEN: - Refer to section 3.3 “Analysis Tool Outages” in this procedure. |  |
| 2 | IF: - RTCA has run within 10 minutes; THEN: - Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |  |
| 3 | IF: - A major change of Resource or Transmission Element Status; THEN: - Re-start RTCA and VSAT. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Determine if the SCADA is of similar magnitude to the Pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Shift Engineer. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP, - Refer to “Managing Constraints in SCED” of this Procedure. |  |
| 4 | IF: - Post-contingency overloads greater than 100% exist without an SPS (identified as RAS in EMS), RAP, PCAP, or TOAP in place to relieve; THEN: - Activate constraints as necessary, - Lower the value in the % Rating column in TCMM to tighten the constraint (minimum of 95%), - Increase the value in the % Rating column in TCM to loosen the constraint (maximum of 100%), - If “%Rating” is placed below 95% or above 100%, make log entry with reasoning (excluding W-N). - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 5 | IF: - A Qualifying Facility (QF) needs to operate below its LSL, or be ordered off line to solve congestion; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 6 | IF: - Post-contingency overloads greater than 100% of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 7 | IF: - Congestion can not be fully resolved and does not have a MP or RAP; THEN: - REQUEST the Shift Engineer investigate the development of a MP or correct errors in the current plan. |  |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint then the constraint will be passed to SCED immediately, - Manually execute the SCED process, - Refer to “Managing Binding and Exceeded Constraints”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |  |
| 9 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Shift Engineer, - If there are known reasons that the contingency is unsolved, notify the Shift Engineer to verify system conditions have not changed. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A Quick Start Resource is needed and not given SCED base points; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running), - Notify QSE as time permits. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| ### Post-Contingency Overloads on Private Use Networks (PUNs) |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Contact the PUNs QSE to determine if the post-contingency is real (review MW, MVAR flows and facility ratings), - If real, give the QSE the opportunity to correct or request a Mitigation Plan for the contingency. |  |
| 2 | IF: - Mitigation Plan is needed; THEN: - Notify the Shift Engineer to work with the QSE to approve a plan. |  |
| 3 | IF: - It is determined that the post-contingency is real and a Mitigation Plan will not be approved; THEN: - Direct the QSE to take action such as lower/raise generation or load (direct only, do not override HDL/LDL or activate constraint in SCED). |  |
| 4 | - Acknowledge the post-contingency overload in TCM - Make log entry of actions taken |  |
| ### Managing Constraints in SCED |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for exceeded constraints). |  |
| 1 | IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk and control room staff. |  |
| 2 | Steps that may be taken to resolve congestion when a transmission constraint is exceeded in SCED: - Verify telemetry is correct, - Verify that the SCED executions are reducing the flows on the subject constraints, - Investigate units with large shift factors that are not being moved or are not following base points, - Create a “Suggestion Plan” for the constraint, - Redistribute A/S to increase the capacity available to SCED, - Instruct QSE to remove the appropriate A/S and to update telemetry, - Notify Resource Operator with undeliverable A/S type, amount and hours from the Resource(s), - If Non-Spin is deployed for congestion, the telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Removing a unit from ONTEST, - Commit/decommit additional units, - Determine if there is a non-cascading constraint that is less severe and can be released to resolve this constraint, - Release the constraint if non-cascading and if the constraint prevents resolving a more severe insecure state, - Instruct Shift Engineer to formulate a mitigation plan which may include - Transmission reconfiguration (switching) - Load rollover to adjacent feeders - Load shed plans |  |
| 3 | Steps that may be taken to resolve insecure state by overriding HDL/LDL: - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - DO NOT override a Resource ONRR - Notify QSE of override (this could exceed ramp rate) - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. |  |
| NOTE | Possible reasons for manually overriding HDL/LDL could be: - Manually dispatching slower moving Resources before an outage to better manage congestion caused by the outage - Manually overriding Resources which are not following Base Points and are affecting constraint management or frequency - Manually overriding Resources which are causing SPS to continuously trip in Real Time |  |
| Log | Log all action taken (including reason for doing a manual override). |  |
| ### QSE Requests to Decommit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Initiate the Emergency Notice Hotline call, AND - Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 2 | Trouble Shooting: IF: - Transmission constraints are active, THEN: - Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |  |

## 4.4	North-Houston Voltage Stability Limit

Procedure Purpose:  Maintain Transmission Stability between the North and Houston.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R2, R4.2 | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 |
|  | IRO-004 R3 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 | IRO-008-1 R1 |
|  | TOP-002 R10 | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 |
|  | TOP-008 R1 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT Dynamic Voltage Stability Limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards |
| VSAT | - Ensure VSAT runs every 30 minutes, - Update RTMONI with new limit each time it changes to give transparency to Market Participants. |
| NOTE | When an unexpected change to system conditions occur between 1700 – 0900 that result in a large limit change from the day-ahead GTL posting: - Declare a Watch by posting on MIS - Make Hotline call to TOs - Notify Real-Time operator to make hotline call - Ensure Shift Engineer posts new GTL Typical Message Script: “ERCOT has updated the posted North - Houston GTL limit on the MIS from what was posted in Day-Ahead due to an unexpected change on the system.” |
| North-Houston 345kV Circuit Outage | IF: - Any of the 345kV lines going into the Houston area has a forced outage; THEN: - Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor Step in this procedure. |
| Monitor | Monitor each of the following Reliability Margins: - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TOs in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| ≤400MW | - Activate the appropriate constraint, - Post message on MIS Public using Notice Builder. Typical Message Script: “ERCOT is constraining for the North-Houston voltage stability limit.” |
| ≤300MW | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL - Instruct Resource Desk Operator to deploy Non-Spin in the Houston area and make Hotline notification, - Issue a Transmission Watch by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North-Houston interface. Non-Spin is being deployed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| NOTE | When the Non-Spin Resource is on-line, they must change their Non-Spin schedule to 0 in order for SCED to dispatch them. |
| ≤200MW | VDI QSGR in the Houston area that were not bid in as Non-Spin. Override LDLs as needed. - Determine QSRG in the Coast Weather Zone (WZ_COAST) - Choose “COMMIT” as the Instruction Type from Resource level |
| ≤100MW | - Instruct the Resource Desk Operator to deploy Load Resources providing RRS in Houston, - Issue a Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Real-Time Operator to make same Hotline notification to QSEs, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice for the North-Houston interface. Load Resources in the Houston area are being deployed to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| 0MW ≥ 15 Minutes | - Instruct Centerpoint to drop firm load in 100 MW blocks. - Continue Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make NXT notification and RCIS posting. Typical Script for Centerpoint: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is instructing Centerpoint to drop [*** MW] of firm load for the North – Houston stability limit. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” Typical Script for Hotline: “At [xx:xx], ERCOT is continuing the Transmission Emergency Notice for the North-Houston interface. Firm Load is being shed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| Cancel | Make appropriate cancellations when back to normal operations. |
| Log | Log all actions taken. |

## 4.5	SPS, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 5.5.2 | 6.5.1.1(a),(c),(e) |  | 6.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.5.2(1) | 6.5.7.1.10 | 6.5.7.1.11(1),(4) | 6.5.7.8 |
|  | 6.5.9 | 6.5.9.1(1)(d) |  | 7.1 |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R2, R3.2, R3.3, R4.2 | IRO-003 R1 | IRO-005-2 R1.1,R1.2, R1.3, R1.7, R1.10, R3, R5, R9, R12, R13, R16, R17 | IRO-006-3 R1, R3, R4, R5, R6 |
|  | IRO-002-1 R6, R8 | IRO-004-1 R3 | TOP-001 R1, R2, R5 | TOP-002-2 R6, R8, R10 |
|  | TOP-004-1 R1, R6, R6.6 | TOP-006-1 R3, R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6, R8 |
|  | PRC-001-1 R6 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP |
| NOTE | Special Protection Schemes (SPS) (identified as RAS in EMS) OR Remedial Action Plans (RAP) - EXAMINE the results of RTCA, - If the background has a color indicating a SPS or RAP, - Refer to Section 3.6 of the Desktop Reference Guide for actions to be taken based on the color of the background. |
| Directives | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log all actions taken. |
| ### Special Protection Systems (SPS) (Identified as RAS in EMS) |  |
| NOTE | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingency loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario, congestion management is not needed until the criteria in Section 3.6 of the Desktop Reference Guide, is met. |
| Monitor | Each SPS will be displayed on the “Real Time Values” spreadsheet, as the SPS activation threshold increases the display changes color as follows: - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 1 | Typically SPSs are to solve post-contingency overloads on the Transmission System. IF: - The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an SPS; THEN: - Utilize congestion management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the SPS will not mitigate all the overloaded elements automatically; THEN: - As system conditions warrant, utilize congestion management techniques to relieve the overload. |
| 3 | IF: - No reliability issues will arise as a result of a SPS’s operation; THEN: - At the Operator’s discretion, allow the SPS to perform its function. |
| 4 | IF: - A WGR SPS on the “Real Time Values” spreadsheet is greater than 90%; THEN: - Active the appropriate generic constraint in TCM. |
| 5 | IF: - An SPS operates; THEN: - Notify affected TO to reset SPS as system conditions warrant, - Notify Shift Supervisor of the need for a Texas RE Report if generation disconnected from the grid or a transmission line tripped. |
| SPS Posting | All SPSs are considered in-service unless otherwise notified by the TO. If the SPS is out of service, ERCOT will post the information on MIS Public using Notice Builder. Once the SPS is placed back in service, ERCOT will cancel the message. Typical MIS posting: The [name] SPS has been taken out of service. |
| Status Change | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated, - “OPS Support Engineering” - “1 ERCOT System Operators” - “DAMTeam” Typical MIS posting: The [name] SPS has been taken out of service. The [name] SPS has returned to service. |
| ### Remedial Action Plan (RAP) |  |
| 1 | TCM DOES NOT model RAPs when generating constraints so they tend to over-constrain at 100% of emergency rating instead of 100% of the 15min rating. - Activate constraints as necessary, - Lower the value in the % Rating column in TCM to tighten the constraint (minimum 95%), - Increase the value in the % Rating column in TCM to loosen the constraint (maximum 100%). |
| 2 | IF: - A RAP exists for the contingency; THEN: - Review the RAP with the associated TO, - Notify the Shift Supervisor of the anticipated actions. |
| 3 | IF: - The contingency anticipated by the RAP takes place; THEN: - Direct the implementation of the RAP, - Respond to requests made by the TO in accordance with the RAP, - If necessary, continue to use additional congestion management methods, - When the contingency clears, notify the TO as soon as possible. |
| ### Pre-Contingency Action Plan (PCAP) |  |
| CAUTION | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. These actions may be taken to increase transmission transfer capability. |
| 1 | WHEN: - RTCA shows a post-contingency overload and a PCAP exists to resolve it; THEN: - Review the PCAP with the associated Transmission Operator, - Notify the Shift Supervisor of the anticipated actions, - Direct the execution of the PCAP with the associated Transmission Operator. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [TO] to implement the ****PCAP and [open/close] [breaker(s)]. [TO] please repeat this back to me. That is correct, thank you.” |
| NOTE | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 2 | IF: - Any PCAPs are still in use (reviewed each day between 0000 and 0500), AND - It is determined, in concurrence with the Shift Supervisor that it is no longer needed; THEN: - Direct the associated Transmission Operator to return the system to: - Its normal status, OR - Its status prior to implementation of the PCAP. |
| ### Mitigation Plan (MP) |  |
| NOTE | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. - With a MP, an operator does not need to declare a Watch for a post contingency overload, - If a MP is enacted and subsequent congestion management techniques do not control post contingency loading, issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder |
| 1 | IF: - A MP exists for the contingency; THEN: - Activate constraint if shift factors exist for ≥ 2% - Review the MP with the associated TO, - TO repeats back the MP to verify the plan is understood |
| 2 | IF: - A MP does not exist or fails to relieve the overload for this contingency and the Outage Notes do not provide a plan; THEN: - REQUEST the Shift Engineer investigate the development of a MP or correct errors in the current plan. |
| 3 | IF: - The anticipated contingency takes place; THEN: - Direct the implementation of the MP to the TO, - TO repeats back directive to verify implementation is understood, - Respond as quickly as possible to requests made by the TO in accordance with the MP, - If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP. |
| 4 | WHEN: - The contingency clears; THEN: - Notify the TO as soon as possible. |
| ### Temporary Outage Action Plan (TOAP) |  |
| 1 | IF: - The post-contingency overload is due to a temporary outage on a transmission line(s) or a transmission facility; THEN: - Locate the outage in the Outage Notes, - Implement the associated actions. |

## 4.6	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security.

| Protocol Reference | 6.3.2(2) | 6.5.7.1.10(3) | 6.5.7.8 | 6.5.7.9(7) |
| --- | --- | --- | --- | --- |
|  | 6.5.9 (3) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R6 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instruction under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |
| ### Manual Dispatch to take a Unit Off-Line |  |
| 1 | This step DOES NOT apply to Qualifying Facilities (QF). For QF’s, refer to Transmission Congestion Management/Post-Contingency Overloads/step 5. IF: - A manual dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue a VDI taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Ensure QSE updates telemetry. |
| ### Manual Dispatch to take a Unit of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one unit of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and request which unit the QSE would like to shutdown, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue VDI to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Log the above information. |
| ### Manual Dispatch to bring a Unit of a Combined Cycle On-line |  |
| 1 | IF: - System conditions require a unit of a Combined Cycle Plant to be manually dispatched on-line; THEN: - Contact the QSE and notify which unit will be committed, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue VDI to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Log the above information. |
| ### Manual Commit of a Resource |  |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition; THEN: - Issue a VDI to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name or capacity in “other information” - See Desktop Guide Section 8.3 for additional information to submit a correct VDI. |
| 2 | Log information. |
| ### Canceling RUC Commitments |  |
| 1 | IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information |
| 2 | Log information. |
| ### Posting Manual Actions |  |
| 1 | IF: - Any manual action is taken (manual override or VDI); THEN: - Post message on MIS Public using Notice Builder. Typical Posting Script: ERCOT is taking manual actions for XXXX constraint. |
| 2 | Log information. |

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15 | 6.3.1 (1) | 6.3.2(2) | 6.5.1.1(a)&(c) |
| --- | --- | --- | --- | --- |
|  | 6.5.5.1(2) &(3) | 6.5.6 | 6.5.7 | 6.5.7.7 |
|  | 6.5.9.1(1)(c) | 6.6.7.1 | 6.7.6 |  |
| Guide Reference | 2.2.4 | 2.7.2(h)(ii) | 2.7.4.1(1) | 2.7.4.3 |
| NERC Standand | IRO-005-2 R1.2, R1.3, R1.4 | NUC-001-2 R4.2 | TOP-002-2 R8, R10 | VAR-001-1 R1, R2, R4, R6, R7, R8, R9, R10, R12 |
|  | VAR-002-1 R3.1 | IRO-002-1 R6, R8 | TOP-004-2 R6.2 | TOP-006-1 R2 |
|  | EOP-001-0 R4.2 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "normal" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS) Secure site. Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Voltage Tables | For Comanche Peak - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. For South Texas Project - System; - 345 kV. - Nominal Voltage; - 362.25 kV. - Tolerance; - +0% or -6.14%. - Maximum Voltage; - 362.25 kV. - Minimum Voltage; - 340 kV. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. When STP is in an alternate line up, the minimum voltage is 347 kV. When STP is in an alternate line up without the unit auxiliary transformer, the minimum voltage is 355 kV. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated in the voltage tables; THEN: - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate QSE. |
| ### Voltage Issues |  |
| NOTE | - Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Section 3.9 of the Desktop Guide. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damages is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implements and studies shall that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. |
| 1 | WHEN: - Indicated by SCADA alarms, OR - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. |
| 2 | WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct a QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| Exceed URL | For multi-generator busses, ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL until all On-Line Generation at the same transmission bus have been instructed to their respective CURLs or URLs. IF: - Instructing a QSE’s Generation Resource to exceed its Unit Reactive Limit (URL); THEN: - Issue a VDI to the QSE for exceeding the URL (Exceed URL VDI). The VDI must include the following: - Resource name - Specific voltage set point. - Start time - End time - Choose “HOLD X VOLTAGE LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| Reduce MW | IF: - MW output must be reduced to follow a voltage support instruction; THEN: - Issue a VDI to the QSE providing Voltage Support Service (VSS VDI). The VDI must include the following: - Resource name - MW level at time of instruction - MW level Resource needs to move to for Voltage Support - Start time - End time - Choose “STAY AT/ABOVE X MW/MVAR LEVEL” or “STAY AT/BELOW X MW/MVAR LEVEL” as the Instruction Type from Resource level - Notify Shift Engineer of instruction, they will be providing analysis to Settlements. |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| NOTE | The North – Houston VSAT dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure section 4.4. |
| 1 | IF: - VSAT has not run in the last 45 minutes, OR - VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status; THEN: - Rerun the RTNET, RTCA, and RTDCP (VSA). If no change, then: - Notify the Shift Supervisor and Shift Engineer - As deemed necessary make the following Hotline call. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is experiencing problems with the Voltage Stability Analysis program. Maintain voltage levels as required by your procedures and notify ERCOT of any voltage issues within your system. [TO] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) more frequently than the periodic scheduled VSAT run. - Confirm VSAT indicates either “Normal” or “Pending”. Reliability Margin Table. Scenario Name; Safety Margin. O-DFW_L; 200MW. O-CORP_L; 75MW. O-VAL_L; 75MW. O-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. For N-H_G and N_H_L: Refer to section 4.4 North-Houston Voltage Stability Limit of this procedure. |
| 3 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the Extra-Interface Limit pre-contingency value is less than the Safety Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 4. |
| 4 | Determine the contingency status in RTCA (solved/unsolved).IF: - Solved, - Have Shift Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Shift Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct HRUC Operator to commit additional resources in the weak bus area that are available. |
| 5 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 6 | Determine if the Extra-Interface Limit pre-contingency value is greater than the Reliability Margin Value. IF: - The Extra-Interface Limit pre-contingency value is greater than the Reliability margin; THEN: - No further action is required. OR IF: - The Extra-Interface Limit pre-contingency value is less than the Reliability margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 4. If no additional generation is available, continue. |
| 7 | IF: - No additional generation is available; THEN: - Ensure that the OPS Support Engineering group has been contacted to devise a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT. |
| NOTE | Operations Support will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > AVR AND PSS Status |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, - Notify the appropriate TO of the change in status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “1 ERCOT System Operators” |
| 2 | A table which is enterable by the operator has been added for the calculation on the “W-N Stability” spreadsheet. To update the “real time values” spreadsheet when any PSS is forced offline in the West zone: - Open the Stability Limit tab to verify units, - Enter 0 = PSS is offline; 1 = PSS online for each resource change. It allows the Operator to “turn off” a unit when a QSE reports the PSS is out of service which lowers the stability limit. |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 7 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources - When cold weather is 5 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region - When severe cold weather is 5 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - When an approaching Hurricane / Tropical Storm is approximately 5 days away. Unplanned Transmission Outages that may impact System reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When cold weather is 3 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 3 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect System Reliability. Available RMR resources will be committed during the HRUC study. - When an approaching Hurricane / Tropical Storm is approximately 1 day away. - When cold weather is 1 day away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones. - When severe cold weather is 1 day away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones. - When temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones or when temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. - ERCOT varies from time-line for DAM/DRUC. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - Loss of Primary Control Center Functionality. - Load Resource deployment for North-Houston voltage stability. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED). - When cold or severe cold weather is in the ERCOT Region and it is beginning to have an adverse impact on the ERCOT System. |
| ### Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on the MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 8.1	Hurricane / Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 3 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov) |
| NOTE | Operations Support will analyze the situation and make recommendations as to Resource requirements and transmission topology. |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. Coordinate with Outage Coordination for the review of planned and existing outages to be rejected and/or restored. Using the Hotline, issue an OCN to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a [Tropical Storm/Hurricane] [Name] due to a probability of making landfall in the ERCOT Region. TOs are instructed to: - Review planned and existing transmission outages to be withdrawn and/or restored - Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. Using the Hotline, issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is currently projected to impact the ERCOT Region. TOs are instructed to: - Review planned and existing transmission outages to be withdrawn and/or restored. - Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities. - Test communication with other TDSP's and QSEs prior to the hurricane making landfall. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. Using the Hotline, issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is expected to make landfall near [Place] at [time]. TOs are instructed to: - Be prepared to lose load and expect high voltage conditions - Keep ERCOT informed of transmission outages. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency | When Hurricane/Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to [Tropical Storm/Hurricane Name] having an adverse impact on the ERCOT System [specify condition]. TOs are instructed to: - Be prepared to lose load and expect high voltage conditions - Keep ERCOT informed of any issues ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public using Notice Builder. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

## 8.3	Severe Cold Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for severe cold weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 3 | Effective Date: December 15, 2011 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Severe cold weather notifications are called when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. |
| OCN |  | When approaching severe cold weather is approximately 5 days away. Using the Hotline, issue an OCN to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a severe cold weather system approaching in the next 5 days with temperatures anticipated to remain 32°F or below in five or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the severe cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory |  | When approaching severe cold weather is 3 days away. Using the Hotline, issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the severe cold weather system approaching in the next 3 with temperatures anticipated to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the severe cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch |  | When approaching severe cold weather is 1 day away. Using the Hotline, issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the severe cold weather system approaching tomorrow. Temperatures are expected to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Prepare for higher than usual loads, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the severe cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency Notice | When severe cold weather is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the severe cold weather system is in the ERCOT Region with temperatures between20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. The frigid temperatures are beginning to have adverse impact on the ERCOT System such as [state what the adverse impacts are]. - Prepare for higher than usual loads and the possibility of load shedding. - Review emergency operating procedures and immediately notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |  |
| Post | Coordinate with the Real-Time Operator for the posting of the notices on MIS Public using Notice Builder. |  |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on MIS Public. |  |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 - / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | - / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT) Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |