## Power Operations Bulletin # 576

ERCOT has posted/revised the Real Time Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 1.2	Scope

The instructions contained in these procedures are limited to those required for the Real-Time Desk.  Instructions for other ERCOT Control Room Positions are contained in separate procedures, one for each position.  These Procedures do not imply that the duties contained herein are the only duties to be performed by this position.  The individual assigned to this position will be required to follow any other instructions and perform any other duties required or requested by appropriate ERCOT Supervision.  Although the steps within the procedures are numbered, the numbering is for indexing purposes and are not sequential in nature.  The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions.

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.3.2(2) | 6.5.7.6.2.2 | 6.5.9.1(1)(b) | 8.2 (2)(b)(vii) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.3.1.2 |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6 | BAL-005-0.b R8 | BAL-007 (Field Trial) | EOP-002-2.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: January 19, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Maintain System Frequency |
| Objective | Frequency should be maintained within +/- 0.03 Hz of schedule Attempt to maintain CPS1 scores over 100 |
| CPS1 less than 100 | IF: Performance drops below 100 for over three consecutive hours; THEN: LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 587 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -587 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) |
| Base Point Deviation | IF: A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: Notify the QSE of the issue. |
| Frequency Deviations | IF: Frequency deviations are equal to or greater than +/- 0.10 Hz, OR Sudden loss of generation greater than 450 MW; THEN: Log the following information: Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) If unit trip: Time of unit trip, Name of unit, Approximate net MW on unit, Approximate lowest frequency, Amount of RRS deployed (if any), AND Approximate ERCOT load. |
| Automatic SCED Runs | LFC triggers automatically when one of the following occurs: Frequency reaches 59.91 Hz or below, SCED runs within a minute of LFC trigger If frequency stays below 59.95 for more than 50 seconds, LFC triggers SCED to run |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: QSE will request VDI(s) Choose Resource tab Choose requesting QSE for Participant Name Choose Resource name Enter MW amount deployed in Current Operating Level Choose Other For Resource for Instruction Type State Hydro deployed in response to frequency in Other Information Initiation Time, and Completion Time A VDI will be needed for each Resource IF: QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR Request QSE to remain On-line May not exceed 30 minutes per deployment for each frequency deviation or event Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| Response to High Frequency |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND Regulation Down service remains and is deploying; THEN: Manually run SCED IF: Frequency goes above 60.05 Hz, AND Out of Down Regulation; THEN: CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, Enter manual offset (the offset will continue until removed). IF: There is no generation left for SCED to lower; THEN: Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, Call QSE with instruction and follow up with an electronic VDI Choose “DECOMMIT” as the Instruction Type from Resource level Enter “capacity surplus” in “other information” |
| 10 MINUTES | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, Verify SCEDs capacity to decrease Base Points GEN-LDL, Enter manual offset, Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, Verify SCEDs capacity to decrease Base Points GEN-LDL, Re-adjust manual offset, Manually run SCED, Log the event and notify Shift Engineer to send an event notification to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. IF: There is no generation left for SCED to lower; THEN: Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, Call QSE with instruction and follow up with an electronic VDI Choose “DECOMMIT” as the Instruction Type from Resource level Enter “capacity surplus” in “other information” |
| 20 Minutes | IF: 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, Call QSE with instruction and follow up with electronic VDI Choose “DECOMMIT” as the Instruction Type from Resource level Enter “capacity surplus” in “other information” |
| 25 Minutes | IF: 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, Call QSE with instruction and follow up with electronic VDI Choose “DECOMMIT” as the Instruction Type from Resource level Enter “capacity surplus” in “other information” |
| Stable | IF: A manual offset was used; THEN: Ensure that it has been removed. |
| Log | Log all actions taken. |
| Response to Low Frequency |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: Hydro RRS - 59.75 Hz Load Resource providing RRS – 59.7 Hz |
| Monitor/ Deploy | IF: Frequency drops below 59.95 Hz, AND Regulation Up service remains and is deploying; THEN: Manually run SCED (do not run SCED more than once between SCED runs) IF: Frequency drops below 59.95 Hz, AND Out of Up Regulation; THEN: Check the GTBD_TO_HDL on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset If using OpsMon Dashboard, do not enter an offset > than GTBD_TO_HDL If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: Frequency is below 59.95 Hz and out of Up Regulation, AND GTBD_TO_HDL on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS does not have adequate up room; THEN: Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS Check the “Manual RRS” to activate box, Enter the “Desired RRS MW”, Select Enter, Select Commit. QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, Confirm Responsive Reserve has been deployed, Verify SCEDs capacity to increase Base Points, Enter manual offset If room is available Manually run SCED IF: There is no generation left for SCED to increase; THEN: Confirm with the Resource Operator that Non-Spin has been deployed, Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS Check the “Manual RRS” to activate box, Enter the “Desired RRS MW”, Select Enter, Select Commit. QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. Remember to remove the manual RRS amount when frequency has recovered. Notify the Shift Supervisor of the need to possibly commit additional Resources. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, Verify SCEDs capacity to increase Base Points (HDL-GEN), Re-adjust manual offset, If room is available Manually run SCED, Log the event and notify Shift Engineer to send notification of the event to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. |
| 20 Minutes | IF: 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, Verify SCEDs capacity to increase Base Points (HDL-GEN), Re-adjust manual offset, If room is availableManually run SCED. |
| 25 Minutes | IF: 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, Verify SCEDs capacity to increase Base Points, Re-adjusted manual offset, Do Not enter an offset > than (HDL-GEN) Manually run SCED. |
| Stable | IF: RRS was manually deployed; THEN: Uncheck the Activate Manual Responsive Reserve, IF: An manual offset was used; THEN: Ensure that it has been removed. |
| Log | Log all actions taken. |
| Monitor Frequency for the Loss of EMS or Site Failover |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. ERCOT Control Room digital wall frequency displays PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or PI ProcessBook → ERCOT → TrueTime Frequency (Austin) |
| Actions When Frequency Telemetry is Incorrect |
|  | IF: Frequency is believed to be incorrect; THEN: Check the current Frequency and switch to a different source, Contact the Help Desk. |

## 4.1	Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved and that the solution is reasonable.

| Protocol Reference | 3.8.3 | 6.3.2(2) | 6.5.7.1.13(3) | 6.5.7.6.2.1(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.7.6.2.2 | 6.5.7.6.2.1(1) | 6.5.7.6.2.1(4) | 6.5.1.1(b) |
|  | 6.5.5.2(6) | 6.5.7.6.2.3 | 6.5.9.1(2) |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: January 19, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Workflow Controller Messages |
| NOTE | The SCED Workflow Controller provides three color coded messages as indicated in the following: GREEN – Informational (i) and Success (s) BLUE – Warning (w) RED – Error (e) and Fatal Error (f) |
| 1 | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages Monitor SCED Workflow Controller logs for “Warning” and “Error” messages. |
| 2 | IF: The log indicates an “Error” or “Fatal Error”; THEN: Contact the Help Desk and notify all Control Room staff, Attempt to resolve the issue following, refer to Section 5.5 of the Desktop Guide, Refer to Section 3.2 “Managing SCED Failures” in this procedure. |
| SCED Solution Time Parameter |
| NOTE | Typically SCED should produce a solution within 20 seconds. It is highly desirable to have at least 3 executions of SCED in any 15 minute period. |
| Automatic Trigger | Verify that SCED is automatically triggered: Periodically every 5 minutes About 60 seconds after RRS is automatically deployed by LFC IF: SCED is not automatically executed (but has not failed); THEN: Manually execute SCED, Immediately notify the Shift Supervisor and Shift Engineer, Continue to manually execute SCED approximately every 5 minutes until the condition is corrected. |
| Manual Trigger | SCED may be manually triggered when the following is identified: Frequency deviates +/-0.05 Hz for more than 5 minutes Generation Resource trips and Frequency is > 59.91 Hz When approximately 50% of Regulation has been deployed Approximately 60 seconds after Generation Resources providing RRS have been deployed. As frequently as needed after Load Resources providing RRS have been deployed. |
| LOG | Log all actions taken as necessary. |
| Large Resource Trips or Runbacks |
| 1 | IF: A QSE has the loss of any Resource greater than 200 MW; THEN: Review the following: Ensure their telemetry reflects the trip, Manually deploy SCED if needed, Determine the impact on (HASL-GEN), Notify Control Room staff of all actions taken Log the event. |
| NOTE | See Section 3.1, Frequency Control Operating Procedure. |
| Quick Start Generation Resource |
| QSGR | A Generation Resource that in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test that establishes an amount of capacity that can be deployed within a ten minute period. |
| COP | The QSE for a QSGR that is available for deployment by SCED shall set the COP Resource Status ON, the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spin, then the A/S Resource Responsibility for Non-Spin shall be set to the Resource’s Non-Spin responsibility in the COP. If the Resource’s Non-Spin responsibility is greater than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP LSL to zero. |
| Telemeter | The QSGR that is available for deployment by SCED shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR that is providing Off-Line Non-Spin shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED. A QSGR with a telemeter breaker status of open and a telemeter Resource Status of ON shall not provide Regulation or Responsive Reserve Service. |
| QSGR Qualification Test | WHEN: Conducting a QSGR qualification test for Operations Analysis; THEN: Issue a VDI Choose “OTHER_RES” as the Instruction Type from Resource level Enter “QSGR Qualification Test” in “Other Information” |
| Generation Resource Shut-down/Start-up Process |
| NOTE | ERCOT’s preferred methodology for moving a generator output down to a state suitable for de-synchronization: All A/S Responsibility assigned to the Resource must first be moved to other Generation Resources, Generation Resources are expected to be on normal SCED control until reaching no greater than 110% of the units normal LSL before changing status to “ONTEST”. This can be accomplished by the QSE doing one of the following: Allow SCED to move the unit down to LSL by normal dispatch; The QSE may telemeter the unit’s HSL=LSL in order for SCED to move the unit to LSL at normal ramp rate; then when at or below 110% of LSL, the QSE changes the unit status to “ONTEST” for shut-down. |
| Telemetry Issues that could affect SCED and/or LMPs |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR A Resource is generating more than their telemetered HSL; THEN: SCED will set the HDL=LDL=MW making the Resource undispatchable, Request the QSE to make corrections to their telemetry (Resource status, Resource limits, A/S responsibilities, etc) |
| Market Participant Over-ride | IF: Market Participant cannot fix the issue in a timely manner; THEN: Ask the Market Participant to over-ride the bad telemetry. |
| Market Participant unable to Override | IF: For some reason, the Market Participant cannot over-ride the bad telemetry; THEN Request the Shift Engineer to over-ride the bad telemetry, Manually run SCED, if needed. |

## 8.1	Responding to Market Participant Issues

Procedure Purpose:  Responding to Market Participant issues regarding website questions, SCED Deployments, LMPs, etc.

| Protocol Reference | 6.5.7.1.13(4) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 19, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Market Participant Backup Control Center Transfer |
| 1 | If notified by a QSE that they will be transferring to their backup control center, or from their backup to primary, Identify Market Participant and if they are a [QSE] or [TO] Send e-mail to 1 ERCOT System Operators Make log entry. |
| Market Participant Issues |
| 1 | If the MPs are not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |
| 2 | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |
| 3 | If the MPs are having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |
| 4 | As time permits, log and notify the Shift Supervisor of any actions taken and unresolved issues. |
| Missing Data from MIS Postings |
| 1 | IF: A call is received about data missing or data being incorrect, THEN: Transfer the call to the Help Desk, and Notify the Shift Engineer. |
| Log | Log the information. |
| Requests to Decommit Self-committed Resource in Operating Period |
| 1 | IF: A request is made by a QSE to decommit a self-committed Resource in the Operating Period; THEN: Transfer the call to the Resource Desk Operator. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step ReviewUpdated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts”Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |