## Power Operations Bulletin # 581

ERCOT has posted/revised the DC Tie Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-2.1 R1 | EOP-001-0 R4.1 | IRO-001-1.1 R3 | PER-001-0 R1 |
|  | TOP-001-1 R1 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 1, 2012 |
| --- | --- | --- |

- English shall be used as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System.

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator.

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, Regional Reliability Coordinator, and Interchange Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure security and reliability of the ERCOT system.

- The SO issues Dispatch Instructions for the Real-Time operation of Transmission Facilities to a TO, and to a QSE for the Real -Time operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT participants during system restoration activities.

- The SO shall ensure compliance with the ERCOT Protocols and Operating Guides on identified transfer limits.  The SO receives all specified notifications for the MPs with regard to energy transactions (Balanced Schedules), AGC control modes, routine adjustments, and equipment limitations or outages.

- The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide emergency energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s load frequency control system.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan that has been approved by the NERC Operating Committee.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 2.3	NXT Notification Requirements

Procedure Purpose:  To ensure the operator stays current using the system and to ensure system is tested.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Beginning of each Shift | - Log into the Taylor NXT Communicator Emergency Notification System (ENS) at the beginning of each shift, UNLESS: - TaylorENS is unavailable - Notified by Telecommunications/Help Desk/Shift Supervisor of maintenance, etc. - Testing Non-Routinely used Telecommunications - Refer to Desktop Guide Common to Multiple Desks Section 2.8, - Notify Help Desk immediately if unable to log into the NXT Communicator and request immediate assistance. |
| NXT Test | On the first weekend of each month, between the hours of 0800-2200: - Coordinate the actual test time with the Shift Supervisor, - Test NXT Communicator by activating the “SO ENS Test” scenario, - If any issues are found, open help ticket and cc: “shiftsupv”, - Make log entry. |

## 3.1	Approve E-Tags for the SPP DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-2 R1.2 | INT-005-2 R1 | INT-006-2 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | TOP-002-2 R5, R9 |  |  |

| Version: 1 | Revision: 11 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - AEP TOP located in Ohio is the DC Tie Operator (AEP DC TIE) for the DC_E (East tie) and DC_N (North tie) - If either DC Tie is over-scheduled, contact SPP Tariff (SPP Tariff) |
| NOTE | ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties. |
| NOTE | Per Protocol section 4.4.4.2 (2)(b), A QSE requesting the Oklaunion Exemption shall set up a separate QSE solely to schedule DC Tie exports under the exemption. See Desktop Guide DC Tie Desk Section 2.6. |
| 1 | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria used to automatically validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCO specified in the Physical Path IF: - Either of the above validations fail; THEN: - The E-Tag will be automatically denied. IF: - You feel an E-Tag failed validation erroneously; THEN: - Go to the list of approved ERCOT Registered QSE’s at the following website: http://www.ercot.com/mktparticipants/ - Select the “List of Market Participants in ERCOT Region”, - Select the DC Tie Scheduling List tab to view the ERCOT Registered QSEs. IF: - The QSE name is on the list but was denied by WebTrans; THEN: - Approve the E-Tag and inform the OATI help desk. WebTrans Reference Display: Validation > Tag Validation Monitor |
| 2 | When a New or Updated E-Tag is received in WebTrans system: Manually validate the following: - “ERCO” must not be listed as a PSE in Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard) or CD (central daylight) - “Transaction type” must be “Energy or Normal” - “ERCOT-E” or “ERCOT-N” must be selected for the correct POR (Point-of-Receipt) or POD (Point of Delivery) in the Physical Path - “CSWS” must be included as a Scheduling Entity on the SWPP TP row in the Physical Path. EXCEPT if “CSWS” is listed as the Generation Control Area (GCA) or Load Control Area (LCA) in the Physical Path. (Note: If CSWS is listed in both the TP and GCA or LCA, this will cause double counting in the Tie Operators net-scheduled value so the “before the start of the hour” check out will not match. These type tags should be denied) - There are no losses (MW) in the ERCOT Control Area. This would be either to or from SPP as shown on the “Energy and Transmission Profiles” section - Tags are permitted to be submitted within the COP time frame (up to seven days in advance), but a separate tag for each day must be submitted and the Start Time and Stop Time MUST NOT cross the midnight hour. IF: - Any of the above information is incorrect; THEN: - Deny the E-Tag, otherwise proceed below. IF: - One or more E-Tags are submitted that will cause the DC Tie to be overscheduled; THEN: - Contact SPP Tariff (SPP Tariff) approximately 30 minutes prior to the schedule start time to ensure they also see the over-schedule; they will take action to correct the over-schedule. If the correction is not in place by 20 minutes before the over-schedule will occur, ERCOT will curtail the E-Tag to zero (0) based on the criteria of “Last in – First out” until the over schedule is alleviated. IF: - ERCOT curtails an E-Tag due to an over-schedule that was not corrected in time; THEN: - Contact the source/sink control area to ensure the curtailment will be implemented as soon as possible. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| NOTE | If verification needs to be made in the current day HRUC will be used unless it is a current hour tag. If verification needs to be made for the next day DRUC will be used. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. OATI: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name. |

## 3.2	Import and Export Limits for the CFE DC Ties

Procedure Purpose: To confirm the import and export limits of the CFE DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Daily import and export limits for the Railroad and Eagle Pass DC Ties, and Laredo VFT will be provided by the Operations Engineering Support Group on the “Transmission Limits to Be Monitored” sheet. MIS Secure>GRID>Transmission>Generic Transmission Limits If the limits are not posted, notify the Operations Support Engineer. |
| 1 | Once the DC-Tie limits for next day are received, verify the sum of the E-Tags do NOT exceed the export limits on any DC-Tie. If so, contact the PSE of the last E-Tag received and request adjustments to be made. |
| 2 | When CFE has the ability to import additional energy into ERCOT, this could exceed the posted import limits. ERCOT has no issues with imported energy and these tags should be accepted. IF: - A tag is received that will exceed an import limit; THEN: - Accept the tag, - Notify the Operations Support Engineer to have the posted limit updated. |
| 3 | Coordinate with the ERCOT Transmission & Security Operator to ensure the import and export limits are updated in RTMONI hourly. EMS>EMP Applications>RTMONI Constraints Monitoring>Monitor Displays>Real Time Monitoring Groups Dir>DC_Ties |

## 3.7	DC-Tie Trips

Procedure Purpose: The process when DC-Ties trip.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | INT-004-2 R1 | INT-005-2 R1.1 | INT-010-1 R2 |  |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### CFE DC-Ties |  |
| 1 | IF: - Any of the CFE DC-Ties trip, THEN: - ERCOT will have the responsibility to curtail the E-Tags. - Curtail the E-Tags for the Tie that tripped (see Desktop Guide DC Tie Desk Section 2.3 or 2.4), AND - Instruct DC Tie Operator (AEP TO) to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] due to [DC-Tie name] tripped. Please notify CFE. Please repeat this back to me. That is correct. Thank You.” |
| 2 | Once the DC-Tie that tripped is operational, re-load the curtailed E-Tag(s), if applicable: - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Instruct DC Tie Operator (AEP TO) to make notification to CFE to approve re-loads. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. ERCOT has re-loaded curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name]. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank You” |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TO) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| ### SPP DC-TIES |  |
| 1 | IF: - Any of the SPP DC-Ties trip, THEN: - SPP has the responsibility to curtail the E-Tags. |

## 4.1	ERCOT Declares EEA 1

Procedure Purpose: Steps to perform when ERCOT declares an Energy Emergency Alert (EEA) 1.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |
|  | IRO-006-5 R1, R4 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE DC-Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP Tariff), page 2 - The DC Tie operator for the SPP DC-Ties can be reached using the Turret phone button labeled (AEP DC TIE), page 19 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to and from SPP. They can be reached using the Turret phone button labeled (AEP QSE), page 4 - AEP Tenaska is the generation dispatcher that a VDI for emergency energy is issued to and from CFE. They can be reached using the Turret phone button labeled (AEP TENASKA QSE), page 4 |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC-Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC-Ties. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. |
| Comision Federal de Electricidad (CFE) |  |
| 1a | IF: - There are export schedules on any CFE DC-Tie; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | IF: - There is export inadvertent payback flowing to CFE; THEN: - Stop inadvertent payback by contacting the DC-Tie Operator (AEP TO) Typical Script to DC Tie Operator (AEP TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC-Tie] be ramped to zero. Please notify CFE.” |
| 3a | Contact DC-Tie Operator (AEP TO) and request them to contact CFE to inquire about the availability of emergency energy on all available CFE DC-Ties. IF: - Emergency energy is available; THEN: - Request the DC-Tie Operator to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP Tenaska (AEP TENASKA QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP Tenaska (AEP TENASKA QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| 4a | IF: - CFE can not supply ERCOT with emergency energy; THEN: - Make log entry with information. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1”. |
| 2b | IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide DC Tie Desk Secion 2.3 or 2.4) Typical script to DC Tie Operator (AEP DC TIE): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag (see Desktop Guide DC Tie Desk Section 2.5) - Notify the Shift Supervisor |
| 3b | IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DC TIE). Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1 and is requesting the inadvertent payback on [name DC-Tie] go to zero.” |
| 4b | IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC-Tie Operator (AEP DC TIE) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | IF: - The SPP DC-Ties are not at maximum import into ERCOT; THEN: - Notify the SPP Tariff desk (SPP Tariff) to determine the availability of transmission service for an EEA 1 schedule. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie to start a schedule into ERCOT?” IF: - No current hour transmission service is available; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor IF: - Status changes from EEA 1 to EEA 2 or 3; THEN: - Proceed to Section 4.2 |
| 6b | IF: - Transmission service is available; THEN: - Notify AEP QSE (AEP QSE): Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” IF: - No available capacity; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor. IF: - Capacity is available; THEN: - Request AEP QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you” NOTIFY: - DC Tie Operator (AEP DC TIE): Typical Script for DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and the E-Tag (s) for an EEA 1 schedule. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency into ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 1 to EEA 2. Thank you”. If moved to EEA 2 or 3 proceed to section 4.2, ERCOT Declares EEA 2 or 3. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all actions taken. |

## 4.2	ERCOT Declares EEA 2 or 3

Procedure Purpose: Steps to secure emergency energy across the DC tie(s) in an Energy Emergency Alert (EEA) 2 or 3.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0 R1, R3.1, R4.2, R7.2 | EOP-002-2.1 R1, R2, R4, R6.4, R6.6 | INT-010-1 R3 | IRO-005-2 R4, R10 |
|  | IRO-006-5 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE ties can be reached using the Turret phone button labeled (AEP TO), page 4 - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP Tariff), page 2 - The DC Tie operator for the SPP DC Ties can be reached using the Turret phone button labeled (AEP DC TIE), page 19 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to and from SPP. They can be reached using the Turret phone button labeled (AEP QSE), page 4 - AEP Tenaska is the generation dispatcher that a VDI for emergency energy is issued to and from CFE. They can be reached using the Turret phone button labeled (AEP TENASKA QSE), page 4 |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC-Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC-Ties. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| EEA | When notified by Hotline that ERCOT has declared EEA 2 or 3, proceed with this procedure. |
| Comision Federal de Electricidad (CFE) |  |
| 1a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There are export schedules on any CFE DC-Tie; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback flowing to CFE; THEN: - Stop inadvertent payback by contacting the DC-Tie Operator (AEP TO) Typical Script to DC Tie Operator (AEP TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC-Tie] be ramped to zero. Please notify CFE.” |
| 3a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. Contact DC-Tie Operator (AEP TO) and request them to contact CFE to inquire about the availability of emergency energy on all available CFE DC-Ties. IF: - Emergency energy is available; THEN: - Request the DC-Tie Operator to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP Tenaska (AEP TENASKA QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP Tenaska (AEP TENASKA QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| 4a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - CFE can not supply ERCOT with emergency energy; THEN: - Make log entry with information. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Thank you.” |
| 2b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide DC Tie Section 2.3 or 2.4). Typical script to DC Tie Operator (AEP DC TIE): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag, - Notify the Shift Supervisor. |
| 3b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DC TIE). Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3] and is requesting the inadvertent payback on [name DC-Tie] go to zero.” |
| 4b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC-Tie Operator (AEP DC TIE) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | Complete this step if in EEA 1 there was no non-firm transmission service available or EEA 1 was skipped. Notify the SPP Tariff desk (SPP Tariff) to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” IF: - No emergency transmission service is available, THEN: - Do NOT proceed and make log entry. - Notify Shift Supervisor |
| 6b | IF: - Emergency transmission service is available; THEN: - Request emergency energy from AEP QSE (AEP QSE) Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” IF: - No available capacity, THEN: - Do NOT proceed and make log entry. IF: - Capacity is available; THEN: - Request AEP QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you.” NOTIFY: - DC Tie Operator (AEP DC TIE): Typical Script for DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and the E-Tag (s) for emergency energy into ERCOT. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 2 to EEA 3. Thank you”. IF EEA 1 has ended continue with this procedure. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC); Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide DC Tie Secion 2.5), - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all action taken |

## 4.3	Emergency Energy to CFE

Procedure Purpose: Provide Emergency Energy to CFE across the DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R1 | INT-010-1 R3 |  |  |

| Version: 1 | Revision: 8 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If CFE requests the emergency energy, no emergency notification needs to be declared by ERCOT. |
| 1 | IF: - Notified by the ERCOT Transmission Operator or the DC Tie Operator (AEP TO) of CFEs emergency situation; THEN: - Identify if CFE has export schedule(s) that can be curtailed, if CFE has no exports, proceed to step 2, - Curtail the appropriate E-Tag(s) (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact the DC Tie Operator (AEP TO) when curtailment is complete and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to CFEs emergency situation. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | IF: - CFE has export inadvertent payback flowing into ERCOT; THEN: - Notify DC Tie Operator (AEP TO) to stop inadvertent payback Typical Script to DC Tie Operator (AEP TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting the inadvertent payback being imported to ERCOT on [name DC-Tie] go to zero due to CFEs emergency situation. Please repeat this back to me. That is correct. Thank you.” |
| 3 | IF: - Notified by the ERCOT Transmission Operator or the DC Tie Operator (AEP TO) that CFE is requesting emergency energy; THEN: - Verify with the ERCOT Transmission Operator that sending emergency energy to CFE would not put ERCOT in an insecure state, IF: - ERCOT is able to send CFE emergency energy; THEN: - Request the DC-Tie Operator (AEP TO) to ramp the appropriate DC-Tie with the amount of emergency energy that ERCOT is able to send, Typical script to DC-Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT will send [amount] of emergency energy on [DC-Tie(s)] Please ramp Ties accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” - Notify Shift Supervisor - Issue AEP Tenaska (AEP TENASKA QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to CFE” and which DC-Ties in “Other Information” - End time will be the same as initiation time. - Notify AEP Tenaska (AEP TENASKA QSE) to acknowledge the VDI. |
| 4 | WHEN: - Notified that CFEs emergency has ended; THEN: - Perform/verify the following: - End Emergency Energy, if appropriate - Re-load E-Tag(s), if appropriate (see Desktop Guide DC Tie Section 2.5) - Restart import inadvertent payback, if appropriate |
| Log | Log all actions taken. |

## 4.5	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose: The process to curtail E-Tags for the CFE Ties and request emergency energy if needed.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001 R3.1, R4.2 | INT-004-2 R1 | INT-005-2 R1.1 | INT-010-1 R2 |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific amount, only CFE needs to approve the change. Curtailments will be automatically approved by them. |
| ### Transmission Issues within ERCOT |  |
| 1 | Due to ERCOT transmission issues it may be necessary to curtail export E-Tags using the Last-in-First-Out (LIFO). IF: - Notified by the ERCOT Transmission Operator of the need to curtail exports on a specific DC-Tie; THEN: - Verify if the E-tag needs to be curtailed immediately or if at least a 30 minute notice can be given, - Verify the MW amount the E-tag needs to be curtailed to; IF: - Curtailment needs to take place immediately, proceed with this step. If at least 30 minutes can be given proceed to step 2. THEN: - Verify with ERCOT Transmission Operator that a Transmission Watch or Emergency has been declared, - Curtail the appropriate E-Tag (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE - Contact PSE with curtailment information. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] starting at [xx:xx] due to transmission issues within ERCOT. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | IF: - At least a 30 minute notice can be given (Issuance of Watch/Emergency is not needed), THEN: - Curtail the appropriate E-Tag, - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE - Contract PSE with curtailment information. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC-Tie name] starting at [xx:xx] due to transmission issues within ERCOT. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank You” . |
| 3 | Once notified by the ERCOT Transmission Operator that the transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Section 2.5), - Ensure DC Tie Operator (AEP TO) sees the re-loaded E-Tags, and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx], the transmission issues within ERCOT have been resolved and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CFE to approve re-loads. Please repeat this back to me. That is correct. Thank you.” |
| 4 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TO) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 5 | IF: - Notified by the ERCOT Transmission Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.1 ERCOT Declares EEA 1. |
| LOG | Log all actions taken. |
| ### Transmission Issues within CFE |  |
| 1 | Due to CFE transmission issues it may be necessary to curtail import E-Tag(s) for them. IF: - Notified by the ERCOT Transmission Operator or the DC Tie Operator (AEP TO) of the need to curtail imports on specific CFE DC-Ties; THEN: - Verify the amount and time of the curtailment - Curtail the appropriate E-Tag (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact the DC Tie Operator (AEP TO) when curtailment is complete and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag [tag number] on the [DC tie name] due to transmission issues within CFE. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified that transmission issues are resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Ensure DC Tie Operator (AEP TO) sees the re-loaded E-Tags, and instruct them to make notification to CFE. |
| 3 | IF: - The re-loaded E-Tag goes passive deny because CFE did not approve the E-Tag in the allotted time; THEN: - Re-load the E-Tag again, - Call the DC Tie Operator (AEP TO) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.3, Emergency Energy to CFE. |
| LOG | Log all actions taken. |

## 4.8	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 8 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - When cold weather is 5 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region - When severe cold weather is 5 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### ADVISORY |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When cold weather is 3 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 3 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### WATCH |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect System Reliability. - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When cold weather is 1 day away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 1 day away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones or when temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT varies from time-line for DAM/DRUC. |
| ### EMERGENCY NOTICE |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED). - When cold or severe cold weather is in the ERCOT Region and it is beginning to have an adverse impact on the ERCOT System. |
| ### Notifications |  |
| HOTLINE | Notify QSEs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| POST | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the only option is “public” - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| LOG | Make log entry. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 - / 1 - / 2 - / 2 - / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 - / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |
| 2.3 3.1 3.2 3.3 3.6 3.7 3.8 3.9 3.11 4.1 4.2 4.3 4.5 4.6 4.8 | 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 7 1.0 / 4 1.0 / 6 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated step “Beginning of each Shift” Updated 1st note Updated steps 1, 2 & 3 Updated 1st, 4th note and step 1 Updated step 1 “Imports” and step 2 “Exports” Updated Steps 1, 2 and 4 in “CFE DC-Ties” Updated 2nd note and steps 1-3 Updated steps 1-3 Updated steps 1 and 2 Updated all steps Updated all steps Updated all steps Updated all steps Removed reference of Austin Control Room Added projected reserve capacity shortage and Extreme Hot Weather in Watch | September 1, 2011 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 6 1.0 / 7 | Updated step 2 Updated step 1 Updated Turret Phone, step 3a in Comision Federal de Electricidad (CFE) and step 5b to implement NPRR 379 Updated Turret Phone and step 3a in Comision Federal de Electricidad (CFE) Updated step 3 | October 1, 2011 |
| 4.6 | 1.0 / 7 | Updated step TO Hotline Call | November 1, 2011 |
| 3.1 3.3 4.6 4.8 | - / 9 1.0 / 9 1.0 / 8 1.0 / 7 | Updated step 2 Updated step 1 Added new section and updated all steps Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.3 4.6 | 1.0 / 1 1.0 / 10 1.0 / 10 1.0 / 9 | Updated Scope Updated step 2 Updated step 1 Updated Hotline call scripts | January 19, 2012 |
| 2.1 2.3 3.1 3.2 3.7 4.1 4.2 4.3 4.5 4.8 | 1.0 / 1 1.0 / 4 1.0 / 11 1.0 / 5 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 7 1.0 / 8 | Added dispatch instructions paragraph Updated Desktop Guide reference Added 3rd Note Changed Shift Engineer to Operations Support Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 2nd Note & all steps 1 – 3 Updated step 1 of Watch | March 1, 2012 |