## Power Operations Bulletin # 582

ERCOT has posted/revised the Real Time Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1	System Operator Responsibility and Authority

Procedure Purpose:  To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.11 | 6.5.1.2(3) | 6.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-2.1 R1 | EOP-001-0 R4.1 | IRO-001-1.1 R3 | PER-001-0 R1 |
|  | TOP-001-1 R1 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 1, 2012 |
| --- | --- | --- |

- English shall be used as the language for all communications between and among Operating Personnel responsible for the Real-Time Generation control and operation of the interconnected Bulk Electric System.

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include the shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator.

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, Regional Reliability Coordinator, and Interchange Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure the Security and Reliability of the ERCOT System.

- The SO issues Dispatch Instructions for the Real-Time Operation of Transmission Facilities to a TO, and to a QSE for the Real-Time Operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT Participants during system restoration activities.

- The SO shall consider all equipment operating limits when issuing Dispatch Instructions except as stated in Protocol Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TSP, a DSP, or a Generation Resources QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

- The SO performs security analyses on a Day Ahead and Real-Time basis and ensure that all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines necessary to maintain safe and reliable operating conditions on the ERCOT System in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s Load Frequency Control System.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan which has been approved by the NERC Operating Committee.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.3.2(2) | 6.5.7.6.2.2 | 6.5.9.1(1)(b) | 8.2 (2)(b)(vii) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.3.1.2 |  |  |  |
| NERC Standard | BAL-002-0 R2.4, R6 | BAL-005-0.b R8 | BAL-007 (Field Trial) | EOP-002-2.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 595.8 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -595.8 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, - Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) |
| Base Point Deviation | IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) - If unit trip: - Time of unit trip, - Name of unit, - Approximate net MW on unit, - Approximate lowest frequency, - Amount of RRS deployed (if any), AND - Approximate ERCOT load. |
| Automatic SCED Runs | LFC triggers automatically when one of the following occurs: - Frequency reaches 59.91 Hz or below, SCED runs within a minute of LFC trigger - If frequency stays below 59.95 for more than 50 seconds, LFC triggers SCED to run |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: - QSE will request VDI(s) - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time - A VDI will be needed for each Resource IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per deployment for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - Manually run SCED IF: - Frequency goes above 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, - Enter manual offset (the offset will continue until removed). IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 10 MINUTES | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Shift Engineer to send an event notification to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.75 Hz - Load Resource providing RRS – 59.7 Hz |
| Monitor/ Deploy | IF: - Frequency drops below 59.95 Hz, AND - Regulation Up service remains and is deploying; THEN: - Manually run SCED (do not run SCED more than once between SCED runs) IF: - Frequency drops below 59.95 Hz, AND - Out of Up Regulation; THEN: - Check the GTBD_TO_HDL on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset - If using OpsMon Dashboard, do not enter an offset > than GTBD_TO_HDL - If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - GTBD_TO_HDL on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS does not have adequate up room; THEN: - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the “Manual RRS” to activate box, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - If room is available - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the “Manual RRS” to activate box, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. - Notify the Shift Supervisor of the need to possibly commit additional Resources. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available - Manually run SCED, - Log the event and notify Shift Engineer to send notification of the event to BAALfieldtrials@ercot.com and Shift Supervisor to complete a Texas RE Event form. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is availableManually run SCED. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED. |
| Stable | IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Austin) |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Contact the Help Desk. |

## 4.1	Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved and that the solution is reasonable.

| Protocol Reference | 3.8.3 | 6.3.2(2) | 6.5.7.1.13(3) | 6.5.7.6.2.1(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.7.6.2.2 | 6.5.7.6.2.1(1) | 6.5.7.6.2.1(4) | 6.5.1.1(b) |
|  | 6.5.5.2(6) | 6.5.7.6.2.3 | 6.5.9.1(2) |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Workflow Controller Messages |  |
| NOTE | The SCED Workflow Controller provides three color coded messages as indicated in the following: - GREEN – Informational (i) and Success (s) - BLUE – Warning (w) - RED – Error (e) and Fatal Error (f) |
| 1 | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages Monitor SCED Workflow Controller logs for “Warning” and “Error” messages. |
| 2 | IF: - The log indicates an “Error” or “Fatal Error”; THEN: - Contact the Help Desk and notify all Control Room staff, - Attempt to resolve the issue, refer to Desktop Guide Real Time Desk Section 2.5, - Refer to Section 3.2 “Managing SCED Failures” in this procedure. |
| ### SCED Solution Time Parameter |  |
| NOTE | Typically SCED should produce a solution within 20 seconds. It is highly desirable to have at least 3 executions of SCED in any 15 minute period. |
| Automatic Trigger | Verify that SCED is automatically triggered: - Periodically every 5 minutes - About 60 seconds after RRS is automatically deployed by LFC IF: - SCED is not automatically executed (but has not failed); THEN: - Manually execute SCED, - Immediately notify the Shift Supervisor and Shift Engineer, - Continue to manually execute SCED approximately every 5 minutes until the condition is corrected. |
| Manual Trigger | SCED may be manually triggered when the following is identified: - Frequency deviates +/-0.05 Hz for more than 5 minutes - Generation Resource trips and Frequency is > 59.91 Hz - When approximately 50% of Regulation has been deployed - Approximately 60 seconds after Generation Resources providing RRS have been deployed. - As frequently as needed after Load Resources providing RRS have been deployed. |
| LOG | Log all actions taken as necessary. |
| ### Large Resource Trips or Runbacks |  |
| 1 | IF: - A QSE has the loss of any Resource greater than 200 MW; THEN: - Review the following: - Ensure their telemetry reflects the trip, - Manually deploy SCED if needed, - Determine the impact on (HASL-GEN), - Notify Control Room staff of all actions taken - Log the event. |
| NOTE | See Section 3.1, Frequency Control Operating Procedure. |
| ### Quick Start Generation Resource |  |
| QSGR | A Generation Resource that in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test that establishes an amount of capacity that can be deployed within a ten minute period. |
| COP | The QSE for a QSGR that is available for deployment by SCED shall set the COP Resource Status ON, the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spin, then the A/S Resource Responsibility for Non-Spin shall be set to the Resource’s Non-Spin responsibility in the COP. If the Resource’s Non-Spin responsibility is greater than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP LSL to zero. |
| Telemeter | The QSGR that is available for deployment by SCED shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR that is providing Off-Line Non-Spin shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED. A QSGR with a telemeter breaker status of open and a telemeter Resource Status of ON shall not provide Regulation or Responsive Reserve Service. |
| QSGR Qualification Test | WHEN: - Conducting a QSGR qualification test for Operations Analysis; THEN: - Issue a VDI - Choose “OTHER_RES” as the Instruction Type from Resource level - Enter “QSGR Qualification Test” in “Other Information” |
| ### Generation Resource Shut-down/Start-up Process |  |
| NOTE | ERCOT’s preferred methodology for moving a generator output down to a state suitable for de-synchronization: - All A/S Responsibility assigned to the Resource must first be moved to other Generation Resources, - Generation Resources are expected to be on normal SCED control until reaching no greater than 110% of the units normal LSL before changing status to “ONTEST”. This can be accomplished by the QSE doing one of the following: - Allow SCED to move the unit down to LSL by normal dispatch; - The QSE may telemeter the unit’s HSL=LSL in order for SCED to move the unit to LSL at normal ramp rate; then when at or below 110% of LSL, the QSE changes the unit status to “ONTEST” for shut-down. |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to their telemetry (Resource status, Resource limits, A/S responsibilities, etc) |
| QSE Override | IF: - The QSE cannot fix the issue in a timely manner; THEN: - Ask the Market Participant to over-ride the bad telemetry. |
| QSE unable to Override | IF: - For some reason, the QSE cannot override the bad telemetry; THEN - Request the Shift Engineer to override the bad telemetry, - Manually run SCED, if needed. |

## 5.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 9 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a Projected Reserve Capacity Shortage that could affect System Reliability and may require more Resources. - When cold weather is 5 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region - When severe cold weather is 5 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region - When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Unplanned Transmission Outages that may impact System Reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse Reliability impacts and Contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When cold weather is 3 days away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones in the ERCOT Region. - When severe cold weather is 3 days away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones in the ERCOT Region. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term Operating Reliability. - In such circumstances ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market (DAM) in accordance with ERCOT Procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission System conditions are such that operations within first contingency criteria are not likely or possible due to Forced Outages or other conditions. - Loss of communications or a control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from the Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect System Reliability. - When an approaching Hurricane / Tropical Storm is approximately 1 day away. - When cold weather is 1 day away when temperatures are forecasted to be in between 20°F and 26°F and the maximum temperature is expected to remain 32°F or below in three or more Weather Zones. - When severe cold weather is 1 day away and when temperatures are forecasted to remain between 20°F and 26°F or below in five or more Weather Zones. - When temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones or when temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). - A Transmission condition has been identified that requires Emergency Energy from any of the CFE DC-Ties. - Conditions have developed that require additional Ancillary Services in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based Congestion Management techniques embedded in SCED will not be adequate to resolve Transmission Violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require Operations with active Transmission Violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the Reliability of the ERCOT System. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. - ERCOT varies from time-line for DAM/DRUC. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum Reliability Standards during the Operating Period utilizing every Resource practically obtainable from the Market - ERCOT forecasts an inability to meet applicable Reliability Standards and has exercised all other reasonable options - A Transmission condition has been identified causing unreliable Operation or overloaded elements - A Single Severe Contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements for which no practicable Resource solution exists - ERCOT has determined a fuel shortage exists that would affect Reliability - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED) - When cold or severe cold weather is in the ERCOT Region and it is beginning to have an adverse impact on the ERCOT System. |
| ### Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify QSEs: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public utilizing Notice Builder. - For “free form” messages, the “Notice Priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Log all actions taken. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| ### Version: 1 | Revision: 7 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls < 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls < 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA. When a media appeal for voluntary energy conservation is enacted, QSEs should be notified via Hotline call (see EEA 2 for typical script). - Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore Reliability. - QSEs need to contact the Texas Commission on Environmental Quality (TCEQ) for enforcement discretion on air permitting requirements. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Select the activate EEA flag in EMS, - Using the Hotline, notify all QSEs to implement EEA 1. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is declaring EEA 1, QSEs are to perform their necessary steps for EEA 1. Report to ERCOT any loss of generation or issues, and ERCOT is reminding you that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | IF: - Generation Resource (that are not bid in for Non-Spin) have a unit status of OFF and can be brought On-line within the timeframe of the emergency; THEN: - Issue a VDI to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) |
| 3 | IF: - A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: - Issue a VDI to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) |
| 4 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 60.00Hz; THEN: - Determine whether system conditions require the deployment of Load Resources and/or EILS by considering the following: - If at peak hour, will the EILS be sufficient and have they already been deployed in the current contract period. - If not at peak hour, will half of Load Resources be sufficient - PRC < 1750 MW, deploy Group 1 (as system conditions require, deploy remaining Load Resources). - PRC < 1375 MW, deploy both Groups 1 and 2 simultaneously. - Using the Hotline, notify all QSEs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. |
| Load Resources | IF: - Deploying Load Resources, the Resource Operator must complete the XML deployment of the Load Resources before the Hotline call is made. - PRC < 1750 MW, deploy Group 1 - PRC < 1375 MW, deploy both Groups 1 and 2 simultaneously Typical Script for one Group: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2 and has deployed Group 1 Load Resources. Implement all measures associated with EEA 1, if not already implemented. [QSE] please repeat this back to me. That is correct, thank you” Typical Script for both Groups: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2 and has deployed all Load Resources. Implement all measures associated with EEA 1, if not already implemented. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| EILS | IF: - Deploying EILS, deploy all EILS Loads as a single block. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2. ERCOT is directing QSEs to deploy all contracted EILS in the current time period until further notice. Implement all measures associated with EEA 1 if not already implemented. [QSE] please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| When EILS Business Hours Change | IF: - EILS are deployed, and additional EILS Loads that are available due to business hour changes THEN: - Deploy the next business hour, if needed Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA 2. ERCOT is directing QSEs to deploy all contracted EILS in the current time period until further notice. All previously deployed EILS are to remain deployed until recalled. [QSE] please repeat this back to me. That is correct, thank you”. |
| NOTE | - EILS can only be deployed twice during a contract period with a maximum of 8 hours of deployment per contract period. - Contract Periods: - June – September - October – January - February – May For current deployment data, refer to the Real Time Values Spreadsheet “EILS Tab” |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Typical Script: “This is ERCOT Operator [first and last name]; ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Using the Hotline, notify all QSEs to implement EEA 3 and any measures associated with EEA 1 and 2, if not already implemented. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3, [MW Amount] of firm load is being shed. Implement all measures associated with EEA 1 and 2, if not already implemented. [QSE] please repeat this back to me. That is correct, thank you” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 7.1	Monthly Testing of Satellite Phones

Procedure Purpose:  To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001 R2 | EOP-005 R5 |  |  |

| Version: 1 | Revision: 2 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with the TOs. As the Shift Supervisor makes the call to the individual TO, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TO. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7) for a list of the TOs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Conference Bridge are Desk specific. Select: SATELLITE directory or go to page 35 to view the programmed numbers on the Turret Phone for each Bridge: - BLACKSTRT RUC – RUC Desk - BLACKSTRT RES – Resource Desk - BLACKSTRT REAL – Real-Time Desk - BLACKSTRT TS#1 – Transmission Desk - BLACKSTRT TS#2 – Transmission Desk (Island Coordination) |
| 1 | IF: - The pre-programmed number does not function correctly, THEN: - Refer to the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7.2) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the QSEs fail to connect to the Bridge call, THEN: - Investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the QSEs that were unable to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| Log | Log the results in the Operations Log. |
| ### Alternate Control Center |  |
| 1 | When working out of the Alternate Control Center during the monthly scheduled dates: - Test the Turret Satellite Phone on each desk. |
| 2 | Inform the Shift Supervisor when testing has been completed and identify any issues encountered. |
| Log | Log the results in the Operations Log. |

## 8.1	Responding to Market Participant Issues

Procedure Purpose:  Responding to Market Participant issues regarding website questions, SCED Deployments, LMPs, etc.

| Protocol Reference | 6.5.7.1.13(4) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Backup/Alternate Control Center Transfer |  |
| 1 | When notified by a QSE that they will be transferring to or from their backup/alternate control center, - Identify the [QSE] in the email notification - Send e-mail to “1 ERCOT System Operators” - Make log entry. |
| ### QSE Issues |  |
| 1 | If a QSE is not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |
| 2 | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |
| 3 | If a QSE is having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |
| 4 | As time permits, log and notify the Shift Supervisor of any actions taken and unresolved issues. |
| ### Missing Data from MIS Postings |  |
| 1 | IF: - A call is received about data missing or data being incorrect, THEN: - Transfer the call to the Help Desk, and - Notify the Shift Supervisor and Shift Engineer. |
| Log | Log the information. |
| ### Requests to Decommit Self-committed Resource in Operating Period |  |
| 1 | IF: - A request is made by a QSE to decommit a self-committed Resource in the Operating Period; THEN: - Transfer the call to the Resource Desk Operator. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Transfer call to the ERCOT Transmission Operator. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step ReviewUpdated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts”Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 4.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |