## Power Operations Bulletin # 590

ERCOT has posted/revised the Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-2.1 R1 | IRO-001-1.1 R3 | PER-001-0 R1 | TOP-001-1 R1 |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

- English shall be used as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System.

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include the shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator.

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, Regional Reliability Coordinator, and Interchange Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure the Security and Reliability of the ERCOT System.

- The SO issues Dispatch Instructions for the Real-Time Operation of Transmission Facilities to a TO, and to a QSE for the Real-Time Operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT Participants during system restoration activities.

- The SO shall consider all equipment operating limits when issuing Dispatch Instructions except as stated in Protocol Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TO or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

- The SO performs security analyses on a Day Ahead and Real-Time basis and ensures that all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide Emergency Energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCN’s, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines necessary to maintain safe and reliable operating conditions on the ERCOT System in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s Load Frequency Control System.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan which has been approved by the NERC Operating Committee.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 3.1	Compliance Monitoring

Procedure Purpose: To monitor QSE performance

| Protocol Reference | 3.9.1(7) & (8) | 6.3.2(2) | 6.4.2.5 (2) | 6.4.2.5(3)(b) |
| --- | --- | --- | --- | --- |
|  | 6.4.8.1(1) | 6.5.7.5(2) | 6.5.9(3) | 8.1.1.3(3) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### Monitor Resource Status for Discrepancies |  |  |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instructions under normal conditions and Emergency Conditions. During Emergency Conditions, ERCOT may verbally request QSEs to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |  |
| Monitor COP | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>COP Monitor Periodically: - Review the COP changes utilizing the Date/Time of Submission column as a reference; IF: - A QSE has changed a resource status code, resource parameter, or ancillary service on a specific resource; THEN: - Review the change in the COP Monitor, AND - Notify the QSE representing the resource if the change is unacceptable to ERCOT. |  |
| Telemetered Status | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>Market Operator Data>Consistency Checks IF: - Discrepancy is identified between a COP and telemetered Resource Status; THEN: - Call the QSE representing Resource to determine the correct resource status and have them make the necessary correction. NOTE: It is not necessary to make calls for inconsistent telemetry/COP for quick start units. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data>Unit Tab WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL - ; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) WHEN: - A Resource is generating above its HASL; THEN: - SCED will set HDL=LDL=MW-5*Down Ramp Rate - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) |  |
| ON TEST | - If the ONTEST Resource Status Code is used to indicate that a Generation Resource is performing a test, the QSE should notify ERCOT by 1800 in the Day-Ahead, - Review the list of approved Resources to be ONTEST, - ONTEST can be used by the QSE when in the start-up and shut-down mode. |  |
| Control Block Up/Down | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details>Unit tab - Control Block Current UP/DN are telemetry points that a QSE can use in emergency situations to communicate that a resources ability to adjust its output has been unexpectedly impaired. - If a QSE has a Control Block set for greater than 5 minutes, the system will set the corresponding (UP/DN) Too Long flag to indicate this to the operator. |  |
| ### Manual Override Checks |  |  |
| 1 | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL and LDL Periodically: - Review the Manual HDL and LDL overrides to ensure they are still needed. IF: - Override exists; THEN: - Coordinate with the Transmission Operator to determine if override is still needed. |  |
| ### Dynamically Scheduled Resource |  |  |
| NOTE | Each QSE may not have more than one DSR Load. |  |
| DSR | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Analyst Displays>Gen Monitoring Displays>Dynamic Schedules>Load Based IF: - A DSR load signal fails for any reason for > than one 15 minute Settlement Interval; THEN: - Notify the QSE and notify the Helpdesk to suspend validation of DSR Output Schedule. IF: - A DSR load signal fails for more than 10 consecutive hours; THEN: - Notify the Helpdesk to have DSR suspended until the signal is reliably restored. |  |
| NOTE | IF: - The signal failure is identified to be an ERCOT communication problem; THEN: - ERCOT will not suspend the QSE’s ability to use DSR. |  |
| ### Monitor QSE Ancillary Services Obligation |  |  |
| Real-Time RRS A/S Shortage |  | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Ancillary Service Monitoring Summary Check at least once an hour, however we are waiting on a display enhancement to make this process manageable: - Click on Responsive Reserve QSE Detail to see which QSEs are short, however clicking on Unit details and Load details will give you the detailed information - Filter on Limit Violation (check marks indicate there is a shortage) WHEN: - A QSE shows a Real-Time A/S shortage; NOTIFY: - The QSE of their RRS shortage; THEN: - Within ten minutes, the QSE must: - Correct the telemetered A/S Resource Responsibility to provide sufficient capacity, OR - Provide both appropriate justification for not satisfying their A/S Obligation AND a plan to correct the shortfall that is acceptable. IF: - The QSE is unable to replace their A/S Obligation; THEN: - Notify the Shift Supervisor and determine if A/S shortage amount and reliability need is sufficient enough for ERCOT to replace from existing offers. |
| A/S Difference in COP |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Participation>Physical Market>SASM Market>Failure To Provide Check approximately 5 minutes after each hour: IF: - A/S Difference (MW) column displays negative values in RED; THEN: - Verify that the Notification Flag column displays a “Y”, - Navigate to the Failure To Provide display and call the QSE with a Failure MW, IF: - The QSE states they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened. IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Failure To Provide Desktop Guide Resource Desk Section 2.8.2. |
| Infeasible A/S Capacity from RUC |  | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market> AS Replacement Check after each HRUC has been published or when RUC operator has notified you of a RUC commitment. NOTE: The infeasible hour indicates the shortage based on the system situation when HRUC runs. Therefore, it may be necessary to review at least 3 hours prior to infeasible hour to notify QSE. IF: - The Infeasible MW column is displaying MW values; THEN: - Assess the infeasible MW and hour based on the SASM timeline - Change the Notification Flag to “Y” and commit to database, - Press the “Send Notification”, - Navigate to the AS Replacement display and call the QSE with the Infeasible MW. IF: - The QSE states they cannot replace the service within two hours; THEN: - Notify the Shift Supervisor and determine if a SASM should be opened; IF: - It is determined that a SASM should be opened; THEN: - Proceed to the SASM>Running a SASM for Undeliverable Desktop Guide Resource Guide Section 2.8.1. |
| NOTE |  | A QSE that has one or more of its Resources RUC-committed to provide Ancillary Services must increase its Ancillary Service Supply Responsibility by the total amount of RUC-committed Ancillary Service quantities. The QSE may only use a RUC-committed Resource to meet its Ancillary Service Supply Responsibility during that Resource’s RUC-Committed Interval if the Resource has been committed by the RUC process to provide Ancillary Service. The QSE shall indicate the exact amount and type of Ancillary Service for which it was committed as the Resource’s Ancillary Service Resource Responsibility and Ancillary Services Schedule for the RUC-Committed Intervals for both telemetry and COP information provided to ERCOT. Upon deployment of the Ancillary Services, the QSE shall adjust its Ancillary Services Schedule to reflect the amounts requested in the deployment. |

## 3.5	System Failures

Procedure Purpose: To ensure Market Participants are notified via MIS Public using Notice Builder of any SCED/RLC/LFC(AGC) failures.

| Protocol Reference | 6.5.9.2 | 6.5.9.1(2) | 6.5.9.2(3) | 6.5.9.2(4) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | WHEN: - Notified by the Real-Time Operator of a SCED/RLC/LFC(AGC) failure; THEN: - Post the following message on MIS Public using Notice Builder: Typical MIS posting: “ERCOT has issued an Emergency Notice due to the failure of [SCED/RLC Failure], and/or [LFC].” |
| 2 | WHEN: - Notified by the Real-Time Operator that SCED/RLC/LFC(AGC) has been restored; THEN: - Cancel message on MIS Public using Notice Builder. |
| Log | Make log entry of actions taken. |

## 3.6	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service and/or Load Resources for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R2, R4.2 | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 |
|  | IRO-004 R3 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006 R1, R4 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 8 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Deploy Non-Spin & Post | WHEN: - Notified by the Transmission Operator to deploy Non-Spin in the Houston area for the North-Houston Interface; THEN: - Deploy Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) (Refer to Desktop Guide Resource Desk Section 2.2) - Post on MIS Public using Notice Builder. Typical MIS posting: “ERCOT is issuing a Watch for the North to Houston interface and deploying Non-Spin Reserve to specific resources”. |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| Deploy Load Resources & Post | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Deploy Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by XML (Refer to Desktop Guide Resource Desk Section 2.1) - Post on MIS Public using Notice Builder. Typical MIS posting: “ERCOT is issuing an Emergency Notice for the North to Houston interface and deploying specific Load Resources”. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Recall Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.1) - Cancel message on MIS Public using Notice Builder. |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Recall Non-Spin in the Houston area (Coast Weath Zone WZ_COAST) by sending a Zero MW XML, (Refer to Desktop Guide Resource Desk Section 2.2) - Cancel message on MIS Public using Notice Builder. |
| Log | Log the actions taken. |

## 3.7	Deploying Non-Spin for Local Congestion

Procedure Purpose:  Mitigating local congestion.

| Protocol Reference | 6.1 (3) | 6.5.1.2 (1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - Notified by the ERCOT Transmission and Security operator that specific Resources carrying Non-Spin are needed for local congestion; THEN: - Deploy specific Resources |
| POST | Post message on MIS public utilizing Notice Builder. Typical MIS Posting: ERCOT is deploying Non-Spin Reserve for [XXXX] constraint. |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| 2 | IF: - The Non-Spin obligation ends for the Resource deployed, AND - The Resource is still needed; THEN: - Issue an electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose Resource tab - Choose Commit as the Instruction Type - State Local Congestion in Other Information |
| 3 | IF: - An additional Resource is needed to be deployed; THEN: - The previous Resource deployed will need to be deployed again, along with the additional Resource. |
| Termination | IF: - Notified by the ERCOT Transmission and Security Operator that Non-Spin is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.2). |
| CANCEL POSTING | Cancel the MIS message. |
| LOG | Log actions. |

## 4.1	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve or reject Resource decommitments in the Operating Period.

| Protocol Reference | 6.4.6 | 6.4.6.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Operating Period |  |
| NOTE | - The Operating Period is the two-hour period comprised of the Operating Hour and the clock hour preceding the Operating Hour - A QSE may request to decommit a Resource other than a QSGR for any interval that is not a RUC-Committed Interval by verbally requesting ERCOT to consider its request - ERCOT shall review the requests in order of receipt - A QSE may decommit a QSGR without any request for any interval that is neither a RUC-Committed Interval nor an interval in which a manual override by the ERCOT Operator. |
| NOTE | If a combined cycle train (CCT) is transitioning from one configuration to another, this is not a QSE requested decommit. |
| 1 | IF: - A QSE requests to decommit a Resource that has been Self-Committed (other than a QSGR); THEN: - Determine if the Resource is receiving negative LMPs - If negative LMPs, proceed with this procedure - If no negative LMPs, proceed to step 2 IF: - A Resource is receiving negative LMPs; THEN: - Determine if Resource is carrying A/S - If yes, inquire how A/S will be replaced - Determine if there could be a capacity issue if Resource is decommitted (PRC drops < 2500) - If Resource is not allowed to decommit, override HDL to LSL (see Desktop Guide Common to Multiple Desks Section 2.13) - If override is used, the Resource will not be able to carry A/S, and will need to be marked as undeliverable - If no capacity issue exists, grant approval to decommit - Issue an electronic VDI - Choose “Resource” tab - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type tab |
| 2 | IF: - A QSE requests to decommit a Resource that has been Self-Committed (other than a QSGR); THEN: - Determine if the Resource is carrying A/S. - If yes, inquire how A/S will be replaced, - Determine if there could be a capacity issue if Resource is decommitted - If no capacity issue exists, proceed - Notify the Transmission Operator to make determination if needed for congestion management, - If not needed for congestion management. - Issue electronic VDI - Choose “Resource” tab - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type tab |
| 3 | Log actions taken. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 6.4.8.1 | 6.4.8.1.1 | 6.4.8.1.2 | 6.4.8.1.3 |
| --- | --- | --- | --- | --- |
|  | 3.16 (4) | 6.4.8.2 | 6.4.8.2.2 | 6.5.9(4) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - Once the notice is given, no further offers are eligible for that SASM. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. - See Desktop Guide Common to Multiple Desks Section 2.15 if the savecase function fails when running a SASM |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services will have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify that the RUC Operator has issued an Emergency Notice by making a Hotline call to the QSEs, - Procure all Ancillary Services for the next operating day through a SASM, (Refer to Desktop Guide Resource Desk Section 2.8.4) |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor about the remaining A/S insufficiencies. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline Notification and post message on MIS Public using Notice Builder, - Procure more Ancillary Services through a SASM (Refer to Desktop Guide Resource Desk Section 2.8.3). Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reason]. At [xx:xx] ERCOT will open a SASM to procure the additional Ancillary Services for hours [hours] for operating day [day]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor about the remaining A/S insufficiencies. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | Once verified that all Ancillary Service has been procured, cancel the Watch: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace A/S capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the A/S capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to Desktop Guide Resource Desk Section 2.8.1 or 2.8.2). |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies. |
| 3 | IF: - A QSE is unable to provide their SASM awards; THEN: - Determine if there is time to open an additional SASM, AND - Send failure to provide notification. |
| 4 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 5 | Send information in an email to the following distribution list: - SASM |

## 7.1	Market Notices

Procedure Purpose:  Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 9 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - When extreme cold weather is 5 days away and daily temperatures are forecasted to remain 32°F or below in the three largest weather zones. - When an approaching Hurricane / Tropical Storm is approximately 5 days away. Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When extreme cold weather is 3 days away and daily temperatures are forecasted to remain 32°F or below in the three largest weather zones. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect System Reliability. - When an approaching Hurricane / Tropical Storm is approximately 1 day away. - When extreme cold weather is 1 day away and daily temperatures are forecasted to remain 32°F or below in the three largest weather zones. - When temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones or when temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT varies from time-line for DAM/DRUC. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED). - When extreme cold weather is beginning to have an adverse impact on the ERCOT System. |
| ### Scripts |  |
| Hotline | Hotline calls are usually made by Real-Time Operator, the scripts below are for reference if needed: Notify QSEs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 9.1	Respond to Miscellaneous Issues

Procedure Purpose: To minimize telemetry issues that could have an impact on LMPs.

| Protocol Reference | 6.3.2(3) | 3.10.7.5 | 3.10.7.5.1 | 3.13.7.5.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.7.1.5 | 6.5.7.1.13(4) |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step |  |  | Action |  |
| --- | --- | --- | --- | --- |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |  |  |  |
| Notification of Telemetry Issue |  |  | IF: - There is a telemetry issue, THEN: - Ensure the appropriate Control Room personnel are aware of the issue, and - Instruct the QSE to correct the issue. |  |
| QSE Override |  |  | IF: - The QSE cannot fix the issue in a timely manner, THEN: - Ask the QSE to override the bad telemetry. |  |
| QSE unable to Override |  |  | IF: - For some reason, the QSE cannot override the bad telemetry, NOTIFY: - Shift Supervisor and Operations Support Engineer The Operations Support Engineer will work with the QSE and/or the ANA group to override the bad telemetry, however it may be necessary for the Real-Time operator to make manual adjustments in SCED until the issue is resolved. |  |
| ### Backup/Alternate Control Center Transfer |  |  |  |  |
| 1 |  |  | When notified by a QSE that they will be transferring to or from their backup/alternate control center, - Identify the [QSE] in the email notification - Send e-mail to “1 ERCOT System Operators” - Make log entry. |  |
| ### QSE Issues |  |  |  |  |
| 1 |  | If a QSEis not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |  |  |
| 2 |  | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |  |  |
| 3 |  | If a QSE is having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |  |  |
| 4 |  | As time permits, log and notify the Shift Supervisor of any actions taken and unresolved issues. |  |  |
| ### Missing Data from MIS Postings |  |  |  |  |
| 1 |  | IF: - A call is received about data missing or data being incorrect, THEN: - Transfer call to the Help Desk, and - Notify the Shift Supervisor and Operations Support Engineer. |  |  |
| Log |  | Log the information. |  |  |
| ### Courtesy Hotline calls for ERCOT Application Issues |  |  |  |  |
| 1 |  | WHEN: - Notified from IT support of application(s) issues that are causing Market Participants an inability to submit data to ERCOT; THEN: - Make a courtesy hotline to inform them. Typical script: “This is ERCOT Operator [first and last name]. This is a courtesy call to inform you that ERCOT is experiencing application problems which is causing QSEs issues with submittals. |  |  |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |  |  |  |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Transfer call to the ERCOT Transmission Operator. |  |  |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |