## Power Operations Bulletin # 591

ERCOT has posted/revised the Shift Supervisor Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.1	System Operator Responsibility and Authority

Procedure Purpose: To ensure the System Operators know their roles, responsibility and authority.

| Protocol Reference | 6.5.1.1 | 6.5.1.2(3) | 6.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.2(1) |  |  |  |
| NERC Standard | EOP-002-2.1 R1 | EOP-001-0 R4.1 | IRO-001-1.1 R3 | PER-001-0 R1 |
|  | TOP-001-1 R1 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

- English shall be used as the language for all communications between and among operating personnel responsible for the real-time generation control and operation of the interconnected Bulk Electric System.

The System Operator (SO) shall, in accordance with NERC Reliability Standards, have clear decision-making authority to act and to direct actions to be taken by Transmission Operators, Balancing Authorities, Generator Operators, Transmission Service Providers, Load-Serving Entities, and Purchasing-Selling Entities within its Reliability Coordination Area to preserve the integrity and reliability of the Bulk Electric System during both normal and emergency conditions.  These actions shall be taken without delay, but not longer than 30 minutes which may include shedding of firm load without obtaining approval from higher-level personnel.  The ERCOT System Operator represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

- The SO on duty is, in accordance with the ERCOT Protocols, Operating Guides, and NERC Reliability Standards, and acting as the Balancing Authority, Transmission Operator, Regional Reliability Coordinator, and Interchange Coordinator shall request and receive information required to continually monitor the operating conditions and request that individual Market Participants (MPs) make changes, which will assure security and reliability of the ERCOT system.

- The SO issues Dispatch Instructions for the Real-Time operation of Transmission Facilities to a TO, and to a QSE for the Real-Time operation of a Resource.

- The SO shall, on an ERCOT-wide basis, coordinate the ERCOT System Restoration (Black Start) Plan.  The SO shall implement the Black Start Plan and shall direct the reconnection efforts of the islands, established by restoration activities.  The SO shall coordinate the mutual assistance activities of the ERCOT participants during system restoration activities.

- The SO shall consider all equipment operating limits when issuing Dispatch Instructions except as stated in Protocol Section 6.5.9, Emergency Operations, if a Dispatch Instruction conflicts with a restriction that may be placed on equipment from time to time by a TO, or a Generation Resource’s QSE to protect the integrity of equipment, ERCOT shall honor the restriction.

- The SO performs security analyses on a Day Ahead and real-time basis and ensures all Forced Outages are entered into the Outage Scheduler. The SO shall obtain or arrange to provide emergency energy over the DC Tie(s) on behalf of ERCOT.

- The SO shall issue appropriate OCNs, Advisories, Watches, and Emergency Notices, and coordinate the reduction or cancellation of clearances, re-dispatch of generation, and request, order, or take other action(s) that the SO determines is necessary to maintain safe and reliable operating conditions on the ERCOT system in accordance with ERCOT Protocols, Operating Guides, and NERC Reliability Standards.  The SO will implement and terminate ERCOT Time Corrections, and will determine the need for and implement the operation of a Qualified Scheduling Entity (QSE) on Constant Frequency Control for loss of ERCOT’s load frequency control system.

- As the Reliability Coordinator, ERCOT ISO shall comply with its Regional Reliability Plan that has been approved by the NERC Operating Committee.

The SPP DC-Tie processes, procedures, or plans that support or affect SPP shall be reviewed at least once every 3 years and updated if needed.  These would include any DC-Tie procedures, inadvertent energy procedures, and emergency procedures.

## 3.3	Disseminating Information to System Security Response Group (SSRG)

Procedure Purpose: To communicate information concerning disturbances or unusual occurrences to appropriate parties in the Interconnection.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.8 |  |  |  |
| NERC Standard | CIP-001 R1, R2, R3 | EOP-004 OE-417 |  |  |

| Version: 1 | Revision: 4 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Threats can be viewed at the following links: http://www.esisac.com/SitePages/Home.aspx, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert levels are listed in the Security Alert Plan. |
| NOTE | - The SSRG e-mail exploder list is used to disseminate information to the SSRG members of the ERCOT Region when an SSRG conference call is not necessary. - This information is intended for use within the industry and not for public release. - At the beginning of each e-mail state the follow “This information is intended for use within the industry and not for public release” - At the bottom of each e-mail, be sure to include a Confidentiality Notice and your signature. - The Reliability Coordinator Information System (RCIS) is used to disseminate information to other RCs in other Interconnections. - Do not list the entity name on the SSRG e-mails or on the RCIS. |
| NOTE | The only notification that is required is for suspected sabotage (cyber or physical). However, some entities make notifications on the following: - Copper thefts - Substation break-in - Vandalism - Malicious mischief - Suspicious photos |
| 1 | IF: - Notified by a QSE or TO of a disturbance or unusual occurrence; THEN: - Verify the following: - Is the occurrence considered “theft of property”? (proceed to Step 2) - Is the occurrence being investigated as a “suspected sabotage event” (proceed to Step 3). |
| 2 | IF: - Theft of property can be reasonably determined and the incident is not related to a suspected sabotage event; THEN: - Verify that local Law Enforcement Agencies have been notified, - Send an e-mail to the ‘SSRG’ distribution list, stating in the e-mail that the event is currently not considered as an act of suspected sabotage. |
| 3 | IF: - The entity has determined the event to be a suspected sabotage event or if the entity is unable to make that determination without further investigation/information; THEN: - Verify that the FBI has been notified, - Send an e-mail to the ‘SSRG’ distribution list, stating in the e-mail that the event is considered an act of suspected sabotage OR further investigation/information is needed to determine if event is an act of suspected sabotage, - Notify TOs and QSEs via Hotline with information you have, - Post on the RCIS using “CIP Free Form” (see Desktop Guide Shift Supervisor Section 2.2), - Coordinate with the Manager, System Operations or designee to determine if procedure 3.4 SSRG Conference Calls is necessary and for any NERC and DOE reporting requirements. Typical Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT notified the System Security Response Group (SSRG) of a suspected sabotage event [give information]. Please notify your SSRG representative.” |
| 4 | WHEN: - Updates are received; THEN: - Send an updated e-mail to the ‘SSRG’ distribution list, - Update RCIS as needed |
| Physical | For suspected physical sabotage at the ERCOT facilities, refer to ERCOT Guideline GL7.8.1 located under the “Sabotage Event Recognition” tab in each procedure manual. RCIS and SSRG postings will also be required. |
| Cyber | When notified by Cyber Security of a reportable event at ERCOT, collect the information to post under “CIP Free Form” on the RCIS. |

## 3.6	Monitoring W-N Stability and N-H Voltage Limits

Procedure Purpose: To collect data on the West – North dynamic stability limit and the North – Houston VSAT voltage stability limit for the NERC Reliability Metric.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-004-2 R1 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North stability and the N-H voltage are IROLs; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor W-N stability and N-H voltage limits. |
| 2 | If the W-N stability or N-H voltage stability exceed the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. - Save the study in the STNET directory. If the W-N stability limit or N-H voltage stability limit is exceeded for more than 30 consecutive minutes, notify the Manager, System Operations immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

## 5.6	Equipment Limitation and Rating Changes

Procedure Purpose:  To ensure line rating changes are documented and correct.

| Protocol Reference | 6.5.3(2) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Line Rating Changes |  |
| NOTE | Normally line rating changes can only be changed when a NOMCR is received. |
| 1 | IF: - Notified by a TO of an incorrect line rating; THEN: - Notify the Operations Support Engineer. |
| 2 | Make log entry. |
| ### TO Temporary Equipment Limitation Notifications |  |
| 1 | IF: - Notified by a TO of any limitations on the Transmission Facilities that may affect Dispatch Instructions; THEN: - Notify the Operations Support Engineer. |
| 2 | IF: - The Operations Support Engineer confirmed the Temporary Equipment Limitation Notifications may affect Dispatch Instructions; THEN: - Notify the Manager, System Operations, or designee to post on the MIS Secure Area the Transmission Facility limitations that may affect Dispatch Instructions. |
| 3 | Make log entry. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Regional Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R4.1, R5 | EOP-002-2.1 R3, R6.3, R7.2 | EOP-004-1 R1, R3.1 | IRO-014-1 R1.1.2 |
|  | IRO-015-2 R15 | TOP-002-2 R4 | DOE OE-417 |  |

| Version: 1 | Revision: 9 | Effective Date: May 1, 2011 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template between 0300 – 0400 and again between 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - When Off-Line Non-Spin is deployed (provide times) - A special update is not needed; provide information next time report is updated. - Conditions change that required new notices to be issued or cancelled (e.g., OCN , Advisory, Watch, or Emergency Notice ) - Clarify whether Transmission Watch/Emergency is due to a planned or forced outage. - A projected reserve capacity shortage develops - Local reliability concerns arise including actual overloads or loss of load - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas restrictions, not expected to cause reliability issues - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Send updated report when conditions have returned to normal. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Physical Responsive Reserve ≤ 1750 MW and trending downward - Critical - Physical Responsive Reserve ≤ 1375 MW and trending downward Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - High - EEA Level 2 in effect - Physical Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.8 Hz - Critical - EEA Level 3 in effect |  |
| ### Texas RE Event Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations or designee - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis process, events include the following: Category 1 Events: - An unexpected outage, contrary to design, of three or more elements caused by a common disturbance. For example: - The loss of a combination of NERC-defined elements or facilities - The loss of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); combined cycle units count as one unit - Unplanned evacuation from a control center facility with BPS SCADA functionality for 30 minutes or more - Failure or misoperation of SPS/RAS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BPS emergency - Unintended BPS system separation that results in an island of 100 MW to 999 MW. Excludes BPS radial connection, and non-BPS (distribution) level islanding - The loss of generation of 1,000 MW – 1,399 MW Category 2 Events: - Complete loss of all BPS control center voice communication system for 30 minutes or more - Complete loss of SCADA, control or monitoring functionally for 30 minutes or more - Loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - Voltage excursions equal to or greater than 10% lasting more than 15 continuous minutes due to a BPS emergency Category 3 Events: - Loss of load or generation of 1,400 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Loss of load or generation from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Loss of generation of 10,000 MW or more - Loss of load of 10,000 MW or more |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations or designee when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". |  |
| OE-417 Reporting Events | DOE OE-417 initial reports are to be completed within 1 hour, forms can be downloaded at: ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc. Electronic forms are preferred. OE-417 reports are required for the following events: - System-wide voltage reduction of 3 % or more - Public appeal to reduce the use of electricity for purposed of maintaining the continuity of the electric power system - Load shedding of 100 MW or more implemented under emergency operational policy - Uncontrolled loss of 300 MW or more of firm system loads form more than 15 minutes from a single incident - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Fuel supply emergencies that could impact system adequacy or reliability - Loss of electric service to more than 50,000 customers for 1 hour or more - Complete operation failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system |  |
| NERC IROL and Preliminary Disturbance Report EOP-004-1 | NERC Preliminary Disturbance reports are to be completed within 24 hours, forms can be downloaded at: http://www.nerc.com/page.php?cid=5¦66 NERC Disturbance reports are required for the following events: - Loss of bulk power transmission component that significantly affects the integrity of system operations, which resulted in actions such as: - Modification of operating procedures - Modification of equipment to prevent reoccurrence of event - Identification of valuable lessons learned - Identification of non-compliance with NERC standards or policies - Identification of a disturbance that is beyond recognized criteria (i.e. three-phase fault with breaker failure, etc) - Frequency or voltage going below the under-frequency or under-voltage load shed points - The occurrence of system separation or system islanding or both - Loss of generation of 1,000 MW or more - IROL violation - Any action taken by a GOP, TOP, BA, or LSE that results in: - Sustained voltage excursions equal to or greater than ±10 percent - Major damage to power system components - Failure, degradation, or misoperation of system protection, SPS, RAPs, or other operating system that do not require operator intervention, which did result in, or could have resulted in, a system disturbance. - Firm load shedding of 100 MW or more to maintain the continuity of the BES - Loss of firm load demands totaling more than 200 MW or 50 percent of the total customers for ≥ 15 minutes |  |
| 1 | When required to file a report (If Manager or designee is unavailable): Forward the TO or QSE report or the Director of Cyber Security’s report to: - NERC (esisac@nerc.com, fax (609) 452-9550) - DOE (doehqeoc@oem.doe.gov, fax (202) 586-8485) - “NERC and DOE Disturbance Reporting” e-mail list. |  |
| ### RCIS Reporting |  |  |
| NOTE | Refer to Desktop Guide Shift Supervisor Section 2.2. |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| TEA Postings | There are four levels of Transmission Emergency Alert (TEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “System Emergency”: - “ERCOT is declaring TEA 1 on the North-Houston interface” - “ERCOT is declaring TEA 2 on the North-Houston interface; Load Resources have been deployed in the Houston area”. - “ERCOT is declaring TEA 3 on the North-Houston interface; firm load is being curtailed in the Houston area”. - “ERCOT is in TEA 0 and back to normal operations” |  |
| SEA Postings | There are four levels of Security Emergency Alerts (SEA). This is currently a NERC pilot project. As ERCOT enters each level, postings must be made on the RCIS under “CIP Free Form”: - “ERCOT is declaring SEA 1 for a [cyber or physical] attack on [control center, generating facility, substation, and transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 2 for a [cyber or physical] attack on [control center, generating facility, substation, and transmission line] located in [west, north, south, central] Texas”. - “ERCOT is declaring SEA 3 for a [cyber or physical] attack on [control center, generating facility, substation, and transmission line] located in [west, north, south, central] Texas”. - “ERCOT is in SEA0 and no longer under threat”. |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed, THEN: - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - Verify the High and Low temperature forecast from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically during the day, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | When alerts and warnings for GMDs are issued for K-7 or higher: - Notify the TOs and QSEs by posting message on MIS Public using Notice Builder, Log the information. |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability. |  |

## 7.1	Abnormal Events

Procedure Purpose:  To provide guidance for those events outside normal operating parameters.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.3 |  |  |  |
| NERC Standard | BAL-002-0 R6.2 | EOP-001-0 R4.4, R5 | EOP-004-1 R1, R3.1 | IRO-005-2 R1.7, R1.10, R6 |
|  | DOE OE-417 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - The ERCOT Shift Supervisor will act as the main contact and answer inquiries between the control room and other ERCOT operations groups during abnormal events - See Phone Book at Shift Supervisor’s Desk |
| ### System Disturbance |  |
| NERC | ERCOT ISO shall fully restore the minimum Contingency Reserve requirement of the ERCOT Region’s largest single contingency (1375 MW) within 90 minutes, and restore Responsive Reserves to 2300 MW or greater as soon as possible. |
| 1 | IF: - A system disturbance causes the ERCOT system to violate the Single Contingency Secure status; THEN: - Verify that the System Operators take all actions necessary as described in the ERCOT Operating Guides. |
| 2 | IF: - The system disturbance cannot be normalized with current on-shift staff; THEN: - Identify and Assign additional System Operators, Operations Support, Operations Analysis, or Market Operations staff to assist in normalizing the system condition. |
| 3 | The ERCOT Shift Supervisor will ISSUE Emergency Communications & Notifications to ERCOT staff and management in accordance with Desktop Guide Shift Supervisor Section 2.1. |
| ### Degraded Weather |  |
| 1 | WHEN degrading weather conditions are forecasted, verify that the System Operators on the Transmission & Security and Real-Time desks issued corresponding OCN, Advisories, and Watches. |
| 2 | Monitor reserves and Ancillary Services capacities during degraded weather periods such as extreme hot weather, extreme cold weather, and other significant weather events. Determine if additional A/S is needed. |
| 3 | IF: - Forecasted weather conditions are extreme, and it has been deemed necessary that additional staff is required; THEN: - Identify and Assign additional System Operators, Operations Support, Operations Analysis, or Market Operations staff to assist in operating the system during degraded weather conditions. |

## 7.4	Hurricane/Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov) |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Ensure OCN is issued. - Review the expected path of the hurricane/tropical storm and consult with the Operations Support Engineer to determine if multiple contingencies should be studied due to the possibility of transmission outages or loss of load. - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. Outages that could be critical are: - Getaways from power plants, in the affected areas, that need to remain on during the storm for reliability. - 345 KV transmission paths in the affected areas, OR - 345 KV transmission paths that will significantly impact the flow of power to and from the affected area. |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. - Ensure Advisory is issued. - If STP is in the path of the hurricane/tropical storm and the QSE is planning to take the unit offline, - Contact Operations Support to run studies to determine the impact and evaluate system conditions. - If necessary determine the generation needed to replace the loss of capacity from STP. - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. - Ensure Watch is issued - If necessary, instruct the RUC Operator to commit additional Resources as per Operations Support recommendations. - Determine if the need to have a conference call bridge open with the most affected TOs. - Determine if the need for additional support staff from EMMS Production, ANA, Operations Support, and Operators. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Emergency Notice | When Hurricane/Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. - Ensure Emergency Notice is issued |

## 7.5	Extreme Cold Weather

Procedure Purpose: To ensure ERCOT is prepared for Severe Cold Weather Operations

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Extreme cold weather notifications are called when temperatures are forecasted to remain 32°F or below in the following weather zones: - North Central (NORTH_C) - South Central (SOUTH_C) - Coast (COAST) |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When approaching extreme cold weather is approximately 5 days away: - Ensure OCN is issued - Continue to monitor the expected path of the approaching extreme cold front - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market allows - Review emergency operating procedures |
| Advisory | When approaching extreme cold weather is 3 days away: - Ensure Advisory is issued - Continue to monitor the expected path of extreme cold front - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early - Contact Operations Support to run studies to determine the impact of current and future outages - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market or if additional Ancillary Services will be needed - Review emergency operating procedures |
| Watch | When approaching extreme cold weather is 1 day away: - Ensure Watch is issued - Continue to monitor the expected path of extreme cold front - Review emergency operating procedures - Determine the need for additional support staff - Determine if additional Ancillary Services will be needed - Ensure maximizing generator availability is complete - Determine if Resources need to be committed early before freezing temperatures arrive - Consider if fuel switching is needed. |
| Emergency Notice | When extreme cold weather has arrived and is beginning to have an adverse impact on the ERCOT System: - Ensure Emergency Notice is issued - Implement emergency procedures as needed |

## 7.6	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for Extreme Hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| OCN |  | When Extreme Hot weather is forecasted approximately 5 days away: - Ensure OCN is issued - Continue to monitor the weather - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment |
| Advisory |  | - When Extreme Hot weather is forecasted approximately 3 days away: - Ensure Advisory is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored |
| Watch |  | When Extreme Hot weather is forecasted approximately 1 day away: - Ensure Watch is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early - Contact Operations Support to run studies to determine the impact of current and future outages - Review emergency operating procedures |
| Emergency Notice |  | When Extreme Hot weather has arrived and is beginning to have an adverse impact on the ERCOT System: - Ensure Emergency Notice is issued - Implement emergency procedures as needed |
| Log | Log all information in the Operator log and notify the ERCOT Manager, System Operations or designee of any issues. |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |