## Power Operations Bulletin # 592

ERCOT has posted/revised the Transmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.1	System Overview

Procedure Purpose: Analyze data to maintain system security.

| Protocol Reference | 6.3.2(3)(a) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-1 R6, R8 | IRO-005-2 R1.1, R1.2, R1.3 | NUC-001-1 | PRC-001-1 R2.2 |
|  | TOP-006-1 R2 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Review | REVIEW each of the following as necessary to confirm system reliability status: - Alarms - State Estimator (SE) - Real Time Contingency Analysis (RTCA) - Transmission Constraint Manager (TCM) - Approved and Forced Outages - Load Forecast - Daily Transmission Limits - Voltage and Stability Limits - Real Time Monitoring (RTMONI) - Security Constrained Economic Dispatch (SCED) - Real Time Reserve Monitoring |
| Gap Study | Run a gap study for the next day’s peak hour to ensure all contingencies can be solved. If necessary, request the Operations Support Engineer to review results and make suggestions. If both CPSES units are offline, the Auxiliary load will need to be manually adjusted to 45 MW at both units. - Refer to Desktop Guide Transmission Desk Section 2.5 Conducting Future Security Analysis if necessary. - Save study - Log the following: - Study name - Any issues that could not be resolved and actions taken. |
| STP Lines | A minimum of two transmission lines should be in service at all times. The in-service lines should be from at least two of the groups in the table below: Independent Groups of STP Transmission Lines Group 1; Group 2; Group 3. STPZWP39; STPELM18; DOWSTP18. STPELM27; DOWSTP27. STPWAP39. Note: The 3 Transmission lines, STP – Blessing (BLESSING), STP – HILLJE (HLJSTP64), STP – HILLJE (CKT_3124) (EMS naming convention) are not included in this table because these circuits are not part of STP’s credited offsite sources. If a minimum of two lines are not in service, notify the QSE. |
| Protective Relay or Equipment Failure | When notified by a TO that a protective relay or equipment failure reduces system reliability: - Ask the TO how it reduces ERCOT Grid system reliability and if any corrective actions have been taken, - Notify the Operations Support Engineer to verify that system reliability has been affected. If so, a corrective action must be taken within 30 minutes, - Determine if other TOs are affected by this failure and make notification by phone, - Make log entry of events. |
| Dynamic Transmission Limits | IF: - Any changes in the system that could affect the security and dynamic transmission limits; THEN: - Post message on MIS Public using Notice Builder. |

Procedure Purpose: To ensure SOLs and IROLs are monitored.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002 R8, R9 | IRO-008-1 R2 | NUC-001 | TOP-004 R4 |

| Version: 1 | Revision: 7 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Reliability Coordinator must ensure SOL and IROL monitoring continues if analysis tools are unavailable. The analysis tools needed are: - State Estimator - RTCA - VSAT/TSAT Real-Time Assessments must be performed at least once every 30 minutes to determine if any IROLs are exceeding or are expected to exceed its limit |
| 1 | IF: - RTCA or the State Estimator has not solved within the last 10 minutes, THEN: - Notify Operations Support Engineer, - Refer to Desktop Guide Transmission Desk Section 2.1 and run through the checklist, - Request Operations Support Engineer to calculate limits manually if EMS will be unavailable for an extended period of time. |
| 2 | If RTCA or the State Estimator has NOT solved within the last 15 minutes or ERCOT ISO has experienced a critical failure of its EMS: Make a Hotline call to issue an Advisory to the TOs: - Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory due to ERCOT’s RTCA and State Estimator have not solved in the last 15 minutes. Please monitor your own service area and notify ERCOT if you exceed the normal rating of your transmission elements. Report West - North and North – Houston stability limits if power flows reach 70% of their respective limits. Continue to monitor voltages in your area and notify ERCOT of any forced line operations.” [Select TO], “Please repeat that back for me.” - If repeat back is CORRECT, “That is correct, thank you.” - If INCORRECT, repeat the entire process until the repeat back is correct. |
| 3 | Notify the appropriate Nuclear Plant’s QSEs and inform them that ERCOT’s RTCA is not function and is expected to be functional within approximately [# minutes]. |
| 4 | Post Advisory message on MIS Public using Notice Builder. |
| 5 | Once RTCA and State Estimator are operational: Make a Hotline call to cancel the Advisory to the TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory, ERCOT’s RTCA and State Estimator are functioning and we are back to normal operations. [Select TO], “Please repeat that back for me.” If the repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| 6 | Notify the appropriate Nuclear Plant’s QSEs to inform them that RTCA is now functional. |
| 7 | Cancel Advisory message on MIS Public using Notice Builder. |
| 8 | If VSAT and/or TSAT has not solved within 1 hour: - Manually run VSAT/TSAT, - If no results, notify Operations Support Engineer, - If RTMONI is unavailable, the last good value will be recorded in PI or on the website. If transmission outages start/end during the failed period, refer to Operations Engineering Day-ahead limits which incorporate outage analysis. |
| 9 | Make log entry of events. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11(1)&(4) | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.2.2 |  |  |  |
| NERC Standard | IRO-003 R1 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-002 R6, R8 |
|  | IRO-004 R3 | TOP-001 R1, R2, R5 | TOP-002 R6, R8, R10 | TOP-004-1 R1, R6, R6.6 |
|  | TOP-006 R5 | TOP-008 R1, R2, R4 | EOP-003-1 R6 |  |

| Version: 1 | Revision: 15 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (major telemetry, etc), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. Error! Hyperlink reference not valid.A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) located in the Outage Notes - Unit specific dispatch instructions (Manual Dispatch or VDI) - If approved by the Shift Supervisor, Non-Spin may be used. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP , - A hardcopy of the SPSs is maintained on the floor by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congestion management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – Mitigate local congestion and increase W/N transfers - Big Lake – Mitigate local congestion and increase W/N transfers - Firerock ETT – Mitigate local congestion and increase W/N transfers - Nelson Sharp – Valley import during outages and flow in/out of Corpus Christi - Hamilton Road – Control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – Control Laredo import issues during outages - Thomaston – Control flow into Cuero, Yoakum and Victoria Areas |  |
| NOTE | Refer to OpsMon Display 08 HRUC Phase Shifter Position |  |
| ### Review Planned Outage Notes |  |  |
| 1 | Review daily outage notes: IF: - Outage notes recommend slower moving Resources to be lowered to maintain system security; THEN: - Take a real-time snap shot to determine where Resource(s) are needed before outage is taken - Use the manual override to step down Resource(s) - Once Resource(s) are down to where snap shot showed, - Give approval for switching, - Release manual overrides, and - Activate SCED constraint (when necessary). - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions due to XXXX outage. |  |
| 2 | IF: - An outage requires a Resource to be On-line to solve a voltage issue and having the Resource On-line causes a post-contingency overload; THEN: - Manually override the Resources to its LSL - Notify QSE of action - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions due to XXXX outage. |  |
| Log | Log actions taken. |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - SE and/or RTCA is not solving; THEN: - Notify Operations Support Engineer, IF: - SE and/or RTCA has not solved for 15 minutes, THEN: - Refer to section 3.3 “Analysis Tool Outages” in this procedure. |  |
| 2 | IF: - RTCA has run within 10 minutes; THEN: - Examine the RTCA contingency violations “Branch” summary, and ensure that no post-contingency branch violation greater than 100% of the emergency rating exists. |  |
| 3 | IF: - A major change of Resource or Transmission Element Status; THEN: - Re-start RTCA and VSAT. |  |
| Log | Log actions taken. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | WHEN: - Post-contingency overloads are approaching 100% of the Emergency Rating; THEN: - Determine if the SCADA is of similar magnitude to the pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate. - Make log entry. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP exist - Verify that a PST cannot be used to resolve congestion |  |
| 4 | IF: - Post-contingency overloads of 100% or greater exist that needs to be passed to SCED to be resolved; THEN: - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint if needed (minimum of 95%, excluding W-N), - If experiencing oscillation issues, notify the Operations Support Engineer to investigate - If constraint needs to be controlled before the next SCED run: - Manually run RTCA after activating the constraint, - Manually execute the SCED process - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 5 | IF: - A Qualifying Facility (QF) needs to operate below its LSL, or be ordered off-line to solve congestion; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 6 | IF: - Post-contingency overloads of 100% or greater of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 100% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”. |  |
| 7 | IF: - Congestion can not be fully resolved and does not have a MP or TOAP; THEN: - REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.5 Mitigation Plan). |  |
| 8 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A Quick Start Resource is needed and not given SCED base points; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running, - Notify QSE as time permits - Post message on MIS Typical Posting Script: ERCOT is taking manual actions for XXXX constraint. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| Log | Log actions taken. |  |
| ### Post-Contingency Overloads on Private Use Networks (PUNs) |  |  |
| 1 | IF: - Post-contingency overloads greater than 100% of the Emergency Rating exist; THEN: - Contact the PUNs QSE to determine if the post-contingency is real (review MW, MVAR flows and facility ratings), - If real, give the QSE the opportunity to correct or request a Mitigation Plan for the contingency. |  |
| 2 | IF: - Mitigation Plan is needed; THEN: - Notify the Operations Support Engineer to work with the QSE to approve a plan. |  |
| 3 | IF: - It is determined that the post-contingency is real and a Mitigation Plan will not be approved; THEN: - Direct the QSE to take action such as lower/raise generation or load (directs only, do not override HDL/LDL or activate constraint in SCED). |  |
| 4 | - Acknowledge the post-contingency overload in TCM - Make log entry of actions taken |  |
| ### Managing Constraints in SCED |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for exceeded constraints). |  |
| 1 | Verify that the SCED executions are reducing the flows on each constraint that is binding. |  |
| 2 | If a constraint is exceeded in SCED, which can be determined when it has reached its max shadow price. Review the following bullets to determine the next action: - Ensure at least 2% shift factors for units dispatchable by SCED exists for constraint (general rule) - If not, see section 4.5 Mitigation Plan - Ensure curtailed units are following base points (RLC Output Data display), - Verify that units with large shift factors (SF button on TCM display) do not have a status of ONTEST (RLC Output Data display), - Redistribute A/S to increase capacity available to SCED (see separate procedure below), - Determine if a unit carrying Off-line Non-Spin is needed to solve congestion, - Ask Resource Operator to deploy Non-Spin for the specific unit - The telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Determine if additional units need to be committed/decommitted, - Determine if there is a non-cascading conflicting constraint that is preventing the constraint to solve, - Override Resource that is in conflict to optimal output for both constraints - Release the constraint that prevents resolving the more severe post-contingency overload, - Create a “suggestion plan” for the constraint if can’t determine course of action from shift factors |  |
| 3 | At times, it may be necessary to manually override HDL/LDL, these reasons could include the following: - Manually dispatching slower moving Resources before an outage to better manage congestion caused by the outage - Manually overriding Resources which are causing an SPS to continuously trip - Conflicting constraints - Unsolved contingencies IF: - An override is necessary; THEN: - Notify QSE of override - Consider doing the override in steps as to not exceed ramp rate - Post message on MIS under Operational Information Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. NOTE: - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - DO NOT override a Resource ONRR |  |
| 4 | IF: - All applicable steps above have been completed, AND constraint is still exceeded in SCED (max shadow price); THEN: - Instruct Operations Support Engineer to develop a mitigation plan, AND - Contact Manager or designee to investigate further |  |
| NOTE | ERCOT-MA>Market Operation>Real-Time Market>SCED Displays>External Input Data>EMS/TCM Constraint: Generator Shift Factors OR EMP Applications>TCM-Transmission Constraint Manager>Related Displays>Message Log for CAM IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk to issue a ticket to EMMS Production to fix immediately. |  |
| Log | Log all action taken including the following: - Reason for doing a manual override - Any security violations that were ≥ 125% of the Emergency Rating |  |
| ### Redistribute A/S to Increase Capacity available to SCED |  |  |
| 1 | RLC Unit Input Data display IF: - A/S needs to be removed from a specific unit in order to increase capacity to SCED; THEN: - Determine which A/S to remove - Instruct the QSE to remove the A/S by updating their telemetry to free that capacity to SCED - Notify Resource Operator with undeliverable A/S type, amount and approximate hours. |  |
| LOG | Log all actions taken |  |
| ### Unsolved Contingencies |  |  |
| 1 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Operations Support Engineer to investigate |  |
| LOG | Log all action taken including the following: - Reason for unsolved contingency - Actions taken to resolve |  |
| ### Model Inconsistencies/Updates |  |  |
| 1 | IF: - Any inconsistencies in ratings, impedance changes, etc. are found; THEN: - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required, correct it through the NOMCR process. |  |
| 2 | IF: - There is a difference in line ratings between ERCOT and a TO; THEN: - The most limiting rating will be used until the correct rating can be determined - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required correct it through the NOMCR process. |  |
| LOG | Log all actions taken |  |
| ### QSE Requests to Decommit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Initiate the Emergency Notice Hotline call, AND - Coordinate with Real-Time Operator to determine if an active transmission constraint is causing the SCED failure. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. [TO] please repeat this back to me. That is correct, thank you.” |  |
| 2 | Trouble Shooting: IF: - Transmission constraints are active, THEN: - Remove the active constraints one at a time while manually executing RTCA and SCED to determine which constraint is causing the failure. |  |

Procedure Purpose: Maintain Transmission stability between the West and North.

| Protocol Reference | 3.10.7.6(3) | 6.5.9.1(1)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Refernce |  |  |  |  |
| NERC Standard | IRO-002 R6, R8 | IRO-003 R1 | IRO-004 R3 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 |
|  | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-008-1 R2 | IRO-009 R4 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 9 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North dynamic stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| NOTE | If unexpected changes to system conditions occur between 1700 – 0900 that result in a large limit change from the day-ahead GTL posting: - Declare a Watch by posting on MIS - Make Hotline call to TOs - Notify Real-Time operator to make hotline call - Notify Operations Support Engineer to post new GTL Typical Message Script: “ERCOT has updated the posted West-North GTL limit on the MIS due to an unexpected change on the system.” |
| 1 | WHEN: - The West-North TSAT limit displayed on the W-N Stability spreadsheet changes value or color; THEN: - Verify the value is accurate and update limit on RTMONI to give transparency to TOs - . |
| AVR/PSS | WHEN: - AVR or PSS status changes are reported concerning West area generation; THEN: - Notify the Operations Support Engineer to make the changes in TSAT, AND - Follow process in Section 6.1 PSS and AVR of this manual. |
| 2 | IF: - The monitored flow on the Stability-WN monitor is approaching 85%; THEN: - Activate the West-North constraint, - Post message on MIS Public using Notice Builder, Typical Message Script: “ERCOT is constraining for the West-North stability limit.” |
| 3 | Once wind output is controlled, ease % up to allow maximum output. IF: - West – North reaches 100%; THEN: - Continue to tighten constraint, - Call QSEs with the largest WGR base point deviations |
| 4 | IF: - West – North exceeds 100% for 10 minutes; THEN: - Instruct QSEs with the largest WGR base point deviation to zero immediately (violate ramp rate), - Issue electronic VDI as time permits, - Notify the control room staff. Typical Script: “This is ERCOT operator [first and last name]. The West to North flow is exceeding the stability limit; At [xx:xx] ERCOT is directing you to take [unit name] to zero effective immediately, which means you may violate your ramp rate. I will be sending you an electronic VDI shortly. [QSE] please repeat this back to me. That is correct, thank you.” |
| 5 | IF: - Congestion management techniques fail to control the flow within 20 minutes; THEN: - Issue directive to TO to open WGR breaker with the largest WGR base point deviation (refer to Real-Time spreadsheet tab “West Wind”), - Issue electronic VDI as time permits, - Notify the control room staff. |
| Log | Log all actions taken. |
| ### Managing W-N during System Failures |  |
| 1 | IF: - The W-N constraint was active during the system failure THEN: - The Real-Time Operator will instruct the QSEs whose WGRs were being curtailed, to stay curtailed at their current output. |
| 2 | IF: - The W-N constraint was not active OR - W-N needs to be constrained further during the system failure THEN: - Issue unit specific verbal directives to QSEs with WGRs. |
| 3 | WHEN: - System is functioning; THEN: - Activate or tighten W-N constraint - Issue electronic VDIs for directives given. |
| Log | Log all actions taken. |

## 4.4	North-Houston Voltage Stability Limit

Procedure Purpose:  Maintain Transmission Stability between the North and Houston.

| Protocol Reference | 3.10.7.6 (3) | 6.5.9.1(1)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-003 R1 | IRO-002 R6, R8 | IRO-003 R1 | IRO-004 R3 |
|  | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-008-1 R1 | TOP-002 R10 |
|  | TOP-004 R1, R2, R6, R6.6 | TOP-006 R5 | TOP-007 R3, R4 | TOP-008 R1 |

| Version: 1 | Revision: 8 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards |
| VSAT | - Ensure VSAT runs every 30 minutes, - Update RTMONI with new limit each time it changes to give transparency to Market Participants. |
| NOTE | When an unexpected change to system conditions occur between 1700 – 0900 that result in a large limit change from the day-ahead GTL posting: - Declare a Watch by posting on MIS - Make Hotline call to TOs - Notify Real-Time operator to make hotline call - Notify Operations Support Engineer to post the new GTL Typical Message Script: “ERCOT has updated the posted North - Houston GTL limit on the MIS from what was posted in Day-Ahead due to an unexpected change on the system.” |
| North-Houston 345kV Circuit Outage | IF: - Any of the 345kV lines going into the Houston area has a forced outage; THEN: - Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor Step in this procedure. |
| Monitor | Monitor each of the following Reliability Margins: - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TOs in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| ≤400MW | - Activate the appropriate constraint, - Post message on MIS Public using Notice Builder. Typical Message Script: “ERCOT is constraining for the North-Houston voltage stability limit.” |
| ≤300MW | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL - Instruct Resource Desk Operator to deploy Non-Spin in the Houston area and make Hotline notification, - Issue a Transmission Watch by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North-Houston interface. Non-Spin is being deployed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| NOTE | When the Non-Spin Resource is on-line, they must change their Non-Spin schedule to 0 in order for SCED to dispatch them. |
| ≤200MW | VDI QSGR in the Houston area that were not bid in as Non-Spin. Override LDLs as needed. - Determine QSRG in the Coast Weather Zone (WZ_COAST) - Choose “COMMIT” as the Instruction Type from Resource level |
| ≤100MW | - Instruct the Resource Desk Operator to deploy Load Resources providing RRS in Houston, - Issue a Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Real-Time Operator to make same Hotline notification to QSEs, - Notify Shift Supervisor to make posting on RCIS. Typical Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice for the North-Houston interface. Load Resources in the Houston area are being deployed to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| 0MW ≥ 15 Minutes | - Instruct Centerpoint to drop firm load in 100 MW blocks. - Continue Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make NXT notification and RCIS posting. Typical Script for Centerpoint: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is directing Centerpoint to drop [*** MW] of firm load for the North – Houston stability limit. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” Typical Script for Hotline: “At [xx:xx], ERCOT is continuing the Transmission Emergency Notice for the North-Houston interface. Firm Load is being shed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” |
| Cancel | Make appropriate cancellations when back to normal operations. |
| Log | Log all actions taken. |

## 4.5	SPS, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 5.5.2 | 6.5.1.1(a),(c),(e) |  | 6.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.5.2(1) | 6.5.7.1.10 | 6.5.7.1.11(1),(4) | 6.5.7.8 |
|  | 6.5.9 | 6.5.9.1(1)(d) |  | 7.1 |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-003-1 R6, R8 | IRO-003 R1 | IRO-005-2 R1.1,R1.2, R1.3, R1.7, R1.10, R3, R5, R9, R12, R13, R16, R17 | IRO-006-5 R1, R3, R4, R5, R6 IRO-006-TRE-1 |
|  | IRO-002-1 R6, R8 | IRO-004-1 R3 | PRC-001-1 R6 | TOP-001 R1, R2, R5 |
|  | TOP-002-2 R6, R8, R10 | TOP-004-1 R1, R6, R6.6 | TOP-006-1 R3, R5 | TOP-008 R1, R2, R4 |

| Version: 1 | Revision: 7 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP |
| NOTE | Special Protection Schemes (SPS) (identified as RAS in EMS) OR Remedial Action Plans (RAP) - EXAMINE the results of RTCA, - If the background has a color indicating a SPS or RAP, - Refer to Desktop Guide Transmission Desk Section 2.6 for actions to be taken based on the color of the background. |
| Directives | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log all actions taken. |
| ### Special Protection Systems (SPS) (Identified as RAS in EMS) |  |
| NOTE | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE | Use caution when adjusting the tolerance setting <100% in RTCA. If the post-contingency loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the RTCA result will be as if there is no SPS associated with the contingency. In this scenario, congestion management is not needed until the criteria in Desktop Guide Transmission Desk Section 2.6, is met. |
| Monitor | Each SPS will be displayed on the “Real Time Values” spreadsheet, as the SPS activation threshold increases the display changes color as follows: - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 1 | Typically SPSs are to solve post-contingency overloads on the Transmission System. IF: - The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an SPS; THEN: - Utilize congestion management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the SPS will not mitigate all the overloaded elements automatically; THEN: - As system conditions warrant, utilize congestion management techniques to relieve the overload. |
| 3 | IF: - No reliability issues will arise as a result of a SPS’s operation; THEN: - At the Operator’s discretion, allow the SPS to perform its function. |
| 4 | IF: - An SPS operates; THEN: - Notify affected TO to reset SPS as system conditions warrant |
| SPS Posting | All SPSs are considered in-service unless otherwise notified by the TO. IF: - An SPS is taken out of service; THEN: - Post the information on MIS Public using Notice Builder. WHEN: - The SPS is placed back in service, THEN: - Cancel the message. Typical MIS posting: The [name] SPS has been taken out of service. |
| Status Change | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated, - “OPS Support Engineering” - “1 ERCOT System Operators” - “DAMTeam” |
| ### Remedial Action Plan (RAP) |  |
| 1 | TCM DOES NOT model RAPs when generating constraints so they tend to over-constrain at 100% of emergency rating instead of 100% of the 15min rating. - Activate constraints as necessary, - Lower the value in the % Rating column in TCM to tighten the constraint (minimum 95%), - Increase the value in the % Rating column in TCM to loosen the constraint (maximum 100%). |
| 2 | IF: - A RAP exists for the contingency; THEN: - Review the RAP with the associated TO, - Notify the Shift Supervisor of the anticipated actions. |
| 3 | IF: - A RAP is used to alleviate the identified problem regardless of the contingency listed on the RAP; THEN: - Make log entry. |
| 4 | IF: - The contingency anticipated by the RAP takes place; THEN: - Direct the implementation of the RAP, - Respond to requests made by the TO in accordance with the RAP, - If necessary, continue to use additional congestion management methods, - When the contingency clears, notify the TO as soon as possible. |
| LOG | Log all actions taken. |
| ### Pre-Contingency Action Plan (PCAP) |  |
| CAUTION | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. |
| 1 | WHEN: - RTCA shows a post-contingency overload and a PCAP exists to resolve it; THEN: - Review the PCAP with the associated Transmission Operator, - Notify the Shift Supervisor of the anticipated actions, - Direct the execution of the PCAP with the associated Transmission Operator. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing [TO] to implement the ****PCAP and [open/close] [breaker(s)]. [TO] please repeat this back to me. That is correct, thank you.” |
| NOTE | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 2 | IF: - Any PCAPs are still in use (reviewed each day between 0000 and 0500), AND - It is determined, in concurrence with the Shift Supervisor that it is no longer needed; THEN: - Direct the associated Transmission Operator to return the system to: - Its normal status, OR - Its status prior to implementation of the PCAP. |
| 3 | IF: - A RAP is used to alleviate the identified problem regardless of the contingency listed on the RAP; THEN: - Make log entry. |
| LOG | Log all actions taken. |
| ### Mitigation Plan (MP) |  |
| NOTE | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. - A MP is developed when there is not at least a 2% shift factor for a constraint to be solved in SCED, OR - A MP is developed when there is a 2% or greater shift factor for a constraint but SCED cannot fully solve the constraint - If a MP is used to alleviate the identified problem regardless of the contingency listed on the MP, make a log entry. |
| ≥ 2% Shift Factors Exists | IF: - SCED is unable to solve a contingency and at least a 2% shift factor exists; THEN: - Verify a MP or TOAP exists for the contingency, - Keep constraint active in SCED, - Review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the contingency with a ≥ 2% shift factor; THEN: - Coordinate with Operations Support Engineer to develop a MP - If contingency exists due to an outage, a TOAP should be developed (see TOAP procedure), - Keep constraint active in SCED, - Issue a Transmission Watch if the MP or TOAP is not developed within 30 minutes |
| < 2% Shift Factors | IF: - SCED is unable to solve a contingency and shift factor(s) are < 2%; THEN: - Verify a MP or TOAP exists for the contingency, - Do NOT activate the constraint in SCED - Review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the contingency with shift factor(s) < 2%; THEN: - Coordinate with the Operations Support Engineer to develop MP - If contingency exists due to an outage, a TOAP should be developed (see TOAP procedure) - Issue a Transmission Watch if the MP or TOAP is not developed within 30 minutes |
| TO Issue | IF: - Notified by a TO that it will take more time to implement the MP than is identified on the MP; THEN: - Notify the Operations Support Engineer to restudy and modify MP, - Log actions taken |
| Issue Watch | When issuing a Transmission Watch for an unsolved post-contingency overload (and waiting on MP or TOAP to be developed: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Post message on MIS Public using Notice Builder Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission Watch due to the post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] is being developed. [TO] please repeat this back to me. That is correct, thank you.” Typical MIS posting: At [xx:xx] a Transmission Watch was issued due to the post-contingency overload of [constraint name], a [mitigation plan/temporary outage action plan] is being developed. |
| Cancel Watch | When the MP or TOAP has been developed, cancel the Watch: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Cancel message on MIS Public using Notice Builder Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Transmission Watch for post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] has been developed. [TO] please repeat this back to me. That is correct, thank you.” |
| Contingency Occurs | IF: - The anticipated contingency takes place; THEN: - Direct (if necessary) the implementation of the MP or TOAP to the associated TO, - Respond as quickly as possible to requests made by the TO in accordance with the MP, - If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP. |
| LOG | Log all actions taken. |
| ### Temporary Outage Action Plan (TOAP) |  |
| NOTE | TOAPs are temporary since they are outage related - A TOAP is developed when there is not at least a 2% shift factor for a constraint to be solved in SCED, OR - A TOAP is developed when there is a 2% or greater shift factor for a constraint but SCED cannot fully solve the constraint |
| Planned Outage | IF: - A post-contingency overload is due to a planned outage on a transmission line(s) or a transmission facility; THEN: - Locate the TOAP in the Outage Notes, - Follow the same process as a MP outlined above. |
| Forced Outage | IF: - A post-contingency overload is due to a forced outage or planned outage not recognized by Outage Coordination on a transmission line(s) or a transmission facility; THEN: - Follow the same process as a MP outlined above. |
| LOG | Log all actions taken. |

## 5.1	Outages

Procedure Purpose:  Monitor and Respond to various types of equipment outages, both Transmission and Generation, in order to maintain reliability of the ERCOT Grid.

| Protocol Reference | 3.1.1 | 3.1.4.5 | 3.1.4.6 | 3.1.4.7 |
| --- | --- | --- | --- | --- |
|  | 3.1.5.1 | 3.1.6.10 | 3.1.6.11 |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-003 R1, R4 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT Operators can only make the following changes in the Outage Scheduler: - Remove actual start/end time if it is within 2 hours of the time the MP entered the outage, - Change status, - Add notes If a MP needs assistance or is unable to enter their outages, direct them to Outage Coordination. Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes. |
| NOTE | Forced Outages should be verbally communicated to ERCOT and must be entered into the Outage Scheduler if it is to remain an Outage for longer than two hours. |
| 1 | IF: - An Emergency Condition is declared; THEN: - Determine if Outages can be returned to service if causing negative impacts to reliability, - Make a Hotline call and post Emergency Notice message on MIS Public using Notice Builder. |
| ### Monitor Mode |  |
| 1 | IF: - Any outages, either planned or forced, that may require additional monitoring; THEN: - Mark the outages in the Outage Scheduler OS Monitored Outage display as deemed necessary, - Verify that the marked outages are in monitor mode, - Continue to monitor the marked outages. |
| ### Forced and Unavoidable Extensions |  |
| 1 | IF: - A Forced or Unavoidable Extension is received, review the outage details; THEN: - Monitor congestion and make appropriate changes as necessary, - Determine if it will have an effect on previously approved outages which may be to withdrawn. |
| ### Remedial Switching Action |  |
| Definition | “Remedial Switching Action” is a Forced Outage sub-type in the Outage Scheduler. ERCOT must approve all Remedial Switching Actions prior to implementation by TOs. |
| < 3 Days in length | Remedial Switching Actions are limited to a maximum of 3 days. |
| > 3 Days in length | If the Remedial Switching Action is required to remain active for longer than 3 days, a Planned Outage must be submitted to change the position of effected breakers and switches. |
| Approve | IF: - No issues identified; THEN: - Approve the Outage as received. |
| Reject | IF: - Reliability issues; THEN: - Notify Operations Support Engineer; - Reject the outage to ensure system reliability. |
| Restoration | Breakers and switches in a Remedial Switching Action must be able to be returned to their normal position within 4 hours or less (this allows for drive time for remote switches w/o SCADA). |
| Log | Log all appropriate information. |
| ### Maintenance Outages |  |
| Definition | When a Maintenance Outage is received, the Outage Scheduler will determine the correct Level the outage falls into: - Level 1- Equipment that must be removed from service within 24 hours to prevent a potential Forced Outage; - Level 2 - Equipment that must be removed from service within seven days to prevent a potential Forced Outage; and - Level 3 - Equipment that must be removed from service within 30 days to prevent a potential Forced Outage. |
| Verify Level 1 | IF: - A Maintenance Level 1 Outage is received, review the outage; THEN: - Run a study to determine if the outage will cause any reliability issues. |
| Approve Level 1 | IF: - No issues identified; THEN: - Accept the Outage as received. |
| Deny Level 1 | IF: - Reliability issues; THEN: - Coordinate the start of the outage with the TO to ensure system reliability as long as the outage is allowed to start within 24 hours. |
| Maintenance Level 2 and 3 Outages | IF: - Maintenance Level 2 and 3 outages are received; THEN: - DO NOT check the “Accept” box, - Place the outage in “Study” status, AND - Notify the Outage Coordination group by e-mail (“OPS Outage Coordination” distribution list). |
| Log | Log all appropriate information. |
| ### Consequential Outages |  |
| 1 | WHEN: - A TO enters the breaker and switch statuses associated with an Electrical Bus; THEN: - A downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus. |
| Evaluate | IF: - The TO has submitted the outage in the Outage Scheduler; THEN: - As time permits, perform a study to determine the effects the outage has on the ERCOT system and evaluate the request and verify the Outage meets the applicable requirements. |
| No Violations | IF: - NO, violations of applicable reliability standards exist; THEN: - Approve the request in the Outage Scheduler. |
| Yes Violations | IF: - YES, violations of applicable reliability standards exist; THEN: - Reject the request in the Outage Scheduler. |
| Log | Log all action taken. |
| ### Returning from Planned Outage Early |  |
| 1 | IF: - Notified by a TO or Resource Desk Operator that an outage is returning early from a Planned Outage; THEN: - Monitor congestion and make appropriate changes as necessary. |
| ### Guidelines for Withdrawal of an Outage |  |
| 1 | IF: - Security analysis and/or Operator experience indicates that an “Approved” or “Active” outage may have an adverse impact on system reliability; THEN: - Review the restoration time of the outage and if necessary, - ERCOT may withdraw the outage. |
| 2 | WHEN: - ERCOT withdraws an outage via the Outage Scheduler; THEN: - Enter an explanation in the “Reviewers Notes” listing the reliability concerns that caused the withdrawal, - Notify the following, by e-mail, as soon as possible: - OPS Outage Coordination - OPS Support Engineering - 1 ERCOT Shift Supervisors - Include the following information: - From Station – To Station (if applicable) - The planned Start and End date of the outage. |
| 3 | IF: - A TO or QSE reports that the outage in question has progressed to a point that withdrawal is not practicable within the outages designated restoration time; THEN: - Record this information in the “Outage Scheduler Reviewer’s Notes”, - Log the outage in the Transmission Security Log, - Inform the Shift Supervisor, - Continue monitoring system security, - Request Operations Support Engineer to develop Mitigation plan if necessary. |
| ### Approval of an Outage on Transmission Devices of More than one hour duration |  |
| 1 | IF: - A verbal request for permission to remove a transmission device from service for more than one hour is received; THEN: - Verify with the TO that the work being done will not prevent the device from being placed back in service immediately if needed, - As time permits, determine that such operation will not affect the reliability of the Transmission System, - If outage will cause reliability issues, go to Step 2 - If no impact to the system, go to 3. |
| 2 | IF: - System reliability is impacted; THEN: - Discuss with the TO the possibility of postponing the outage to a later time OR deny the request. |
| 3 | IF: - There is no reliability issue; THEN: - Verbally approve for the TO to remove a transmission device from service. - Instruct TO to make notification when device is place back in service. |
| Log | Log all appropriate information. |
| ### Simple Transmission Outage |  |
| NOTE | A Simple Transmission Outage is a classification of outage that can be removed from service without effecting LMP prices or causing congestion. The Outages are limited to the following 3 basic descriptions: - Expanded Bus Outage - Generator Breaker Maintenance - Open-ended Lines Refer to Desktop Guide Transmission Desk Section 2.2. |
| 1 | IF: - The outage meets the requirements of a Simple Transmission Outage, - Has been submitted between 1 and 2 days in advance, - Has a duration of the outage of 12 hours, AND - Has a less restoration time of 1 hour or less; THEN: - ERCOT will approve or reject within 8 business hours after receipt. |
| ### Opportunity Outages |  |
| Definition | An Outage that may be accepted by ERCOT when a specific Resource is Off-Line due to an Outage. |
| 1 | Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days. |
| 2 | When a Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, the Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled. The QSE must give as much notice as practicable to ERCOT. |
| 3 | Opportunity Outages of Transmission Facilities may be approved by ERCOT when a specific Resource is Off-Line due to a Forced, Planned or Maintenance Outage. A TO may request an Opportunity Outage at any time. |
| 4 | When an Outage occurs on a Resource that has an approved Transmission Facilities Opportunity Outage request on file, the TO may start the approved Outage as soon as practical after receiving authorization to proceed by ERCOT. ERCOT must give as much notice as practicable to the TO. |

# 6.	General Voltage Guidelines

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15 | 6.3.1 (1) | 6.3.2(2) | 6.5.1.1(a)&(c) |
| --- | --- | --- | --- | --- |
|  | 6.5.5.1(2) &(3) | 6.5.6 | 6.5.7 | 6.5.7.7 |
|  | 6.5.9.1(1)(c) | 6.6.7.1 | 6.7.6 |  |
| Guide Reference | 2.2.4 | 2.7.2(h)(ii) | 2.7.4.1(1) | 2.7.4.3 |
| NERC Standand | EOP-001-0 R4.2 | IRO-002-1 R6, R8 | IRO-005-2 R1.2, R1.3, R1.4 | NUC-001-2 R4.2 |
|  | TOP-002-2 R8, R10 | TOP-004-2 R6.2 | TOP-006-1 R2 | VAR-001-1 R1, R2, R4, R6, R7, R8, R9, R10, R12 |
|  | VAR-002-1 R3.1 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "normal" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS) Secure site. Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Voltage Tables | For Comanche Peak - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. For South Texas Project - System; - 345 kV. - Nominal Voltage; - 362.25 kV. - Tolerance; - +0% or -6.14%. - Maximum Voltage; - 362.25 kV. - Minimum Voltage; - 340 kV. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. When STP is in an alternate line up, the minimum voltage is 347 kV. When STP is in an alternate line up without the unit auxiliary transformer, the minimum voltage is 355 kV. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated in the voltage tables; THEN: - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate QSE. |
| ### Voltage Issues |  |
| NOTE | - Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Desktop Guide Transmission Section 2.9. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damages is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implemented and studies are performed showing that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. |
| 1 | WHEN: - Indicated by SCADA alarms, OR - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. |
| 2 | WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct a QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| Exceed URL | For multi-generator busses, ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL until all On-Line Generation at the same transmission bus have been instructed to their respective CURLs or URLs. IF: - Instructing a QSE’s Generation Resource to exceed its Unit Reactive Limit (URL); THEN: - Issue a VDI to the QSE for exceeding the URL (Exceed URL VDI). The VDI must include the following: - Resource name - Specific voltage set point. - Start time - End time - Choose “HOLD X VOLTAGE LEVEL” as the Instruction Type from Resource level - Notify Operations Support Engineer of instruction, they will be providing analysis to Settlements. |
| Reduce MW | IF: - MW output must be reduced to follow a voltage support instruction; THEN: - Issue a VDI to the QSE providing Voltage Support Service (VSS VDI). The VDI must include the following: - Resource name - MW level at time of instruction - MW level Resource needs to move to for Voltage Support - Start time - End time - Choose “STAY AT/ABOVE X MW/MVAR LEVEL” or “STAY AT/BELOW X MW/MVAR LEVEL” as the Instruction Type from Resource level - Notify Operations Support Engineer of instruction, they will be providing analysis to Settlements. |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| NOTE | The North – Houston VSAT voltage stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure section 4.4. |
| Valley Import | WHEN: - VSAT runs and provides an updated limit for the Valley Import; THEN: - Update RTMONI and TCM. |
| 1 | IF: - VSAT has not run in the last 45 minutes, OR - VSAT is indicating “Abnormal”, “Unavailable”, or “Partial” status; THEN: - Rerun the RTNET, RTCA, and RTDCP (VSA). If no change, then: - Notify the Shift Supervisor and Operations Support Engineer - As deemed necessary make the following Hotline call. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is experiencing problems with the Voltage Stability Analysis program. Maintain voltage levels as required by your procedures and notify ERCOT of any voltage issues within your system. [TO] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margin listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) more frequently than the periodic scheduled VSAT run. - Confirm VSAT indicates either “Normal” or “Pending”. Reliability Margin Table. Scenario Name; Safety Margin. O-DFW_L; 200MW. O-CORP_L; 75MW. O-VAL_L; 75MW. O-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. For N-H_G and N_H_L: Refer to section 4.4 North-Houston Voltage Stability Limit of this procedure. |
| 3 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the Extra-Interface Limit pre-contingency value is less than the Safety Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 4. |
| 4 | Determine the contingency status in RTCA (solved/unsolved).IF: - Solved, - Have Operations Support Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Operations Support Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct RUC Operator to commit additional resources in the weak bus area that are available. |
| 5 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 6 | Determine if the Extra-Interface Limit pre-contingency value is greater than the Reliability Margin Value. IF: - The Extra-Interface Limit pre-contingency value is greater than the Reliability margin; THEN: - No further action is required. OR IF: - The Extra-Interface Limit pre-contingency value is less than the Reliability margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 4. If no additional generation is available, continue. |
| 7 | IF: - No additional generation is available; THEN: - Notify Operations Support Engineer to create a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT. |
| NOTE | Operations Support will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > AVR AND PSS Status |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, - Notify the appropriate TO of the change in status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “OPS Advanced Network Applications” - “1 ERCOT System Operators” |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 9 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect System reliability and may require more Resources. - When extreme cold weather is 5 days away and daily temperatures are forecasted to remain 32°F or below in the three largest weather zones. - When an approaching Hurricane / Tropical Storm is approximately 5 days away. Unplanned Transmission Outages that may impact System reliability. - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness. |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away. - When extreme cold weather is 3 days away and daily temperatures are forecasted to remain 32°F or below in the three largest weather zones. - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term operating reliability. - ERCOT may exercise its authority, in such circumstances, to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead in accordance with procedures. - When weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows. - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions. - Loss of communications or control condition is anticipated or significantly limited. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect System Reliability. - When an approaching Hurricane / Tropical Storm is approximately 1 day away. - When extreme cold weather is 1 day away and daily temperatures are forecasted to remain 32°F or below in the three largest weather zones. - When temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones or when temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties. - Conditions have developed such that additional Ancillary Services are needed in the Operating Period. - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM. - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations. - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations. - The need to immediately procure Ancillary Services from existing offers. - ERCOT may instruct TOs to reconfigure ERCOT System elements as necessary to improve the reliability of the ERCOT System. - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request. - ERCOT varies from time-line for DAM/DRUC. |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution. - Loss of Primary Control Center Functionality. - Load Resource deployment for North-Houston voltage stability. - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market. - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options. - A transmission condition has been identified causing unreliable operation or overloaded elements. - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists. - ERCOT has determined a fuel shortage exists that would affect reliability. - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED). - When extreme cold weather is beginning to have an adverse impact on the ERCOT System. |
| ### Scripts |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on the MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| Version: 1 | Revision: 8 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted, QSEs should be notified via Hotline call (see 2b for typical script). - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC falls < 2300 MW; THEN: - Using the Hotline, notify all TOs to implement EEA 1. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is declaring EEA 1 due to Physical Responsive Capability is below 2300 MW. [TO] please repeat this back to me. That is correct, thank you” After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 2. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Relax transmission constraints to provide additional generation at the expense of temporarily creating a security violation as long as the violation does not physically overload any single Transmission Element above its emergency rating. |
| NOTE | The Load Management Program step below is only to be considered on weekdays (except holidays) during the summer months (June to September) between 1330 and 1900 hours due to restrictions in TO Load Management Program contracts. |
| Load Management Program | Monitor predicted load increase over the next hour and into the peak hours as indicated in the prevailing ERCOT Load Forecast. IF: - The current time is AT LEAST 13:30 BUT NOT AFTER 16:00, and - It is predicted that this event will proceed to EEA level 2; THEN: - Using the Hotline, contact all TOs with Load Management Programs, requesting implementation of their Load Management Programs. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; This call applies to the following Transmission Operators: Oncor, Centerpoint, AEP, and TNMP. At [xx:xx], ERCOT is requesting that these TOs deploy all available capacity from their Load Management Programs due to continued increased load growth. [TO] please repeat this back to me. That is correct, thank you.” |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC falls < 1750MW; THEN: - Using the Hotline, notify all TOs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. - If the energy conservation call has not been made previously, it can be combined with this call (see step Media Appeal below). Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2; - [Load Resources and/or EILS] have been deployed, - Reduce customer loads by using distribution voltage reduction measures, if deemed beneficial - *Request deployment of Load Management Programs [TO] please repeat this back to me. That is correct, thank you” * Only applies during the summer months (June to September) and if not already deployed in. After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 3. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Media Appeal | - Unless already in effect, verify with the shift supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify TOs, via Hotline, that a media appeal for conservation is in effect. Typical Script: “This is ERCOT Operator [first and last name]; ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Using the Hotline, notify all TOs to implement EEA 3 and any measures associated with EEA 1 and 2, if not already implemented - *Request deployment of Load Management Programs * Only applies during the summer months (June to September) and if not already deployed. Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3. ERCOT is directing all Transmission Operators to shed their share of [amount] MW. Transmission Operators are to report to ERCOT when this is complete. [TO] please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R4.1, R4.4 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1375 MW; THEN: - Using the Hotline, notify all TOs of firm load restoration. Typical Script when only restoring a portion of the firm load: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is directing all Transmission Operators to restore their share of [amount] MW leaving [amount] MW still off. Report to ERCOT when this task is complete. [TO] please repeat this back to me. “That is correct, thank you.” OR Typical Script when restoring all firm load: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], “at [xx:xx], ERCOT is directing all Transmission Operators to restore all firm load. Report to ERCOT when this task is complete. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load has been instructed to be restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 3 to EEA 2: - Notify the TOs that [Load Resources or EILS] are being restored Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 3 to EEA 2. [Load Resources or EILS] are being recalled. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW AND - All Load Resources or EILS have been instructed to be restored; THEN: - Using the Hotline, notify all TOs of the reduction from EEA 2 to EEA 1 and Load Resources or EILS have been instructed to restore, - If distribution voltage reduction measures were used, restore - If BLTs were implemented, restore - *If Load Management Programs were deployed, restore Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2 to EEA 1, [Load Resources and/or EILS] are being restored. Distribution voltage measures can be returned to normal, if used, *as well as Load Management Programs. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The System can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Using the hotline, notify all TOs of the termination of EEA. Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is terminating EEA 1, a Watch still remains in effect. [TO] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Cancel Watch |  |
| 1 | WHEN: - Requested by the Real-Time Operator - ; THEN: - Cancel Watch Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. Physical Responsive Capability is now above 2500 MW. [TO] please repeat this back to me. That is correct, thank you.” |

## 7.4	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 (8) | 6.5.1.1 | 6.5.3 | 6.5.5.2(1) |
| --- | --- | --- | --- | --- |
|  | 6.5.7.1.10 | 6.5.7.1.11(1) |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001 R1, R4.2 | IRO-002 R6 | IRO-003 R1 | IRO-004 R3 |
|  | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 |  |  |

| Version: 1 | Revision: 5 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Transmission Issues within ERCOT |  |
| 1 | IF: - Post-contingencies or unsolved contingencies cannot be corrected with congestion management techniques or committing additional Resources; THEN: - Determine if there are export schedules over the CFE Ties that would help alleviate the situation if curtailed (which includes reductions). - Notify the ERCOT DC Tie Operator to curtail the schedule(s), specifying the time and MW amount, - Issue a Transmission Watch - Make Hotline call to TOs - Posting message on MIS Public using Notice Builder - Notify Real-Time Desk to make Hotline call to QSEs Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission Watch due to the post contingency loss of (name of contingency) overloads (name of overloaded element) resulting in curtailment(s) over the [name] DC-Tie.” [TO] please repeat this back to me. That is correct, thank you.” Typical Posting: Export schedule(s) to CFE on DC-Tie [Tie name(s)] was curtailed due to the post contingency loss of (name of contingency) overloads (name of overloaded element). Edit script as needed to fit situation. |
| 2 | WHEN: - Committing a Resource by electronic VDI; THEN: - Issue a VDI to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct VDI. |
| LOG | Log all actions taken. |
| ### Transmission/Capacity Issues within CFE |  |
| 1 | IF: - Notified by AEP TO that CFE is unable to maintain reliability and needs to curtail an E-Tag; THEN: - Verify the MW amount, tie and time of the curtailment, - Notify ERCOT DC-Tie operator with information. - Post message on MIS Public using Notice Builder Typical Posting: Import schedule(s) from CFE on DC-Tie [Tie name(s)] was curtailed due to reliability issues within CFE. Edit script as needed to fit situation. |
| 2 | IF: - Notified by AEP TO that CFE is requesting emergency energy; THEN: - Determine which DC-Tie(s) and amount being requested, - Determine or have Operations Support Engineer determine that sending emergency energy to CFE would not put ERCOT in an emergency condition IF: - ERCOT is able to send CFE emergency energy; THEN: - Notify ERCOT DC Tie Operator with information and request they issue a VDI to AEP TENASKA QSE (QAEPS2). |
| 3 | WHEN: - Notified by AEP TO that CFE no longer is in need of emergency energy; THEN: - Notify the ERCOT DC Tie Operator with information. |
| LOG | Log all actions taken. |

## 8.1	Hurricane / Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 4 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov) |
| NOTE | Operations Support will analyze the situation and make recommendations as to Resource requirements and transmission topology. |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. Coordinate with Outage Coordination for the review of planned and existing outages to be rejected and/or restored. Using the Hotline, issue an OCN to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for a [Tropical Storm/Hurricane] [Name] due to a probability of making landfall in the ERCOT Region. TOs are instructed to: - Review planned and existing transmission outages to be withdrawn and/or restored - Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. Using the Hotline, issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is currently projected to impact the ERCOT Region. TOs are instructed to: - Review planned and existing transmission outages to be withdrawn and/or restored. - Review emergency operating procedures, evacuation plans, and the possible need to staff backup facilities. - Test communication with other TOs and QSEs prior to the hurricane making landfall. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. Using the Hotline, issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is expected to make landfall near [Place] at [time]. TOs are instructed to: - Be prepared to lose load and expect high voltage conditions - Keep ERCOT informed of transmission outages. ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency | When Hurricane/Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to [Tropical Storm/Hurricane Name] having an adverse impact on the ERCOT System [specify condition]. TOs are instructed to: - Be prepared to lose load and expect high voltage conditions - Keep ERCOT informed of any issues ERCOT will continue to monitor the Storm. [TO] please repeat this back to me. That is correct, thank you.” |
| Post | Coordinate with the Real-Time Operator for the posting of the notices on MIS Public using Notice Builder. |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

8.2	Extreme Cold Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for extreme cold weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 4 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme cold weather notifications are called when the daily temperatures are forecasted to remain 32°F or below in the following weather zones: - North Central (NORTH_C) - South Central (SOUTH_C) - Coast (COAST) |
| OCN |  | When approaching extreme cold weather is approximately 5 days away, using the Hotline issue an OCN to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for an extreme cold weather system approaching in the next 5 days with temperatures anticipated to remain 32°F or below in the three largest weather zones. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review and implement weatherization and emergency operating procedures, including winterization procedures. Notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the extreme cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory |  | When approaching extreme cold weather is 3 days away, using the Hotline issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme cold weather system approaching in the next 3 with temperatures anticipated to remain 32°F or below in the three largest weather zones. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review and implement weatherization and emergency operating procedures, including winterization procedures. Notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the extreme cold weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch |  | When approaching extreme cold weather is 1 day away, using the Hotline issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme cold weather system approaching tomorrow. Temperatures are expected to remain 32°F or below in the three largest weather zones. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Prepare for higher than usual loads, - Review and implement weatherization and emergency operating procedures, including winterization procedures. Notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the extreme cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency Notice | When extreme cold weather has arrived and is beginning to have an adverse impact on the ERCOT System, using the Hotline issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme cold weather system is beginning to have an adverse impact on the ERCOT System such as [state what the adverse impacts are]. - Prepare for higher than usual loads and the possibility of load shedding. ERCOT will continue to monitor the extreme cold weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |  |
| Post | Coordinate with the Real-Time Operator for the posting of the notices on MIS Public using Notice Builder. |  |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on MIS Public. |  |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |  |

## 8.3	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for Extreme Hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 2 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| OCN |  | When extreme hot weather is forecasted approximately 5 days away, using the Hotline issue an OCN to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Advisory |  | When extreme hot weather is forecasted approximately 1 to 3 days away, using the Hotline issue an Advisory to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the weather system. [TO] please repeat this back to me. That is correct, thank you.” |
| Watch |  | When extreme hot weather is projected for next day or current day and ERCOT has reliability concerns, using the Hotline issue a Watch to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme hot weather with is forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones [today or tomorrow]. ERCOT is expecting statewide power supplies to be very tight. TOs are instructed to: - Review Planned outages and existing outages for the possibility of withdrawing or restoring equipment, - Prepare for higher than usual loads, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the weather and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |
| Emergency Notice | When extreme hot weather has arrived and is beginning to have an adverse impact on the ERCOT System, using the Hotline issue an Emergency Notice to all TOs: Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme hot weather system is beginning to have an adverse impact on the ERCOT System such as [state what the adverse impacts are]. - Prepare for higher than usual loads and the possibility of load shedding. ERCOT will continue to monitor the extreme hot weather system and will convey information and directives as conditions warrant. [TO] please repeat this back to me. That is correct, thank you.” |  |
| Post | Coordinate with the Real-Time Operator for the posting of the notices on MIS Public using Notice Builder. |  |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on MIS Public. |  |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |  |

## 8.4	Other Significant Weather Events

Procedure Purpose:  Monitor severe weather conditions which can arise with little or no warning that can have an impact on the ERCOT grid.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 4 | Effective Date: May 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight line winds - Hail - Severe lightening - Flooding |
| OCN/ Advisory/ Watch | When a significant weather event that could or does impact the ERCOT Region, make the proper notification. Using the Hotline, issue a notification to all TOs: Typical Script: “This call is requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [OCN/Advisory/Watch] due to [type of weather event] in the [location on the grid]. If you experience any issues as a direct result of the weather event, notify ERCOT. |
| Post | Coordinate with the Real-Time Operator for the posting of the notices on MIS Public using Notice Builder. |
| Cancel Posting | Coordinate with the Real-Time Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | - / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT)Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 2.1 2.3 3.4 4.1 4.2 7.4 10.1 | 1.0 / 1 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 13 1.0 / 5 1.0 / 3 1.0 / 2 | Updated Scope Changed TSP to TO Updated database load script Changed insecure state to emergency condition Updated 1st Note, steps 6 & 8 in Post Contingency Overloads, steps 2 & 3 in Managing Constraints in SCED, added Model Inconsistencies/Updates procedure Updated Notes 1 & 2, Steps 1 & 2 Changed insecure state to emergency condition Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 3.3 4.1 4.2 4.3 4.4 4.54.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.5 9.2 10.1 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 14 1.0 / 6 1.0 / 8 1.0 / 7 1.0 / 6 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 8 1.0 / 7 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated Operations Support Engineer Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, added 3rd Note, updated step 1 in Review Planned Outage Notes, steps 1, 2, 3, 4, 6, 7, 8, 9 & QSGR in Post Contingency Overloads, step 2, 4 & Log in Managing Constraints in SCED Updated Operations Support Engineer Updated Operations Support Engineer & step 1, 2 & 3 Updated Operations Support Engineer Updated Desktop Guide reference, 2nd Note, step 5 & SPS Posting & deleted step 4 in SPS, all steps in Mitigation Plan & Temporary Outage Action Plan Updated Desktop Guide reference Updated step 1 in Watch Updated TSP to TO, Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, changed TSP to TO, Desktop Guide reference & step 1 of Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Watch Updated step 1 in Implement EEA Level 1 & step 1 in Implement EEA Level 3 Updated script in step 1 in Restore Firm Load Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer & Desktop Guide reference Updated Desktop Guide reference Updated all steps in Telemetry Issues that could affect SCED and/or LMPs, step 1 in Backup/Alternate Control Center Transfer & Operations Support Engineer | March1, 2012 |
| 3.1 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.2 8.3 8.4 | 1.0 / 3 1.0 / 7 1.0 / 15 1.0 / 9 1.0 / 8 1.0 / 7 1.0 / 4 1.0 / 9 1.0 / 9 - / 8 1.0 / 8 1.0 / 5 1.0 / 4 1.0 / 0 1.0 / 4 1.0 / 2 1.0 / 4 | Updated step Gap Study Added TSAT Updated step 4 & deleted step 9 in Post-Contingency Overloads, clarified step 2 & 3 in Managing Constraints in SCED, Added Unsolved Contingencies Updated for TSAT tool, added Managing W-N during System Failures Updated step IROL and ‘instructing’ to ‘directing’ Updated step Status Change & ‘instructing’ to ‘directing’, updated step 3, 4 & log in RAP, added step 3 and log in PCAP, update Note, added TO Issue in MP Updated Opportunity Outage procedure Added Valley Import to VSAT procedure, deleted step 2 in PSS/AVR section Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather Added Load Management Programs in Implement EEA Added Load Management Programs in Restore EEA Updated for NPRR405 Changed ‘TDSP’ to ‘TO’ & T/S Operator to Real-Time Deleted Cold Weather Revised to 8.2 and changed Severe Cold Weather to Extreme Cold Weather Revised to 8.3, added OCN & Emergency Notice Revised to 8.4 and changed T/S Operator to Real-Time Operator | May 1, 2012 |