## Power Operations Bulletin # 602

ERCOT has posted/revised the Reliability Unit Commitment Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 1.1	Purpose

This procedure provides the System Operator assigned to the Reliability Unit Commitment (RUC) Desk with detailed Procedures required for performing the duties assigned to that position.  The RUC Desk is responsible for the oversight of the WRUC, DRUC, and HRUC market operation within ERCOT.  The RUC Desk is responsible for ensuring that the RUC Market is facilitated and closed according to ERCOT Protocols and procedures.  The RUC Desk also coordinates with the Real-Time Desk, Transmission and Security Desk, Resource Desk, Operations Support Engineer, Shift Supervisor and other ERCOT operators as necessary to maintain grid reliability.  The RUC Desk also responds to QSE’s inquiries about the RUC commitments and other related tasks.

The Weekly Reliability Unit Commitment (WRUC) process is an eight-day (not including the current Operating Day; i.e., the time for which ERCOT has a COP and Load Forecast) look-ahead planning tool that is used to help ERCOT manage Generation Resources having start up times longer than the DRUC or HRUC study periods as well as project the transmission congestion for the next seven days.  The WRUC process will be executed by the Operator each day at 02:00.  The WRUC does not send commitment and dispatch instructions to QSEs.

The Day-Ahead Reliability Unit Commitment (DRUC) process runs for each hour of the next operating day.  It normally commences at 14:30 on the day prior to the operating day and normally completes at 16:00 on the day prior to the operating day.

The Hourly Reliability Unit Commitment (HRUC) process will be run every hour for each hour of the rest of the current day and the next operating day after 18:00 or if DRUC for the next Operating Day has run, or else it runs for only the rest of the current day.

## 1.2	Scope

The instructions contained in these procedures are limited to those required for the RUC Desk.  Instructions for other ERCOT Control Room positions are contained in separate procedures, one for each position.  These Procedures do not imply that the duties contained herein are the only duties to be performed by this position.  The individual assigned to this position will be required to follow any other instructions and perform any other duties required or requested by appropriate ERCOT Supervision.  Although the steps within the procedures are numbered, the numbering is for indexing purposes and are not sequential in nature.  The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions.

## 1.3	Roles/Responsibilities

ERCOT System Operator, Reliability Unit Commitment Desk

The ERCOT System Operator – Reliability Unit Commitment Desk position represents the following NERC functional entities collectively for the ERCOT ISO at any time:

  - Reliability Coordinator.

  - Balancing Authority

  - Transmission Operator

  - Interchange Coordinator

This representation includes the responsibility and clear decision making authority during normal and emergency conditions to direct and implement real-time actions to ensure the stable and reliable operation of the ERCOT Electric Grid. These actions shall include shedding of firm load without obtaining approval from higher-level personnel.

## 2.3	Publish A/S Requirements and Review System Conditions

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

| Protocol Reference | 4.2.1.1 | 4.2.1.2 | 4.2.3 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0b | TOP-002-2 R1, R5 |  |  |

| Version: 1 | Revision: 8 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Review and update A/S Requirements must be completed prior to 0500. - The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month. |
| ### Review Weather Data Information |  |
| 1 | REVIEW the Weather Data for the next operating day in the EMS. |
| 2 | REVIEW REFERENCE DISPLAY: EMS Applications>Weather Details>Real Time Displays>Weather Forecast Directory The Meterlogix phone number is (952) 882-4312. IF: - The Last Weather Source Update or Last Weather Read is less than one (1) hour old; THEN: - Using the usual sources, review the weather forecast for at least two days out. IF: - The data update or read is more than one (1) hour old; THEN: - Notify the Shift Supervisor and the Help Desk. |
| 3 | Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems. The trigger will usually be an extreme weather event which will cause temperatures to be below freezing for an extended period of time, though there could be other reasons. It may be necessary to consider fuel switching and optimize fuel supply if a reliability issue exists. |
| Fuel Switching | IF: - Notified of fuel limitations; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider fuel switching options (gas to oil) if capability exists. |
| Optimize Fuel Supply | IF: - A particular fuel supply is at risk; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider committing Resources with fuel that is not at risk. |
| ### Review and Select Load Forecast |  |
| 1 | - Review and Select load forecast for next day (Refer to Desktop Guide RUC Section 2.17. |
| NOTE | The Net Error Load Forecast Adjustment is scheduled based on the current AS methodology. If ERCOT subtracts a MW value from the load forecast during the month additional Non-Spin will be procured. |
| ### Publish A/S Requirements |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| ### Increasing A/S Requirements before A/S Obligations Publish |  |
| NOTE | This procedure would be performed when it has been determined that additional A/S is needed, such as to support a weather event. |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, increase the hourly ERCOT system total A/S requirements for each requirement needed for each hour of the next operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| 3 | IF: - The A/S requirements were increased, THEN: - The next day will copy the new A/S requirements unless you return the A/S requirements to the A/S Plan requirements for the month. REFERENCE DISPLAY: - Market Participation > Physical Market > AS Market > AS Plan Before 04:00 update the A/S requirements. |
| NOTE | Refer to the A/S requirements for the current month’s A/S Plan if no changes are required. |
| ### Priority Outages |  |
| 1 | A Priority Outage is one that affects generation. Prior to 1200: - From a review of the Outage Notes for the next Operating Day, make lists of Priority Outages, sorted by affected Transmission Operator, - The file is located in P:\DAY AHEAD – TDSP PRIORITY OUTAGE NOTIFICATION, - Print copies, - Fax the lists to the respective TOs accompanied by a request that within 30 minutes of the Actual Start and Actual End times of these Priority Outages, they enter the Actual Start and Actual End times in the Outage Scheduler, - Place in Daily Log File. |
| ### Verification of Published A/S Requirements |  |
| NOTE | This step may be completed after 0600. |
| 1 | VERIFY by spot-checking the following information posted to the ERCOT Market Information System (MIS) for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - MIS; Grid; Transmission; Transmission Outages; Approved and Accepted Transmission Outages - Weather assumptions used to provide the system conditions forecast. - MIS; Markets; Day-Ahead Market; Day-Ahead Public Information; Weather assumptions - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, and Non-spinning Reserve – NSPIN. - MIS; Markets; Day-Ahead Market; Ancillary Service Plans; DAM Ancillary Service Plan. |
| Log | LOG any significant problems including any action taken. |

## 3.1	Tasks prior to Execution of HRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit/de-commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.1 | 5.5.2(5) |
| --- | --- | --- | --- | --- |
|  | 5.5.2(9)(b) | 5.3(3) | 6.3.1(1) | 6.3.2(2) |
|  | 6.3.2(3)(a) | 6.4.1 | 6.4.2.5(3)(b) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 & R11 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Tasks prior to execution of HRUC |  |
| NOTE | The RUC Study Period for DRUC is the next Operating Day. The RUC Study Period for HRUC is the balance of the current Operating Day plus the next Operating Day if the DRUC for the Operating Day has been solved or after 18:00 if DRUC did not solve. |
| Continuous Monitoring | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow IF: - The EMSI Workflow Parameters does not indicate EMSI has run in the last hour and Load Forecast are NOT running (should be continuous); THEN: - Open EMSI Workflow, select “Start up”. When start up is complete, select “Run”. IF: - EMSI Workflow does not complete; THEN: - Notify Helpdesk and Control Room staff. |
| Load Forecast | Periodically monitor the Load Forecast to ensure it is accurate: IF: - Adjustments need to be made, they will be done in the EMS and updated to the MMS; THEN: - Adjust (Refer to Desktop Guide RUC Section 2.17). |
| Wind Forecast Updates | Periodically monitor the Wind Forecast and verify data is updating: IF: - Wind forecast is not updating; THEN: - Notify Supply Integration & Grid Application group, - Be aware that this could skew HRUC results. |
| RMR Consideration | IF: - An RMR unit needs to be considered in HRUC; THEN: - Ensure COP status is “OFF”. IF: - An RMR unit is needed but is not to be considered in HRUC; THEN: - Commit unit before HRUC is executed. |
| COP Validation | REVIEW REFERENCE DISPLAY: Market Participation>Monitoring>Event Manager>Events>filter Event Name for COP Validation IF: - A Resource Forced Outage has occurred and the QSE has not update their COP, OR - COP Validation ERROR; THEN: - Select “START-NOW" in the Status column, - Be aware that the results may be skewed and determine the need for procuring equivalent MW capacity elsewhere. |
| Review AS Differences | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>SASM Market>AS Responsibility – QSE Market Participation>Monitoring>Event Manager>Events IF: - AS Differences exist; THEN: - Notify the Resource Operator. |
| Bad/Suspect Telemetry | Periodically monitor: IF: - Notified of bad/suspect telemetry; THEN: - Determine if issues will be resolved for next HRUC run, - Discuss with Shift Supervisor if the HRUC should be run or delayed until the issues can be resolved, - Consider requesting Operations Support Engineer to manual over-ride SCADA values (be aware that this could skew the results), - If it is determined to delay HRUC, follow the “HRUC Failure/Timeline Deviation” procedure. |
| E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS: IF: - Individual schedules need to be reviewed; THEN: - Go to the MI COP display and filter ‘ERCOT’ as the QSE name. |
| Verify | REVIEW REFERENCE DISPLAYS: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>HRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” |
| DSI | EXECUTE: - The DSI sequence; VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact Help Desk immediately to determine the cause and expected time of resolution. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes> DSI Operator Manual Commitment Market Operations>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data> MF Generator Parameter IF: - An RMR unit is needed but was not picked up in DAM, OR - Is not to be considered in HRUC; THEN: - Commit unit before HRUC is executed. IF: - Additional resources are needed to solve for transmission congestion; THEN: - Consult with the Operations Support Engineer and/or the Transmission and Security Desk Operator to determine which resources should be committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods; THEN: - Change ‘blank’ to ‘Commit’, - List reason. |
| Deselect Contingencies | IF: - It has been determined with the help of Operations Support Engineer that a contingency known to cause errors or that otherwise result in inconclusive study output in RUC; THEN: - After the Operations Support Engineer has deselected the contingency, - Post to the MIS Secure Area contingency that was deselected with the reason and no later than one hour after deselection. |
| NOTE | If a RMR unit was committed in DSI Operator Manual Commitment and it is the only change since the DSI was last run the next step is not necessary. |
| Verify | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the HRUC input data; CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No”, OR - “Use Save case set to “Yes” |
| ### Verify HRUC executed at XX: 03 |  |
| 1 | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages Verify execution of the HRUC sequence. |

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 3.9(7) | 3.9.2(4)&(5) | 5.1 (7)&(9) | 5.3(3) |
| --- | --- | --- | --- | --- |
|  | 5.5.1(11) | 5.5.2 | 5.5.3 | 6.3(1) |
|  | 6.3.1(1) | 6.3.2(2) | 6.4.8.1.2 | 6.4.8.1.3 |
|  | 6.5.9(2) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2 R1 & R11 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.15 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages - Monitor the HRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published. IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for HRUC are invalid, - Notify the Manager or designee immediately, - ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: - The load forecast is not reasonable for each hour; THEN: - Be aware that this could skew the HRUC results, IF: - Any under/over generation exists that HRUC could not resolve; THEN: - Notify Control Room staff. |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on WGR’s or Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue an electronic VDI (priority should be given to WGRs and Resources that resolve congestion - Choose “DECOMMIT” as the Instruction Type from Resource tab - Enter “ERCOT requested decommit/capacity surplus” in Other Information. |
| QSE’s Request to Change Resource supplying A/S | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: - Undeliverable Ancillary Service are indicated; THEN: - Notify the Resource Desk Operator. |
| A/S Insufficiency from SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - A/S Insufficiency; THEN - If deemed necessary, commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, - Refer to Desktop Guide RUC Section 2.18. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints; THEN: - Notify the Resource Desk. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually commit resources as needed Refer to Desktop Guide RUC Section 2.14. |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: - HRUC recommends the commitment of any unit; THEN: - Determine the validity, - Determine the temporal constraints for each of the units. IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason (evaluate later), IF: - There is a reliability reason requiring the resource commitment decision to be made immediately; - Resources returning from outages - Congestion or Capacity deficiencies that are creating HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, uncommitting, examples below: - Evaluate later - Voltage issue - SLWSCRL5 (constraint name) |
| RMR Resources | QSEs will show a COP status of OFF when Resources are available. RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| RMR Commitment | WHEN: - HRUC recommends a RMR unit, AND - A capacity reserve shortage is projected and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; THEN: - Determine if an RMR Resource will need to be considered in HRUC Study Period; ISSUE: - Watch for projected reserve capacity shortage with no market solution; THEN: - Ensure COP status is “OFF” and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event; SELECT: - Commit Resource before HRUC is approved - Commit Resource, - List reason (RMR for Capacity). |
| Hotline | Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed during a HRUC study. [QSE] please repeat this back to me. That is correct, thank you.” Ask Transmission Operator to make Hotline call to TOs. |
| Post | Typical MIS posting: ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. |
| Cancel | Cancel Watch once RMRs are off-line by making hotline call to QSEs and cancelling the posting. Ask Transmission Operator to make hotline call to TOs. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: - Additional resources are needed to solve for transmission issues (such as for voltage issues) and were not picked up in the HRUC run; THEN: - Commit unit before HRUC is approved - Change ‘blank’ to ‘Commit’, - List reason (constraint name or voltage issue). |
| NOTE | - Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. - ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. - If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. - QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If HRUC recommends decommitments; Determine if: - Outage related, - Possible Network Model error/ Normal Breaker status variances, - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort, THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |
| ### VSAT and RUC perform full AC analysis of all contingencies |  |
| NOTE | IF: - RUC cannot complete the process; THEN: - Notify the Transmission & Security Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - External Input data - UC Displays - Input Display Menu - System TCG Data & System Load |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The HRUC results are reasonable and after all necessary modifications have been made; THEN: - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button, AND - Follow the Manage HRUC Timeline Failure in the next section. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>HRUC> HRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>HRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue VDIs to cancel RUC instructions |
| Log | Log actions taken. |

## 3.3	HRUC Failure/Timeline Deviation

Procedure Purpose:  To address situations in which the HRUC process has failed.  Failures can be identified by software failure, results not approved in a timely manner or certain Emergency conditions.

| Protocol Reference | 6.5.9.3.4 (2)(d) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 | IRO-001 R9 |  |  |

| Version: 1 | Revision: 7 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### HRUC Failure/Timeline Deviation |  |
| Failure | IF: - HRUC solved with invalid solution, - Time does not allow for full review of results, OR - HRUC software fails without expectation of timely repair; THEN: - Notify Help Desk and Control Room Staff, - Issue an Emergency Notification by making a Hotline call and posting on MIS Public using Notice Builder. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to HRUC not completing for [state HE] due to [failure or timeline deviation]. HRUC is expected to meet the timeline for next hour, upon completion the Emergency Notice is deemed canceled. [QSE] please repeat this back to me. That is correct, thank you.” |
| Create Save Case | IF: - HRUC is aborted or shut down; THEN: - Go to display System Administration > Savecase Management. - Choose File Type as HRUC. - Fill in File Name (no spaces allowed) - Fill in Description. - Push Create Button. - The message will show up in the Text field. - Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Also refer to Desktop Guide Common to Multiple Desks Section 2.15, if needed. |
| NOTE | IF: - HRUC is having trouble solving in the required timeline due to transmission/capacity violations in the study; THEN: - Have Operations Support Engineer check validity of violation AND if correct, - Consider committing Resource(s) sooner instead of waiting to evaluate later. |
| Commit/ De-Commit Resources By VDI | IF Needed: - Commit/De-Commit Resources by issuing, VDIs for the following: - Choose COMMIT or DECOMMIT as the Instruction Type from the RES Level, - Enter reason (capacity, capacity surplus or contingency name) in “other information” |

## 4.2	Tasks prior to Execution of DRUC

Procedure Purpose:  To make manual corrections for bad/suspect telemetry, load forecast modifications, or to commit Resources prior to running the RUC process.

| Protocol Reference | 3.12.1(3) | 5.1 | 5.5.1 | 5.5.2(5) |
| --- | --- | --- | --- | --- |
|  | 5.5.2(9)(b) | 6.3.1(1) | 6.3.2(3)(a) | 6.4.2.5(3)(b) |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### By 13:00 each day, perform the following |  |
| COP | REVIEW REFERENCE DISPLAYS: Market Participation>Physical Market>Market Operator Data> Missing COP Check Market Participation>Monitoring>Event Manager>Events VERIFY: - “Missing COP Check” has automatically notified the QSEs of missing COPs; SELECT: - “START-NOW" in the Status column if not already completed by Market Operations. |
| Load Forecast | Review the Day Ahead Load Forecast in the EMS IF: - Adjustments need to be made in the EMS; THEN: - Adjust using the following: (Refer to Desktop Guide RUC Section 2.17) Reference Displays: - Load Forecast - Similar Day Function - Load Forecast Scaling functions - Perform load scaling or - Perform peak scaling or - Perform factor scaling - Manually override forecast value(s) - Notify the Shift Supervisor if an invalid Load Forecast exists for the study period of DRUC. |
| Outage Notes/Off-Line Studies | IF: - Resources are needed for identified Voltage issues; THEN: - Once COPs have been updated, identify the appropriate resources that can be utilized if needed. |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>EMS Interface>EMSI Workflow Parameters IF: - The EMSI Workflow Controller (Time Stamped – runs XX:50 every hour) function (data transfer between EMS and MMS) and Load Forecast are NOT running (should be continuous); THEN: - Notify Help Desk and Control Room Staff. |
| Bad/Suspect Telemetry | CHECK: - EMS Operator Alarms for major Generation Resources statuses with BAD/SUSPECT quality codes, IF: - Issues exists and will not be resolved before DRUC execution; THEN: - Discuss with Shift Supervisor if the DRUC should be run or delayed until the issues can be resolved. - Consider requesting Operations Support Engineer to manual over-ride of SCADA values (Be aware that this could skew the results), - If it is determined to delay DRUC, follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure. |
| ### By 13:30 each day, perform the following |  |
| Deselect Contingencies | IF: - It has been determined with the help of Engineering Support that a contingency known to cause errors or that otherwise result in inconclusive study output in RUC; THEN: - After the Operations Support Engineer has deselected the contingency, - The contingency will be automatically posted no later than one hour after deselected to the MIS Secure Area. - MIS; Grid; Generation; Reliability Unit Commitment; Contingencies Deselected in RUC |
| NOTE | - The DRUC process may not be used to buy Ancillary Service unless the Ancillary Service Offers submitted in the DAM are insufficient to meet the requirements of the Ancillary Service Plan. - By default, Resources without an entry in COP are considered to have a Resource Status of OUT and are unavailable in RUC Procedure. |
| WRUC | IF: - Prior to 1330, ERCOT may issue a WRUC instruction to a QSE that a Resource is required to be On-Line for all or part of a future Operating Day; THEN: - The QSE may self-commit the Resource for the WRUC instructed hours by updating the Resource’s COP to reflect the appropriate On-Line Status for the WRUC hours prior to the DRUC process execution, OR - The Resource will be committed as part of the DRUC process for all WRUC-instructed hours not DAM-committed or QSE self committed. |
| ### By 14:00 each day, perform the following |  |
| NOTE | As time permits, try to contact QSEs that have NOT submitted a COP for the DRUC study period. |
| Long Lead Times | Identify resources that have a lead-time greater than the DRUC timeline, WRUC results should be utilized for identifying resources with long lead-times. IF: - Resources are identified; THEN: - Commit the necessary resources as needed. |
| ### By 14:25 each day, perform the following |  |
| NOTE | If the DAM did not complete by 1330, then DRUC will be delayed. MPs need an hour between the completion of DAM and the opening of DRUC to update COPs. |
| Verify | Verify that the DAM has completed. IF: - DAM will not complete until after 1430; THEN: - Follow the “Manage DAM/DRUC Timeline Deviation/Failure” procedure. |
| Setting parameters for ONLINE | REVIEW REFERENCE DISPLAY: System Administration>Data Management Verify that “Connect to Schema” is set to “ONLINE”. |
| Verify | REVIEW REFERENCE DISPLAYS: Market Operation>EMS Interface>EMSI Workflow Parameters Market Operation>EMS Interface>EMSI Workflow Messages EMSI has completed successfully within the last hour Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>DRUC UC Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>NSM Displays>NSM Execution Control Parameters Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters - “Retrieve MF Interface Data” flag set to “Yes”. - “Retrieve MI Interface Data” flag set to “Yes”. - “Retrieve EMS Interface Data” flag set to “Yes”. - “Check Market Status set to “Yes”, - “Use Save case set to “No” |
| ### At 14:30 each day, perform the following |  |
| DSI | EXECUTE: - The DSI sequence VERIFY: - For error or warning messages and take necessary action if needed to correct the errors, - The input data is properly transferred. If NOT: - Contact EMMS production support personnel immediately to determine the cause and expected time of resolution. |
| Verify | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MI DAM AS Insufficiency This display will give the Operator an indication if any A/S insufficiencies have occurred in DAM. If insufficiencies exist, the Operator can start looking at resources that can be committed to resolve the insufficiency in DSP. |
| E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays> External Input Data> MI COP Verify that E-tags are being imported into the MMS. IF: - Individual schedules need to be reviewed; THEN: - Go to the MI COP display and filter ‘ERCOT’ as the QSE name |
| Verify | - Identify and correct Bad/Suspect Telemetry - Modify Input for Block Load Transfer (BLT) movement - Modify Input for Verbal Dispatch Instructions Refer to Desktop Guide RUC Section 2.3 |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> DRUC Displays> DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - Additional resources are needed to solve for voltage issues; THEN: - Consult with the Operations Support Engineer and/or the Transmission and Security Desk Operator to determine which resources should be committed, AND - Determine the temporal constraints for each of the units. IF: - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in future HRUC Study Periods; THEN: - Filter for the unit - Change ‘Auto’ to ‘On’, - List reason. |
| Set Flags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>DSI Execution Control Parameters IF: - Manual changes have been made to the DRUC input data; CHANGE: - The appropriate flags are set to prevent the data from being over-written. - “Retrieve MF Interface Data set to No”, - “Retrieve MI Interface Data set to No”, - “Retrieve EMS Interface Data set to No”, OR - “Use Save case set to “Yes” |
| Execute | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages Execute the entire DRUC sequence (Run All). |
| STNET Studies | Notify: - Operations Support Engineer to run NSA for each hour of the next operating Day. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 5.1 (9)&(11) | 5.3.(3) | 5.5.1(9) | 5.5.2 |
| --- | --- | --- | --- | --- |
|  | 5.5.3(2) | 6.3.1(1) | 6.4.6(4) | 6.4.8.1(3) |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 14 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.15 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with Market Operations and Operations Support Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published, IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for DRUC are invalid, - Notify the Manager or designee immediately, - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “Manage Capacity Insufficiency” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to Desktop Guide RUC Section 2.6, step 5. |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour, - Any under/over generation; THEN: - Be aware of these when running HRUC. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Notified from Market Operations of A/S Insufficiency from DAM; THEN - Issue a Watch - Verify Market Operations has posted message on MIS - Refer to Desktop Guide RUC Section 2.1. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to A/S insufficiency in DAM for operating day [day]. The A/S insufficiencies will be procured in DRUC. [QSE] please repeat this back to me. That is correct, thank you.” |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required, - Valid; THEN - Locate the constraint on the DSP Constraint Summary display, - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, - Commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit; THEN - Determine the validity, - Determine the temporal constraints for each of the units, IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason (evaluate later). IF: - There is reliability reason requiring the resource commitment decision to be made immediately; - Resources with long start-up times - Resources returning from outages - Congestion or Capacity deficiencies that may create HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, uncommitting, examples below: - Evaluate later - Voltage issue - SLWSCRL5 (constraint name) |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS folder: - “6 DRUC Capacity” which is based on the last ran DRUC VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision can be made in the future, THEN: - Post an OCN and make Hotline call for Excess Reserve Capacity for hours projected. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess Reserve Capacity for [hours]. [QSE] please repeat this back to me. That is correct, thank you.” |
| DRUC Committed For Capacity Shortage | IF: - DRUC recommends Resource(s) for capacity; THEN - Determine if start-up time allows enough time to re-evaluate, and - De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: - Post an OCN and make Hotline call for projected Reserve Capacity shortage for hours short. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [hours]. [QSE] please repeat this back to me. That is correct, thank you.” |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Additional resources are needed to solve for transmission issues (such as voltage issues) and were not picked up in the DRUC run, - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period, OR - A Resource was given a WRUC instruction and chose not to self-commit for all hours needed; THEN: - Change ‘blank’ to ‘Commit’ - List reason (capacity, constraint name or voltage issue). |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments; DETERMINE IF: - Outage related’ - Possible Network Model error’ - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort; THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - External Input data - UC Displays - Input Display Menu - System TCG Data & System Load |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made; THEN: - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button - Follow the Manage DRUC Failure/Timeline Deviation procedure. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>DRUC> DRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>DRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue VDIs to cancel RUC instructions |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed and needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |

## 4.4	DAM/DRUC Timeline Deviation

Procedure Purpose: To address situations in which the DAM/DRUC process has deviated from its timeline.

| Protocol Reference | 4.1.2 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 | IRO-001 R9 |  |  |

| Version: 1 | Revision: 8 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### DAM Timeline Deviation |  |
| DAM Timeline Deviation | IF: - Notified by Market Operations that the DAM Market timeline is deviated; THEN: - Notify Shift Supervisor, - Issue a Watch by making a Hotline call (Market Operations will post message on the MIS): Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch for the timeline deviation of the Day Ahead Market; the start of DRUC will be delayed. Another hotline call will be made when DAM completes. [QSE] please repeat this back to me. That is correct, thank you.” WHEN: - DAM completes; THEN: - Make Hotline call to QSE’s and give one hour notice to update COPs - Post message on MIS Public utilizing Notice Builder (Operational Information with low priority) Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the delay of DAM. DAM is now complete; DRUC will begin at [time]. [QSE] please repeat this back to me. That is correct, thank you.” Typical MIS Posting: DAM is complete, DRUC will begin at [xx:xx]. |
| ### Delay of DRUC |  |
| DRUC Delay | By 16:00 IF: - DRUC is delayed; THEN: - Notify Shift Supervisor, - Issue a Watch by making a Hotline call - Post message on the MIS Public using Notice Builder: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch for the timeline deviation of DRUC for [effected date] due to [state issue]. DRUC will now start at [time]. [QSE] please repeat this back to me. That is correct, thank you.” Note: This step may have already been done if DAM did not met its timeline in “DAM Timeline Deviation” |
| Timeline Not Met | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow By 18:00 IF: - DRUC completed and the results cannot be approved; THEN: - No need to abort DRUC Process, just don’t approve. IF: - DRUC has not completed (i.e. software issues); THEN: - Abort DRUC Process. |
| 1 | IF: - DRUC software fails without expectation of timely repair, or due to time constraints due to not completing in a timely manner; THEN: - Notify the Help Desk and control room staff, - Issue an Emergency Notice by making a Hotline call - Posting message on the MIS Public using Notice Builder Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Emergency Notice due to DRUC not completing by 1800 due to [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - DRUC is aborted or shut down; THEN: - Go to display System Administration > Savecase Management. - Choose File Type as DRUC. - Fill in File Name (no spaces allowed) - Fill in Description. - Push Create Button. - The message will show up in the Text field. - Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Also refer to Desktop Guide Common to Multiple Desks Section 2.15, if needed. |
| NOTE | After 1800, HRUC will run for the rest of the current day and the next day even if DRUC has not run successfully. |

## 5.2	Review WRUC Results

Procedure Purpose:  To identify commitments with a long lead time and develop a list of violated/binding constraints that have a high-probability of being binding in SCED or DAM.

| Protocol Reference | 5.1 | 5.5.1(9) | 5.5.2 | 6.3.1(1) |
| --- | --- | --- | --- | --- |
|  | 6.4.6(4) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - WRUC does not send commitments or dispatch instructions to QSEs. - WRUC does not retrieve any QSE-submitted Three-Part Supply Offers. - WRUC relies exclusively on the QSE-submitted COPs. |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Market Operation>Reliability Unit Commitment>WRUC Displays>Workflow>WRUC Workflow Messages |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>WRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints and notify Operations Support Engineer to determine the validity IF: - Invalid, no further action is required - Valid; THEN - Locate the constraint on the DSP Constraint Summary display - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources |
| Long Lead Times | IF: - WRUC or Outage Notes identify a Resource with a lead-time greater than the DRUC time-line; THEN: - Instruct the QSE that their Resource needs to be On-line by [date] at [time] and they have the option of - Self-committing the Resource by updating the COP before the DRUC process execution, or - ERCOT will commit the Resource in the DRUC process |
| Create Save Case | IF: - WRUC is aborted or shut down; THEN: - Go to display System Administration > Savecase Management. - Choose File Type as WRUC. - Fill in File Name (no spaces allowed) - Fill in Description. - Push Create Button. - The message will show up in the Text field. - Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Also refer to Desktop Guide Common to Multiple Desks Section 2.15, if needed. |
| Log | - Any unreasonable constraints/commitments - Commitments with long lead time and any possible alternatives - List of violated constraints and long lead time Resources, if any, which are the only solution for resolving those violated constraints. |

## 6.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 10 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### ADVISORY |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market (DAM) in accordance with ERCOT Procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market (DAM) allows - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### WATCH |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system. - ERCOT varies from time-line for DAM/DRUC |
| ### EMERGENCY NOTICE |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution and/or Emergency Base Points are issued - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum Reliability Standards during the Operating Period using every Resource practically obtainable from the market - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options - A transmission condition has been identified causing unreliable operation or overloaded elements - A Severe Single Contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists - ERCOT has determined a fuel shortage exists that would affect reliability - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED) - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Notifications |  |
| Hotline | Notify QSEs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS using Notice Builder. - For “free form” messages, the “Notice Priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 7.1	Monthly Testing of Satellite Phones

Procedure Purpose:  To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001 R2 | EOP-005 R5 |  |  |

| Version: 1 | Revision: 4 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with the TOs. As the Shift Supervisor makes the call to the individual TO, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TO. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7) for a list of the TOs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Conference Bridge are Desk specific. Select: SATELLITE directory or go to page 35 to view the programmed numbers on the Turret phone for each Bridge: - BLACKSTRT RUC – RUC Desk - BLACKSTRT RES – Resource Desk - BLACKSTRT REAL – Real-Time Desk - BLACKSTRT TS#1 – Transmission Desk (Island Coordination) - BLACKSTRT TS#2 – Transmission Desk |
| 1 | IF: - The preprogrammed number does not function correctly, THEN: - Refer to the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7.2) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the TOs fails to connect to the Bridge call; THEN: - Investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the TOs not able to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |
| ### Alternate Control Center |  |
| 1 | When working out of the alternate during the monthly scheduled dates: - Test the turret Satellite phone on each desk. |
| 2 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| Log | Log the test date and results in the Operations Log. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | - / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 - / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 - / 12 - / 7 - / 6 - / 14 - / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |