## Power Operations Bulletin # 603

ERCOT has posted/revised the Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 1.3	Roles/Responsibilities

ERCOT System Operator, Resource Desk

The ERCOT System Operator – Resource Desk position represents the following NERC functional entities collectively for the ERCOT ISO at any time:

- Reliability Coordinator

- Balancing Authority

- Transmission Operator

- Interchange Coordinator

This representation includes the responsibility and clear decision making authority during normal and emergency conditions to direct and implement real-time actions to ensure the stable and reliable operation of the ERCOT Electric Grid.  These actions shall include shedding of firm load without obtaining approval from higher-level personnel.

## 4.1	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve or reject Resource decommitments in the Operating Period.

| Protocol Reference | 6.4.6 | 6.4.6.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002 R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Operating Period |  |
| NOTE | - The Operating Period is the two-hour period comprised of the Operating Hour and the clock hour preceding the Operating Hour - A QSE may request to decommit a Resource other than a QSGR for any interval that is not a RUC-Committed Interval by verbally requesting ERCOT to consider its request - ERCOT shall review the requests in order of receipt - A QSE may decommit a QSGR without any request for any interval that is neither a RUC-Committed Interval nor an interval in which a manual override by the ERCOT Operator. |
| NOTE | If a combined cycle train (CCT) is transitioning from one configuration to another, this is not a QSE requested decommit. |
| 1 | IF: - A QSE requests to decommit a Resource that has been Self-Committed (other than a QSGR); THEN: - Determine if the Resource is receiving negative LMPs - If negative LMPs, proceed with this procedure - If no negative LMPs, proceed to step 2 IF: - A Resource is receiving negative LMPs; THEN: - Determine if Resource is carrying A/S - If yes, inquire how A/S will be replaced - Determine if there could be a capacity issue if Resource is decommitted (PRC drops < 2500) - If Resource is not allowed to decommit, override HDL to LSL (see Desktop Guide Common to Multiple Desks Section 2.13) - If override is used, the Resource will not be able to carry A/S, and will need to be marked as undeliverable - If no capacity issue exists, grant approval to decommit - Issue an electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Resource” tab - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type tab |
| 2 | IF: - A QSE requests to decommit a Resource that has been Self-Committed (other than a QSGR); THEN: - Determine if the Resource is carrying A/S. - If yes, inquire how A/S will be replaced, - Determine if there could be a capacity issue if Resource is decommitted - If no capacity issue exists, proceed - Notify the Transmission Operator to make determination if needed for congestion management, - If not needed for congestion management. - Issue electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Resource” tab - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type tab |
| 3 | Log actions taken. |

## 6.1	Manage Resource Forced & Maintenance Outages

Procedure Purpose:  Monitor and respond to Resource Forced and Maintenance outages.

| Protocol Reference | 3.1.1(2) (j) | 3.1.4.2 | 3.1.4.4 | 3.1.4.5(1) |
| --- | --- | --- | --- | --- |
|  | 3.1.4.5(2) | 3.1.4.6(2) | 3.1.4.8 | 3.1.6.4(4) |
|  | 3.1.6.5(1) | 3.1.6.9(1) | 3.9.1(2) |  |
| Guide Reference |  |  |  | 6.4.7 |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The QSE should: - Immediately notify ERCOT of a forced outage, - Enter the forced outage in the Outage Scheduler within two hours, - Update their COP within 1 hour - Update their telemetry. A call to the QSE may be necessary if the above are not complete within the designated time frame. |
| NOTE | ERCOT Operators can only make the following changes in the Outage Scheduler: - Remove actual start/end time if it is within 2 hours of the time the MP entered the outage, - Change status, - Add notes If a MP needs assistance or is unable to enter their outages, direct them to Outage Coordination. Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes. |
| Notification | IF: - Maintenance Level 1 Outage is received, review the outage details; THEN: - Discuss the outage request with the Transmission Operator, - If no reliability issues exist, ACCEPT the outage. |
| Reliability Issues | IF: - The Maintenance Level 1 Outage of a Resource creates a system reliability issues; THEN: - Coordinate the start of the Resource Outage to ensure system reliability as long as the outage is allowed to start within 24 hours. |
| Maintenance Level 2 and 3 outages | IF: - Maintenance Level 2 and 3 outages are received; THEN: - The ERCOT Outage Coordination group has a process to review all Maintenance Level 2 and 3 outages without further action. |
| ### Material Deratings |  |
|  | IF: - A Resource’s capability is reduced by 10 MW and is expected to last more than 48 hours; THEN: - The QSE must do the following: - Enter the derating into the Outage Scheduler as a Forced Outage, - Replace AS responsibility if applicable - Update their COP to reflect the changes, - Update the necessary telemetered parameters for the Resource. |
| ### Short-Noticed Resource Outages |  |
|  | IF: - A newly proposed Resource Outage or proposed changes to a Planned Outage is submitted three days or less from the outage start date; THEN: - Notify Outage Coordination Group. |
| ### Opportunity Outages |  |
| NOTE | Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days. The QSE must give as much notice as practicable to ERCOT. |
| 1 | WHEN: - A Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, AND IF: - Approved by ERCOT; THEN: - The Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled. IF: - Reliability issues exist; THEN: - Reject the outage to ensure system reliability, IF: - No issues identified; THEN: - Approve the Outage as received, - Notify the QSE and Outage Coordination Group. |
| ### Returning from Planned Outage Early |  |
| Verify | IF: - A Resource returns from a Planned Outage early; THEN: - Coordinate with the Transmission and RUC Operators to determine if there is an associated transmission outage or any reliability issues exist. |
| Approve | IF: - No issues identified; THEN: - Notify the QSE of approval and to update their COP and Telemetry, - Notify the Outage Coordination Group. |
| Deny | IF: - Reliability issues, OR - Transmission is not available; THEN: - Coordinate between the TO and QSE to schedule a time agreeable to both parties for all facilities to be restored to service, - Notify the QSE within two hours, - Issue a VDI to stay Off-Line (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Can Not Return Early From Outage” as the Instruction Type from Resource level. |
| Log | Log all appropriate information. |

## 7.1	Market Notices

Procedure Purpose:  Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002 R2 | EOP-001-0 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 10 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system. - ERCOT varies from time-line for DAM/DRUC |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution and/or Emergency Base Points are issued - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options - A transmission condition has been identified causing unreliable operation or overloaded elements - A Severe Single Contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists - ERCOT has determined a fuel shortage exists that would affect reliability - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED) - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Scripts |  |
| Hotline | Hotline calls are usually made by Real-Time Operator, the scripts below are for reference if needed: Notify QSEs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify TOs of Notice: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-2.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| ### Version: 1 | Revision: 8 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA. When a media appeal for voluntary energy conservation is enacted QSEs should be notified via Hotline call (Real-time Operator has the responsibility). - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. - QSEs need to contact the Texas Commission on Environmental Quality (TCEQ) for enforcement discretion on air permitting requirements after ERCOT has made contact with TCEQ. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Deploy all available Non-Spin (if not previously deployed) (see Desktop Guide Resource Desk Section 2.2). Make EEA 1 posting to MIS Public using Notice Builder. - Use preformatted notice “EEA Level 1” |
| 2 | IF: - Generation Resource (that are not bid in for Non-Spin) have a unit status of OFF and can be brought On-line within the timeframe of the emergency; THEN: - Issue a VDI to commit the Resource (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) |
| 3 | IF: - A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: - Issue a VDI to commit the Resource (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Commit” as the Instruction Type from Resource level VDIs need a start/stop time (issue one hour at a time) |
| 4 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 60.00Hz; THEN: - Determine whether system conditions require the deployment of Load Resources and/or ERS Resources by considering the following: - If at peak hour, will the 10 MIN ERS be sufficient and have they already been deployed in the current contract period - If not at peak hour, will half of Load Resources be sufficient, or the 30 MIN ERS - Deploy Load Resources and/or ERS, notify the Real-Time Operator when XML message has been completed. Load Resources/ERS must be deployed first before hotline call is made, - Desktop Guide Resource Desk (Section 2.1 for Load Resources; Section 2.9 for ERS). - Make EEA 2 posting to MIS Public using Notice Builder. - Use preformatted notice “EEA Level 2” IF: - Extending Current Deployments of Load Resources; THEN: - Deploy either “Group 1” or “BOTH” Load Resources (see Desktop Guide Resource Desk Section 2.1). |
| ERS Business Hour Changes | IF: - ERS Resources are deployed, and additional ERS Resources are needed and available due to business hour changes; THEN: - Deploy next business hour - Take into consideration the time requirement for the 10 MIN and 30 MIN ERS |
| 2 | IF: Went straight to EEA Level 2; THEN: - Ensure tasks in EEA Level 1 are complete. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Make EEA 3 posting to MIS Public using Notice Builder. - Use preformatted notice “EEA Level 3” |
| 2 | Verify and log that all measures have been implemented. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard | EOP-001-0 R4.1, 4.2, R4.4 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | If 1375 MW of PRC is not restored within 75 minutes, reduce MW loading on Resource(s) to bring reserves up, if available. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC ≥ 1375 MW; THEN: - Transmission Operator will restore firm load. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load have been instructed to be restored; THEN: - When instructed by the Real-Time Operator to recall Load Resources - Send XML message to recall Load Resources, (see Desktop Guide Resource Desk Section 2.1) - Make EEA 3 to EEA 2 posting to MIS Public using Notice Builder. - Use preformatted notice |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Send XML message to recall 10 MIN/30 MIN ERS (see Desktop Guide Resource Desk Section 2.9) - Make EEA 2 to EEA 1 posting to MIS Public using Notice Builder. - Use preformatted notice |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Terminate EEA 1 by posting to MIS Public using Notice Builder. - Use preformatted notice “EEA 1 to Normal” |
| ### Cancel Watch |  |
| 1 | WHEN: - (HDL-GEN) ≥ 500 MW, - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Real Time Operator and recall half of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.2). WHEN: - (HDL-GEN) ≥ 1000 MW, - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Real Time Operator and recall all of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.2). - Cancel message on MIS Public using Notice Builder. |

## 8.2	Monthly Testing of Satellite Phones

Procedure Purpose: To ensure ERCOT maintains communication capability via the Satellite Phone System.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001 R2 | EOP-005 R5 |  |  |

| Version: 1 | Revision: 4 | Effective Date: July 16, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Primary Control Center |  |
| NOTE | When a participant dials into the conference bridge before the moderator dials in, they will hear music and be placed on hold. |
| NOTE | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday, the Satellite Phone System Conference Bridge will be tested with the TOs. As the Shift Supervisor makes the call to the individual TO, they will set a time that the ERCOT Operator will call the Satellite Phone System Conference Bridge and establish communication with the appropriate TO. |
| NOTE | Use the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7) for a list of the TOs that will be contacted by the ERCOT Operator and instructions on how to place a Satellite Phone System Conference Bridge call. |
| NOTE | The numbers for the ERCOT Operator to call into the Conference Bridge are Desk specific. Select: SATELLITE directory or go to page 35 to view the programmed numbers on the Turret phone for each Bridge: - BLACKSTRT RUC – RUC Desk - BLACKSTRT RES – Resource Desk - BLACKSTRT REAL – Real-Time Desk - BLACKSTRT TS#1 – Transmission Desk (Island Coordination) - BLACKSTRT TS#2 – Transmission Desk |
| 1 | IF: - The preprogrammed number does not function correctly; THEN: - Refer to the ERCOT Satellite Phone User Guide (See Desktop Guide Common to Multiple Desks Section 2.7.2) for the appropriate conference number and continue with this procedure. |
| 2 | When prompted: - Enter the Moderator Pass Code - If necessary, allow five minutes for Participants to dial in - As each Participant connects, record the following: - Name of Participant - Company Name - Any problems identified with the connection process |
| 3 | IF: - One or more of the TOs fails to connect to the Bridge call; THEN: - Investigate the cause and log the following: - Reason for inability to connect - Actions taken by ERCOT - Establish a time for a retest of the TOs not able to connect in the initial test. |
| 4 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |
| ### Alternate Control Center |  |
| 1 | When working out of the alternate during the monthly scheduled dates: - Test the turret Satellite phone on each desk. |
| 2 | Inform the Shift Supervisor when test is complete indicating any issues identified. |
| LOG | Log the test date and results in the Operations Log. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outages Updated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |