## Power Operations Bulletin # 612

ERCOT has posted/revised the DC Tie Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.2	Communication

Procedure Purpose:  To ensure that three part communication is used for all directives and ensuring all entities receive Hotline calls.

| Protocol Reference | 6.5.7.8(4) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: November 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## Three-Part Communication |  |
| NERC | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE: | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been placed throughout the procedures as a reminder for the three-part communication. However, a script can not be provided for every scenario. Effective three-part communication skills are mandatory. |
| ## Hotline Call Communication |  |
| 1 | When making Hotline calls, verify that every entity has answered. IF: - Not every entity answered the Hotline; THEN: - Contact them using their OPX line or LD line to provide them with the message - Inquire why they were not on the Hotline call - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| LOG | Log all actions. |

## 3.2	Import and Export Limits for the CFE DC Ties

Procedure Purpose: To confirm the import and export limits of the CFE DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: November 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Daily import and export limits for the Railroad and Eagle Pass DC Ties, and Laredo VFT will be provided by the Operations Engineering Support Group on the “Transmission Limits to Be Monitored” sheet. MIS Secure>GRID>Transmission>Generic Transmission Limits If the limits are not posted, notify the Operations Support Engineer. |
| 1 | Once the DC-Tie limits for next day are received, verify the sum of the E-Tags do not exceed the export limits on any DC-Tie. If so, notify the Shift Supervisor of the possible need to commit additional Resources, closer to real-time. |
| 2 | When CFE has the ability to import additional energy into ERCOT, this could exceed the posted import limits. ERCOT has no issues with imported energy and these tags should be accepted. IF: - A tag is received that will exceed an import limit; THEN: - Accept the tag, - Notify the Operations Support Engineer to have the posted limit updated. |
| 3 | Coordinate with the ERCOT Transmission & Security Operator to ensure the import and export limits are updated in RTMONI hourly. EMS>EMP Applications>RTMONI Constraints Monitoring>Monitor Displays>Real Time Monitoring Groups Dir>DC_Ties |

## 4.5	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose: The process to curtail E-Tags for the CFE Ties and request emergency energy, if needed.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0.1b R3.1, R4.2 | INT-004-2 R1 | INT-005-3 R1.1 | INT-010-1 R2 |

| Version: 1 | Revision: 10 | Effective Date: November 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE DC-Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - AEP Tenaska is the generation dispatcher that a VDI for emergency energy is issued to and from CFE. They can be reached using the Turret phone button labeled (AEP TENASKA QSE), page 4 |
| NOTE | DC Tie Load shall neither be curtailed during the Adjustment Period, nor for more than one hour at a time, except for the purpose of maintaining reliability. |
| NOTE | A Transmission Watch will be issued if the ERCOT System is in an unreliable condition. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific MW amount, only CFE needs to approve the change. Curtailments will be automatically approved by them. |
| ### Transmission Issues within ERCOT |  |
| 1 | It may be necessary to curtail export E-Tags using the Last-in-First-Out (LIFO). IF: - Notified by the ERCOT Transmission Operator of the need to curtail (which includes reductions) exports on a specific DC-Tie; THEN: - Verify the MW amount the E-tag needs to be curtailed, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE - Notify PSE with curtailment information and reason. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] to [state MW amount] starting at [xx:xx] due to transmission issues within ERCOT. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified by the ERCOT Transmission Operator that the E-Tags can be re-loaded: - Notify PSE with reload information, - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Section 2.5), - Ensure DC Tie Operator (AEP TO) sees the re-loaded E-Tags, and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx], the transmission issues within ERCOT have been resolved and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CFE to approve re-loads. Please repeat this back to me. That is correct. Thank you.” |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TO) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission Operator a Transmission Watch has been issued and there is need for emergency energy; THEN: - Request the DC-Tie Operator (AEP TO) to inquire about the availability of emergency energy on [name DC-Tie(s)] Typical Script to DC Tie Operator (AEP TO) Corpus “This is ERCOT operator [first and last name] At [xx:xx] ERCOT declared a Transmission Watch, we are requesting you to contact CFE to inquire about the availability of emergency energy into ERCOT on [name DC-Tie(s)] IF: - Emergency Energy is available; THEN: - Request the DC-Tie Operator (AEP TO) to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Issue AEP Tenaska (AEP TENASKA QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of rest) - Notify AEP Tenaska (AEP TENASKA QSE) that VDI has been issued. IF: - Emergency Energy is not available; THEN: - Notify ERCOT Transmission and Security Desk |
| LOG | Log all actions taken. |
| ### Transmission Issues within CFE |  |
| 1 | Due to reliability issues within CFE it may be necessary to curtail import E-Tag(s) for them. IF: - Notified by the ERCOT Transmission Operator or the DC Tie Operator (AEP TO) of the need to curtail imports on specific CFE DC-Ties; THEN: - Verify the MW amount and time of the curtailment, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact the DC Tie Operator (AEP TO) when curtailment is complete and instruct them to make notification to CFE, - Notify PSE with curtailment information and reason. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag [tag number] on the [DC tie name] to [state MW amount] due to reliability issues within CFE. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified that CFEs reliability issue has been resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Ensure DC Tie Operator (AEP TO) sees the re-loaded E-Tags, and instruct them to make notification to CFE, - Notify PSE with reload information. |
| 3 | IF: - The re-loaded E-Tag goes passive deny because CFE did not approve the E-Tag in the allotted time; THEN: - Re-load the E-Tag again, - Call the DC Tie Operator (AEP TO) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.3, Emergency Energy to CFE. |
| LOG | Log all actions taken. |

## 4.6	Loss of Primary Control Center Functionality

Procedure Purpose: To be performed by the Operator at the alternate Control Center (ACC) in the event that:

- Functionality of the Primary Control Center (PCC) is lost OR

- Communication with the PCC is lost

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1.1 R5 | EOP-001-0.1b R4.4 | EOP-008-0 | IRO-005-3.1a R1.10 |

| Version: 1 | Revision: 12 | Effective Date: November 1, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Contact Security | IF: - Unable to reach any Operator at the PCC (cell phone or PBX Bypass phones); THEN: - Check the Control Room video camera to determine the status of the PCC and personnel, - Contact Security at the ACC - Notify them of the situation AND - Have them attempt to make contact with Security at PCC. - Have them contact you with information acquired OR IF: - Notified by the PCC that they are evacuating and/or transferring sites; THEN: - Continue with procedure. |
| ### Systems are Functional |  |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Bastrop. Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| QSE Hotline Call | Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center and is transferring operations to the alternate control center. Direct all urgent phone calls thru the [Bastrop][Taylor] OPX. All ERCOT systems are functioning at this time. HRUC will be delayed until additional staffing arrives. If you represent a Nuclear Plant, please inform them that RTCA results will not be viewed in a timely manner and is expected to last for approximately 1 hour.” [Select QSE], “Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| TO Hotline Call | Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center and is transferring operations to the alternate control center. Please monitor your own service area and notify ERCOT if you reach the emergency rating of your transmission elements. Report when the West - North or the North – Houston limits reaches 80% of the posted limit. Continue to monitor voltages in your area and notify ERCOT of any forced line outages. Direct all urgent phone calls thru the [Bastrop][Taylor] OPX. [Select TO], Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Additional Notifications | The Manager of System Operations and/or designee will notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support These phone numbers are also programmed into the control room cell phone. |
| MIS Posting | As time permits, post the Emergency Notice in the Public MIS using Notice Builder. Typical Script: ERCOT issues Emergency Notice for the loss of the primary control center. |
| Monitor Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. A potential critical facility becomes a critical facility when the contingency appears in RTCA/TCM as a post-contingency overload. |
| Respond to QSEs | Monitor frequency and re-run SCED/use (manual offset) as needed. IF: - QSEs call in with questions about Operational timelines or non real-time issues; THEN: - Notify the QSE that the all timelines and non real-time issues will be addressed when additional staff arrive, - Document QSE calls to pass along the appropriate Operators as they arrive. |
| Respond to TOs Thermal/ Voltage Limits Reached (SOL) | IF: - Thermal limits have reached their continuous rating; THEN: - Activate associated constraint, OR - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, - Issue unit specific VDIs as necessary, - Make call to QSE with directive, - Follow up with an electronic VDI, - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level, OR - Choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level - Continue to monitor to determine the effect of the plan. ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. WHEN: - Indicated by SCADA alarms, OR - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct a QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| West to North (IROL) | IF: - The West-North stability limit is approaching 70%, OR - The TO calls to report the limit is approaching 70%; THEN: - Activate the “BASECASE W_to_N” constraint in TCM - Update RTMONI with new limit each time it changes to give transparency to Market Participants. - Take action to lower Wind generation in the west by issuing unit specific VDIs as necessary to relieve the congestion, - Make call to QSE with directive - As time permits, choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level See Desktop Guide DC Tie Desk Section 2.7 Activating the W-N |
| North to Houston (IROL) | IF: - The North-Houston stability limit is approaching 80%, OR - The TO calls to report the limit is approaching 90%; THEN: - Activate the “BASECASE N_to_H constraint in TCM - Update RTMONI with new limit each time it changes to give transparency to Market Participants. - Take action to raise generation in Houston area by issuing unit specific VDIs as necessary to relieve the congestion - Make call to QSE with directive, - As time permits, choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Log | Make log entry of events. |
| ### Systems are not Functional |  |
| Constant Frequency | IF: - The loss of PCC involves the loss of EMS (LFC and RLC/SCED; THEN: - Determine which QSE has ample capacity to place on Constant Frequency Control. (REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data) - Direct that QSE to go on “Constant Frequency”. - Issue an electronic VDI when systems are functional - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level |
| Call in Additional Operators | Activate the NXT scenario to call in additional shift personnel, which includes a Shift Supervisor. SELECT: - SO Loss of Control Room at Taylor, OR; - SO Loss of Control Room at Bastrop. Operator will receive an email after 10 minutes with a report of who has responded along with their estimated time of arrival. |
| QSE Hotline Call | Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to loss of primary control center functionality, LFC and SCED failure. ERCOT has put a QSE on constant frequency. All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT. ERCOT may issue unit specific deployments to any Resources as required. Direct all urgent phone calls thru the [Bastrop][Taylor] OPX. [Select QSE]. If you represent a Nuclear Plant, please inform them that RTCA and State Estimator are not functioning and are expected to last approximately 2 hour. “Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. |
| TO Hotline Call | Typical Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is issuing an Emergency Notice due to the loss of primary control center functionality and is transferring operations to the alternate control center. Please monitor your own service area and notify ERCOT if you reach the emergency rating of your transmission elements. Report when the West - North limit reaches 70% or the North – Houston limit reaches 80% of the posted limit. Continue to monitor voltages in your area and notify ERCOT of any forced line outages. Direct all urgent phone calls thru the [Bastrop][Taylor] OPX. [Select TO], Please repeat this back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the entire process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| MIS Posting | As time permits, post the Emergency Notice in the Public MIS using Notice Builder. Typical Script: ERCOT issues Emergency Notice for the loss of the primary control center. |
| Additional Notifications | The Manager of System Operations and/or designee will notify the following: - Help Desk (to notify EMMS Support and Telecommunications) - Engineering Support These phone numbers are also programmed into the control room cell phone. |
| Respond to QSEs | IF: - The QSE that is put on constant frequency is having trouble controlling frequency; THEN: - Issue a unit specific directive to another QSE to help with Regulation. - Issue electronic VDI when systems are functional - Choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level OR - Put a different QSE on constant frequency (Remember to take the first QSE off constant frequency). |
| Respond to TOs Thermal/ Voltage Limits Reached (SOL) | IF: - Thermal limits have reached their emergency rating; THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, and issue unit specific directives to appropriate QSE. - Issue an electronic VDI when systems are functional - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level, OR - Choose “ OTHER FOR RESOURCE” as the Instruction Type from Resource level - Continue to monitor to determine the effect of the plan. ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. WHEN: - Notified by a TO of voltage concerns; THEN: - Initiate a solution in collaboration with the appropriate TO and QSE in the area. WHEN: - TOs have utilized all Static Reactive Power Resources (capacitors, reactors, change in transformer taps) and a voltage issue still remains; THEN: - Instruct the appropriate QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| West to North (IROL) | IF: - If the TO calls to report the limit is approaching 70% and is continuing to trend upward, THEN: - Take immediate action to lower Wind Generation in the west by issuing unit specific directives as necessary to relieve the congestion - Issue electronic VDI when systems are functional - Choose “OTHER FOR RESOURCE” as the Instruction Type from Resource level - Monitor QSE on constant frequency |
| North to Houston (IROL) | IF: - If the TO calls to report the limit is approaching 80% and is continuing to trend upward; THEN: - Take action to raise generation in Houston area by issuing unit specific directives as necessary to relieve the congestion. - Issue electronic VDI when systems are functional - Choose “OTHER FOR RESOURCE” as the Instruction Type from Resource level - Monitor QSE on constant frequency |
| Thermal Limits Reached (SOL) | IF: - Thermal limits have reached their continuous rating and are continuing to trend upward, THEN: - Seek a recommendation from the corresponding TO as to what actions will alleviate the situation, and issue unit specific directives as necessary - Issue electronic VDIs when systems are functional - Choose “COMMIT/DECOMMIT” as the Instruction Type from Resource level - Continue to monitor to determine the effect of the plan. |
| DC Tie Tags | Make every attempt to handle all DC Tie tags. If the workload makes it impossible to keep up with, the tags will be passively denied. |
| Log | - Make log entry of events. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 1.0 / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |
| 2.3 3.1 3.2 3.3 3.6 3.7 3.8 3.9 3.11 4.1 4.2 4.3 4.5 4.6 4.8 | 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 7 1.0 / 4 1.0 / 6 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated step “Beginning of each Shift” Updated 1st note Updated steps 1, 2 & 3 Updated 1st, 4th note and step 1 Updated step 1 “Imports” and step 2 “Exports” Updated Steps 1, 2 and 4 in “CFE DC-Ties” Updated 2nd note and steps 1-3 Updated steps 1-3 Updated steps 1 and 2 Updated all steps Updated all steps Updated all steps Updated all steps Removed reference of Austin Control Room Added projected reserve capacity shortage and Extreme Hot Weather in Watch | September 1, 2011 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 6 1.0 / 7 | Updated step 2 Updated step 1 Updated Turret Phone, step 3a in Comision Federal de Electricidad (CFE) and step 5b to implement NPRR 379 Updated Turret Phone and step 3a in Comision Federal de Electricidad (CFE) Updated step 3 | October 1, 2011 |
| 4.6 | 1.0 / 7 | Updated step TO Hotline Call | November 1, 2011 |
| 3.1 3.3 4.6 4.8 | - / 9 1.0 / 9 1.0 / 8 1.0 / 7 | Updated step 2 Updated step 1 Added new section and updated all steps Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.3 4.6 | 1.0 / 1 1.0 / 10 1.0 / 10 1.0 / 9 | Updated Scope Updated step 2 Updated step 1 Updated Hotline call scripts | January 19, 2012 |
| 2.1 2.3 3.1 3.2 3.7 4.1 4.2 4.3 4.5 4.8 | 1.0 / 1 1.0 / 4 1.0 / 11 1.0 / 5 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 7 1.0 / 8 | Added dispatch instructions paragraph Updated Desktop Guide reference Added 3rd Note Changed Shift Engineer to Operations Support Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 2nd Note & all steps 1 – 3 Updated step 1 of Watch | March 1, 2012 |
| 3.1 3.3 3.7 3.8 3.9 4.54.6 4.8 | 1.0 / 12 1.0 / 11 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 10 1.0 / 9 | Updated step 2 Updated 3rd Note and step 1 Added posting and cancelling messages Updated overview Updated overview Updated procedure based on NPRR405 Updated W-N or N-H steps Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather | May 1, 2012 |
| 1.3 3.2 3.8 3.9 4.5 4.6 4.8 | 1.0 / 1 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 11 1.0 / 10 | Removed ERCOT Shift Supervisor paragraph Updated step 1 Updated step 4 Updated step 4 Added step Turret Phone & 1st Note, updated step 4 Updated several steps based on lessons learned from classroom training and simulation Updated all step 1’s | July 16, 2012 |
| 3.1 | 1.0 / 13 | Updated step 2 | August 29, 2012 |
| 2.2 3.2 4.5 4.6 | 1.0 / 1 1.0 / 7 1.0 / 10 1.0 / 12 | Added Hotline Call Communication Updated 1st Note Updated 1st and 2nd Note Updated steps West to North & North to Houston(IROL) All procedures in this manual have been reviewed. | November 1, 2012 |