## Power Operations Bulletin # 619

ERCOT has posted/revised the Real Time Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.5	Alarm Processing and Acknowledgment

Procedure Purpose: To monitor and acknowledge system alarms.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-2 R6, R8 | IRO-003-2 R2 | IRO-005-3.1a R1.1, R1.2 | TOP-002-2.1b R8 |
|  | TOP-006-2 R2, R5 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: |
| Categories | Tab 1: 345 KV Transmission Equipment Status Tab 2: 138 KV Transmission Equipment Status Tab 3: Generator Breaker, AVR, CAPS, REACTOR and SPS Status Tab 4: RLC alerts Tab 5: Transmission Line Overloads - Voltage Violations - Critical Alarms Tab 6: QKNET alarms Tab 7: ICCP status Tab 8: All other alarms |
| 1 | Monitor the Alarm Summary Display pages 3, 6 and 7 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as System conditions warrant. |
| 3 | Coordinate with the Transmission Operator to clear the alarms approximately every 24 hours or as needed. |

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.3.2(2) | 6.5.7.6.2.2 | 6.5.9.1(1)(b) | 8.2 (2)(b)(vii) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.3.1.2 |  |  |  |
| NERC Standard | BAL-002-1 R2.4, R6 | BAL-005-0.2b R8 | BAL-007 (Field Trial) | EOP-002-3.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 611.5 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -611.5 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, - Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) |
| Base Point Deviation | IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) - If unit trip: - Time of unit trip, - Name of unit, - Approximate net MW on unit, - Approximate lowest TrueTime frequency (use 3 decimals), - Amount of RRS deployed (if any), AND - Approximate ERCOT load. |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: - QSE will request VDI(s) - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time - A VDI will be needed for each Resource IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per deployment for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - Manually run SCED IF: - Frequency goes above 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, - Enter manual offset (the offset will continue until removed). IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 10 MINUTES | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Operations Support Engineer to send an event notification to BAALfieldtrials@ercot.com. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.80 Hz - Load Resource providing RRS – 59.70 Hz |
| Monitor/ Deploy | IF: - Frequency drops below 59.95 Hz, AND - Regulation Up service remains and is deploying; THEN: - Manually run SCED (do not run SCED more than once between SCED runs) IF: - Frequency drops below 59.95 Hz, AND - Out of Up Regulation; THEN: - Check the GTBD2[HDL] on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset - If using OpsMon Dashboard, do not enter an offset > than GTBD2[HDL] - If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - GTBD2[HDL] on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS does not have adequate up room; THEN: - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the “Manual RRS” to activate box, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - If room is available - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the “Manual RRS” to activate box, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. - Notify the Shift Supervisor of the need to possibly commit additional Resources. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available - Manually run SCED, - Log the event and notify Operations Support Engineer to send notification of the event to BAALfieldtrials@ercot.com. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available, manually run SCED. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED. |
| Stable | IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Contact the Help Desk. |

## 3.2	Monitor Large Ramp Events

Procedure Purpose:  The ERCOT Large Ramp Alert System (ELRAS) is designed to monitor the probability of large wind output ramps in the ERCOT region and provide ERCOT Operators with further situational awareness.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The potential for a large ramp can be identified using the “Graphical Forecast” page of ELRAS in the Real-Time Viewing Mode. An example of the page is in figure 1 below. The “Graphical Forecast” page plots the probability of a ramp rate event starting at a given time during the next 6 hours. The graphical displays are broken up into three timeframes; 15-minute probabilities, 60-minute probabilities, and 180-minute probabilities, and Up and Down ramp rate events are split up for each time frame. These displays are interpreted by first looking at a particular interval on a given display. The value for that interval on that display is characterized as the probability of a given MW change occurring over a specified amount of time starting at the specified interval. For example, looking again at figure 1, the “Graphical Forecast” is showing a 50% probability of at least a 2,000 MW increase occurring over 180 minutes starting at 18:00. In other words, between 18:00 and 21:00 there is a 50% chance that the aggregate wind output will increase by at least 2,000 MW. For the purpose of this procedure, the forecasted ramp rates to be considered significant are those that are indicated in Red; 1,000 MW in 15-minutes, 2,000 MW in 60-minutes, and 4,000 MW in 180-minutes. In the event that one of these ramp rates is forecasted to have at least a 50% probability of occurring, determine if the system has the ramp rate to keep up with the wind ramp. |
| ### Down Ramp Event |  |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| 2 | IF: - There is a 50% probability of a projected system wide down-ramp of 4,000 MW within the next 180 minutes, OR - There is a 50% probability of a projected system wide down-ramp of 2,000 MW within the next 60 minutes; THEN: - Refer to the “180 min. HASL(COP) - LF or 60 min. HASL(COP) - LF” on the 60 to 180 minute OpsMon Dashboard to determine if system ramp rate capability is sufficient, AND - Make a Hotline call to provide situational awareness about a possible down-ramp event of 2,000 MW or greater within the next 60 minutes or 4,000 MW or greater within the next 180 minutes. IF: - System ramp rate is not sufficient; THEN: - Notify RUC Operator to procure Resources as needed. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN due to a 50% probability of a [4,000 MW down-ramp in the next 180 minutes] [2,000 MW down-ramp in the next 60 minutes]. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]. |
| 3 | IF: - There is a 50% probability of a projected system wide down-ramp of 1,000 MW within the next 15 minutes; THEN: - Refer to the “HDL-Gen” on the 15 minute OpsMon Dashboard and the available Regulation UP Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Deploy Non-Spin as needed, and - Continue to monitor frequency and “HDL-Gen” |
| ### Up Ramp Event |  |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| 2 | IF: - There is a 70% probability of a projected system Wide up-ramp of 2,000 MW within the next 60 minutes; THEN: - Refer to the “60 min. LF - LSL(COP)” on the 60 to 180 minute OpsMon Dashboard to determine if system ramp rate capability is sufficient, AND - Make a Hotline call to provide situational awareness about a possible wind up-ramp event of 2,000 MW or greater within the next 60 minutes. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN due to a 70% probability of a 2,000 MW up-ramp in the next 60 minutes. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]. |
| 3 | IF: - There is a 70% probability of a projected system wide up-ramp of 1,000 MW within the next 15 minutes; THEN: - Refer to the “Gen - LASL” on the 15 minute OpsMon Dashboard and the available Regulation DOWN Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Monitor frequency and run SCED as often as required. |
| Log | Log actions taken |

## 3.3	System Failures

Procedure Purpose:  To ensure that frequency is maintained in the event of an AGC failure.

| Protocol Reference | 6.5.9(1) | 6.5.9.1(2) | 6.5.9.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-005-0.2b R7 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### SCED Failure |  |
| NOTE | When RLC sees that the SCED solution has not updated within the last 605 seconds, emergency base points (EBP) will automatically activate. This will have to be turned off manually by the operator when SCED recovers. After the EBP flag turns ON, enter increment/decrement MW and commit it, so that EBPs are actually sent out. Any time EBPs are activated, SCED solutions are being blocked from being communicated to MPs. |
| 1 | IF: - Any module of the SCED Workflow Controller fails; THEN: - Manually run the SCED process. |
| 2 | IF: - SCED still fails after manually running, AND - EBPs have automaticly activated; THEN: - Contact the Help Desk, - Initiate an Emergency Notice Hotline call to QSEs, - If West – North (IROL) constraint is active, use script in step 3 - Notify Resource Operator to post a message on MIS Public utilizing Notice Builder, - Notify Transmission Operator to make Hotline call to TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me. That is correct, thank you.” |
| 3 | Script to use if West – North IROL constraint was active when SCED failed: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. The West to North is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. |
| 5 | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Emergency Notice, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], SCED basepoint are now valid and ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me. That is correct, thank you.” |
| Log | Log all actions taken and any issues with the Market Participants. |
| ### SCED Data Input Failure |  |
| 1 | IF: - SCED receives data input failures and gives erroneous results; THEN: - Manually activate EBP, - Contact the Help Desk, - Initiate the Emergency Notice Hotline call - If West – North (IROL) constraint is active, use script in step 2, - Notify Resource Operator to post the message on MIS Public utilizing Notice Builder, - Notify the Transmission Operator to make Hotline call to TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to data input failure to SCED. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | Script to use if West – North IROL constraint was active when data failure occurred: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. The West to North is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Follow steps 4 and 5 above as needed. |
| ### RLC Failure |  |
| 1 | The Resource Limit Calculator (RLC) can fail independently of AGC. If RLC fails, SCED will not function (invalid results), even though it shows available. A RLC failure will be displayed to the Operator in the upper right corner of the RLC display as follows: - Process Status: RLC Up (Normal Operation) - Process Status: RLC Down (will be displayed in RED when failed) - RLC (PI Alarm) will be flashing RED. |
| NOTE | Regulation is functioning, RRS is not. LFC (AGC) will automatically switch to EBP mode. |
| 2 | IF: - RLC has failed; THEN: - Verify the status of AGC - IF AGC is also failed, proceed to the EMS (LFC and RLC) Failure procedure - Contact the Help Desk, - Initiate an Emergency Notice Hotline call to QSEs - If West – North (IROL) constraint is active, use script in step 3, - Notify Resource Operator to post the message on MIS Public utilizing Notice Builder - Notify Transmission Desk Operator to make Hotline call to TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to a SCED failure. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me. That is correct, thank you.” |
| 3 | Script to use if West – North IROL constraint was active when RLC failed: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. The West to North is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output. ERCOT may issue Emergency Base Points until this issue has been resolved. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. |
| 5 | WHEN: - RLC is restored; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Emergency Notice, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel Emergency Notice with TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], SCED solutions are now valid and ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me. That is correct, thank you.” |
| Log | Log all actions taken. |
| ### LFC (AGC) Failure |  |
| NOTE | When LFC (AGC) is paused or suspended and RLC and SCED are functioning, then Regulation, RRS and EBP are not functioning. |
| 1 | IF: - LFC is not functioning as indicated by: - AGC is SUSPENDED or PAUSED OR - “Last AGC Cycle” time on Generation Area Status display is not updating; THEN: - Verify the status of RLC - If RLC is also failed, proceed to the next procedure “EMMS Failure” - If RLC is still functioning properly, - Contact Help Desk, - Continue with this procedure REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency control, THEN: - Direct selected QSE to go on constant frequency, - As time permits, issue electronic VDI, - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into ‘Monitor” mode. Typical Script for Constant Frequency: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing you to go on constant frequency until further notice due to an LFC failure. Please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs - Notify Resource Operator to post the message on MIS Public utilizing Notice Builder, - Notify Transmission Operator to make Hotline call to TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to LFC failure and has placed a QSE on Constant Frequency to provide regulation. SCED Base Points are valid and should be followed. [QSE] please repeat this back to me. That is correct, thank you.” |
| 3 | MONITOR: - Frequency and capacity availability for QSE on constant frequency, AND/OR - The QSE on constant frequency notifies ERCOT of capacity issue; THEN: - Determine available capacity for SCED and enter an operator manual offset, OR if no SCED room - Issue electronic VDI(s) as needed, to Commit/Decommit additional generation to maintain Grid Reliability. - Choose “COMMIT or DECOMMIT” as the Instruction Type from Resource level - Enter “capacity or capacity surplus” in “other information” |
| 4 | WHEN: - ERCOT AGC Control is functioning properly; THEN: - Direct QSE to come off “Constant Frequency” by ending the electronic VDI, - Place ERCOT AGC back into “ON” mode, - Initiate Hotline to cancel the Emergency Notice to QSEs, - Notify Resource Operator to cancel the MIS posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functional and ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me. That is correct, thank you.” |
| Log | Log all actions taken. |
| ### EMMS (LFC and RLC/SCED) Failure |  |
| NOTE | Regulation, RRS, UDBP, BP, EBP, and manual offset not functioning. |
| 1 | LFC (AGC): - AGC is SUSPENDED or PAUSED, - “Last ACE crossing zero” time on the Generation Area Status page is not updating, - AGC operation adversely impacts the reliability of the Interconnection, - SCED and EMS are not functioning, - Problem cannot be resolved quickly RLC: - Process Status: RLC Down will be displayed in RED in the upper right hand corner of the RLC display - RLC (PI Alarm) will be flashing RED. REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency Control; THEN: - Direct the selected QSE to go on constant frequency - As time permits, issue an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into “Monitor” mode Typical Script for Constant Frequency: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing you to go on constant frequency until further notice due to an EMMS failure. Please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs, - Notify Resource Operator to post the message on MIS Public utilizing Notice Builder, - Notify Transmission Operator to make Hotline call to TOs Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to an LFC and SCED failure. ERCOT has placed a QSE on Constant Frequency. All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT. ERCOT may issue unit specific deployments to Resources as required. [QSE] please repeat this back to me. That is correct, thank you.” |
| 3 | MONITOR: - Frequency and Capacity availability for QSE on constant frequency, AND/OR - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Determine which QSE has the most available Capacity, - Issue a unit specific instructions to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |
| 4 | IF: - There is no longer any available capacity to issue unit specific deployments; THEN: - Issue electronic VDI(s) as needed, to Commit/Decommit additional Generation to maintain Grid Reliability - Choose “COMMIT or DECOMMIT” as the Instruction Type from Resource level. - Enter “capacity or capacity surplus” in “other information” |
| 5 | WHEN: - AGC and RLC is restored; THEN: - Direct QSE to come off constant frequency by ending VDI, - Place ERCOT AGC back into “ON” mode, - Cancel VDI(s) for additional generation, if issued, - Initiate Hotline to cancel Emergency Notice to QSEs, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel Emergency Notice with TOs. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At, [xx:xx], LFC is now functional and SCED solutions are valid. ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me. That is correct, thank you.” |
| Log | Log all actions taken. |

## 3.4	Potential DCS Event

Procedure Purpose:  To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.4.2(2)(a)(ii) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-1 R2.4, R6.2 | EOP-001-0.1b R5 | EOP-002-3.1 R5, 6.1 |  |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC Recovery Criteria | Restore system frequency to the following limit within 15 minutes: - Scheduled Frequency if it was greater than or equal to scheduled Frequency prior to the disturbance, OR - Its pre-disturbance value if it was less than scheduled frequency prior to the disturbance. ERCOT shall fully restore the minimum Contingency Reserve requirement of ERCOT Region’s Largest Single Contingency (1375 MW) within 90 minutes. The 90 minute restoration period begins at the end of the Disturbance Recovery period which is when system frequency is restored as described above. ERCOT will restore Responsive Reserves to 2300 MW or greater, as soon as possible. |
| DCS | - A loss of Generation, equal to or greater than 1100 MW (consisting of a single generator or the total of multiple generators within 1 minute), or there is NO indication of a Generation loss and the magnitude of the event is determined to be greater than 1000 MW - Determine the magnitude of the event by using the “Raw ACE” tag, Analyze the change in this tag after a minimum of 30 seconds to avoid the initial overshoot. Example: If the “Raw ACE” pre-disturbance value is +150 MW, and post disturbance (30 seconds) value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. - It can be assumed that a potential NERC Reportable DCS Event has occurred |
| NOTE | The steps below will need to happen quickly, let phones ring, or if available, another desk will take the calls. |
| 1 | IF: - ERCOT experiences a low frequency disturbance; THEN: - Immediately check to ensure that SCED sees the units correct telemetry (HSL of zero or Resource Status of “off”), Contact the QSE(s) if telemetry needs to be changed, - If SCED does not automatically execute within 60 seconds of the event, manually execute a SCED run, - Enter a manual off-set as necessary. |
| 2 | IF: - Frequency dropped below 59.7 Hz; THEN: - Load Resources have deployed on UFR. |
| NOTE | If Load Resources are deployed it may become necessary to periodically execute SCED manually and/or use the manual offset to control frequency. |
| 3 | WHEN: - System frequency has been restored; THEN: - Make Hotline call to QSEs to recall Load Resources. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is recalling all Load Resources. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| PRC Below 2300 | IF: - Physical Responsive Capability falls below 2300 MW; THEN: - Implement EEA (see specific procedure). |
| Log | Make log entry. |

## 3.5	Monitor Capacity and Reserves and Respond to Shortages or Surplus

Procedure Purpose:  Monitoring sufficient operating reserves.  Deploying and recalling Non-Spin and dealing with capacity surplus.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-1 R2.4 | IRO-005-3.1a R1.4, R1.5, R4 |  |  |

| Version: 1 | Revision: 6 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Day-Ahead process, the Adjustment Period process, and the Real-Time process must be utilized before ordering Resources to specific output levels with Emergency Base Point instructions. |
| ## Insufficient Generation |  |
| Capacity Shortage | Triggers to deploy Non-Spin MONITOR: - The OpsMon Dashboard - 01 SCED GEN ONLINE and scroll down to Lookahead Load Ramping from MTLF - Avail CAP 30Min represents (HASL – Gen) – (30 minute load ramp) IF: - Avail_CAP_30Min < 0 THEN: - Coordinate with the Resource Operator to deploy half of available Non-Spin. IF: - Avail_CAP_30Min < -300, OR - PRC is < 2500 MW; THEN: - Coordinate with the Resource Operator to deploy all of available Non-Spin. |
| Recalling Non-Spin | WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 2800 MW; THEN: - Coordinate with the Resource Operator to recall half of the deployed Non-Spin. WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 3000 MW; THEN: - Coordinate with the Resource Operator to recall all of the deployed Non-Spin. |
| ## Surplus Generation |  |
| SCED Surplus | MONITOR: - The Generation Area Status Page IF: - (GEN-LDL) < 200 MW; THEN: - Consult with RUC Operator to ensure HRUC is seeing the situation and is decommitting Resources, - If needed, issue VDI(s) to Resource(s) to help alleviate the surplus - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| Log | Log all actions taken as necessary. |

## 3.6	Monitor and Control Time Error Correction

Procedure Purpose:  This procedure will establish the standard for implementing time error correction.  ERCOT ISO is the Reliability Coordinator and Balancing Authority that implements and terminates ERCOT Time Corrections in accordance with ERCOT Protocols and Operating Guides.  ERCOT Reliability Coordinator is the Interconnection Time Monitor within the ERCOT Interconnection.

| Protocol Reference | 6.5.7.6.1(8)(b) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.1(3)(c)(vi) | 2.2.9.1 | 2.2.9.2 |  |
| NERC Standard | BAL-004-0 R1, R2, R3, R4 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Requirements | - When time error is equal to or greater than +/- 30 seconds, ERCOT may initiate a time correction. - Time Error Corrections normally start and end on the hour or half-hour. - The Time Error Correction will be ended when the error is less than +/- 27.0 seconds. - The time correction may be postponed if it is determined that load patterns in the immediate future will result in the desired time correction - Time Error Correction Notifications shall be labeled alphabetically on a monthly basis (A-Z). In the succeeding month, the first Time Error Correction will revert back to “A”. |
| Log | Log the start time, stop time, Time Error ID letter, time error, and Frequency Offset for each start and termination. |
| Initiating Time Error Correction | IF: - Time error is greater than +/- 30 seconds; THEN: - Start Time Error Correction Schedule, - Enter the appropriate Time Error ID letter, - Enter the frequency offset using – 0.02 for fast time correction (59.98 Hz) or +0.02 for slow time correction (60.02 Hz), - Enter a Start Time later than the current time AND enter a Stop Time later than the scheduled start time, - Before starting the Time Error, notify the QSEs via a Hotline call of the start time and frequency offset, - Log in the Operator’s Log start time, stop time, Time Error ID letter, time error, and frequency offset for each start and termination. Typical Script: “This call requires everyone to remain on the line until it is complete. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is initiating a Time Error Correction, we will enter the frequency offset using [-0.02] or [+0.02] at [time]. The current time error is [time]. Thank you.” |
| NOTE | If a Time Error Correction is prematurely terminated or a scheduled Time Error Correction is cancelled for reliability considerations, log all actions taken and wait at least one hour between sending the termination and re-initiation notices. |
| Terminating Time Error Correction | Monitor the Time Error until it reaches an acceptable value (+/- 27.0 seconds) - Time Error Correction may be terminated after five hours, or after any hour it has reached an acceptable value of +/- 27.0 seconds. - Notify all QSEs using a Hotline call, if available, before ending the time correction. Typical Script: “This call requires everyone to remain on the line until it is complete. This is ERCOT Operator [first and last name]. ERCOT is ending the Time Error Correction at [xx:xx]. The current time error is [time]. Thank you.” |

## 3.7	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R2, R4.2 | EOP-003-1 R1 | IRO-002-2 R6, R8 | IRO-003-2 R1 |
|  | IRO-004-2 R3 | IRO-005-3.1a R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 R1 | TOP-002-2.1b R10 |
|  | TOP-004-2 R1, R2, R6, R6.6 | TOP-006-2 R5 | TOP-007-0 R3, R4 | TOP-008-1 R1 |

| Version: 1 | Revision: 2 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Issue Watch & Deploy Non-Spin | WHEN: - Notified by the Transmission Operator that Non-Spin needs to be deployed in the Houston area for the North-Houston Interface; THEN: - Using the hotline, issue a Watch, - Resource Operator will deploy the Non-Spin Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North to Houston interface. ERCOT will be deploying Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| Issue Emergency Notice & Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the hotline, issue the Emergency Notice Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT has issued an Emergency Notice for the North to Houston interface and has issued you an electronic directive for the deployment of specific Load Resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the hotline, cancel the Emergency Notice, Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Emergency Notice for the North to Houston interface and has issued you an electronic directive for the recall of Load Resource deployments. ERCOT is reminding everyone that a Watch is still in effect until further notice. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Using the hotline, cancel the Watch, Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the North to Houston interface. ERCOT has recalled Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log the actions taken. |

## 5.4	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| RESERVES | If 1375 MW of PRC is not restored within 75 minutes, reduce MW loading on Resource(s) to bring reserves up, if available. |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - PRC ≥ 1375 MW; THEN: - Using the Hotline, notify all QSEs of firm load restoration. Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is restoring firm load. [QSE] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Move From EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load has been instructed to be restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 3 to EEA 2 - Coordinate with the Resource Desk and recall Load Resources Typical script for Load Resource recall: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 3 to EEA 2. QSEs are to recall all Load Resources at this time. [QSE] please repeat this back to me. “That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| NOTE | Once Load Resources are recalled, they have 3 hours to return to service. |
| ### Move From EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 2 to EEA 1 - Coordinate with the Resource Desk and recall ERS Resources. Typical script for ERS recall: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2 to EEA 1. QSE’s are to recall all ERS Resources at this time. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | Once ERS Resources are recalled, they have 10 hours to return to service. |
| ### Move From EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Uncheck the EEA flag in EMS and make inactive, - Using the hotline, notify all QSEs of the termination of EEA. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is terminating EEA 1. A Watch still remains in effect. [QSE] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Cancel Watch |  |
| 1 | WHEN: - PRC is ≥ 2800 MW, AND - Non-Spin has been recalled; THEN: - Cancel Watch Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. At this time, Resource testing may resume. [QSE] please repeat this back to me. That is correct, thank you.” |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated Nerc Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Udated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |