## Power Operations Bulletin # 621

ERCOT has posted/revised the Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.3	Notifications for Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.9.4.1 | 6.5.9.4(5) | 6.5.7.6.2.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.1(1) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4 | EOP-001-0 R3.1 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005-2 R1.4, R1.5, R4 |

| Version: 1 | Revision: 9 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at management’s discretion, may issue an appeal through the public news media for voluntary energy conservation at any time. - System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. |
| ### Advisory |  |
| Issue Advisory | IF: - PRC falls < 3000 MW; THEN: - Coordinate with the Real-Time Operator, AND - Post message on MIS Public using Notice Builder. Typical MIS posting: “ERCOT is issuing an Advisory for Physical Responsive Capability less than 3000 MW.” |
| Cancel Advisory | WHEN: - PRC > 3000 MW; THEN: - Coordinate with Real-Time Operator, AND - Cancel message on MIS Public. |
| Log | Make log entry. |
| ### Watch |  |
| Issue Watch | IF: - PRC falls < 2500 MW; THEN: - Coordinate with the Real-Time Operator, AND - Post message on MIS Public using Notice Builder. Typical MIS postings: “ERCOT is issuing a Watch for Physical Responsive Capability less than 2500 MW”. |
| Cancel Watch | WHEN: - PRC > 2800 MW; THEN: - Coordinate with Real-Time Operator, AND - Cancel message on MIS Public. |
| Log | Make log entry. |

## 3.4	Responding to Capacity Shortages

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Capacity Shortages as requested by the Real-Time Operator.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R3.1 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If Non-Spin is being deployed 20 minutes past the top of the hour, deselect Off-line Resources whose COP Non-Spin Resource Responsibility is “ZERO” for next hour. (Refer to Desktop Guide Resource Desk Section 2.2) |
| Deployment | WHEN: - Notified by the Real-Time Operator to deploy Non-Spin; THEN: - Coordinate with the Transmission Operator to verify the Non-Spin does not create congestion, - Deploy Non-Spin, (Refer to Desktop Guide Resource Desk Section 2.2) |
| Additional Deployment | IF: - Additional Non-Spin becomes available going into next hour; THEN: - Determine if the additional Non-Spin is needed, - Deploy if needed (Refer to Desktop Guide Resource Desk Section 2.2) |
| Commit | IF: - Notified by a QSE that their Off-line Non-Spin obligation has ended, AND - PRC < 2500 MW; THEN: - Request that the Resource stay On-line, - Issue an electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose Resource tab - Choose Commit as the Instruction Type - State Capacity in Other Information |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| Termination | WHEN: - Notified by the Real-Time Operator that the Non-Spin is no longer needed; THEN: - Recall as instructed (Refer to Desktop Guide Resource Desk Section 2.2) |

## 3.6	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service and/or Load Resources for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0 R2, R4.2 | EOP-003-1 R1 | IRO-002-2 R6, R8 | IRO-003-2 R1 |
|  | IRO-004-2 R3 | IRO-005-2 R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 | TOP-002-2b R10 |
|  | TOP-004-2 R1, R2, R6, R6.6 | TOP-006-1 R5 | TOP-007-0 R3, R4 | TOP-008-1 R1 |

| Version: 1 | Revision: 9 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Deploy Non-Spin | WHEN: - Notified by the Transmission Operator to deploy Non-Spin in the Houston area for the North-Houston Interface; THEN: - Deploy Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) (Refer to Desktop Guide Resource Desk Section 2.2) |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Deploy Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by XML (Refer to Desktop Guide Resource Desk Section 2.1) |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Recall Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.1). |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Recall Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML, (Refer to Desktop Guide Resource Desk Section 2.2). |
| Log | Log the actions taken. |

## 3.7	Deploying Non-Spin for Local Congestion

Procedure Purpose:  Mitigating local congestion.

| Protocol Reference | 6.1 (3) | 6.5.1.2 (1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - Notified by the ERCOT Transmission and Security operator that specific Resources carrying Non-Spin are needed for local congestion; THEN: - Deploy specific Resources |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| 2 | IF: - The Non-Spin obligation ends for the Resource deployed, AND - The Resource is still needed; THEN: - Issue an electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose Resource tab - Choose Commit as the Instruction Type - State Local Congestion in Other Information |
| 3 | IF: - An additional Resource is needed to be deployed; THEN: - The previous Resource deployed will need to be deployed again, along with the additional Resource. |
| Termination | IF: - Notified by the ERCOT Transmission and Security Operator that Non-Spin is no longer needed; THEN: - Recall the Non-Spin, by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.2). |
| LOG | Log actions. |

## 4.1	Approve/Reject Resource Decommitment Request

Procedure Purpose:  Review and approve or reject Resource decommitments in the Operating Period.

| Protocol Reference | 6.4.6 | 6.4.6.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2a R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Approve/Reject Decommitment QSE Requests in Operating Period |  |
| NOTE | - The Operating Period is the two-hour period comprised of the Operating Hour and the clock hour preceding the Operating Hour - A QSE may request to decommit a Resource other than a QSGR for any interval that is not a RUC-Committed Interval by verbally requesting ERCOT to consider its request - ERCOT shall review the requests in order of receipt - A QSE may decommit a QSGR without any request for any interval that is neither a RUC-Committed Interval nor an interval in which a manual override by the ERCOT Operator. |
| NOTE | If a combined cycle train (CCT) is transitioning from one configuration to another, this is not a QSE requested decommit. |
| 1 | IF: - A QSE requests to decommit a Resource that has been Self-Committed (QSGRs are not required to get prior approval before decommitting); THEN: - Determine if the Resource is receiving negative LMPs - If negative LMPs, proceed with this procedure - If no negative LMPs, proceed to step 2 IF: - A Resource is receiving negative LMPs; THEN: - Determine if Resource is carrying A/S - If yes, inquire how A/S will be replaced - Determine if there could be a capacity issue if Resource is decommitted (PRC < 2500) - If Resource is not allowed to decommit, override HDL to LSL (see Desktop Guide Common to Multiple Desks Section 2.13) - If override is used, the Resource will not be able to carry A/S, and will need to be marked as undeliverable - If no capacity issue exists, grant approval to decommit - Issue an electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Resource” tab - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type tab |
| 2 | IF: - A QSE requests to decommit a Resource that has been Self-Committed (QSGRs are not required to get prior approval before decommitting); THEN: - Determine if the Resource is carrying A/S. - If yes, inquire how A/S will be replaced, - Determine if there could be a capacity issue if Resource is decommitted - If no capacity issue exists, proceed - Notify the Transmission Operator to make determination if needed for congestion management, - If not needed for congestion management. - Issue electronic VDI (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Resource” tab - Choose “QSE REQUESTED DECOMMIT” as the Instruction Type tab |
| 3 | Log actions taken. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 3.16 (4) | 5.2.2.2 | 6.4.8.1 | 6.4.8.1.1 |
| --- | --- | --- | --- | --- |
|  | 6.4.8.1.2 | 6.4.8.1.3 | 6.4.8.2 | 6.4.8.2.2 |
|  | 6.5.9(4) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. - See Desktop Guide Common to Multiple Desks Section 2.15 if the savecase function fails when running a SASM |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs of time the SASM will begin Time X + 30min = Determine amount of A/S to be procured Time X + 35min = Execute SASM Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs forA/S Resource Responsibility |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify that the RUC Operator has issued an Emergency Notice by making a Hotline call to the QSEs, - Procure adequate Ancillary Services for the next operating day through a SASM, (Refer to Desktop Guide Resource Desk Section 2.8.4) |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor about the remaining A/S insufficiencies. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline Notification and post message on MIS Public using Notice Builder, - Procure more Ancillary Services through a SASM (Refer to Desktop Guide Resource Desk Section 2.8.3). Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reason]. At [xx:xx] ERCOT will open a SASM to procure the additional Ancillary Services for hours [hours] for operating day [day]. [QSE] please repeat this back to me. That is correct, thank you.” |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor about the remaining A/S insufficiencies. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | Once verified that all Ancillary Service has been procured, cancel the Watch: Typical Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me. That is correct, thank you.” |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace A/S capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the A/S capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to Desktop Guide Resource Desk Section 2.8.1 or 2.8.2). |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies. |
| 3 | IF: - A QSE is unable to provide their SASM awards; THEN: - Determine if there is time to open an additional SASM, AND - Send failure to provide notification. |
| 4 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 5 | Send information in an email to the following distribution list: - SASM |
| ### Daily Reconfiguration SASM |  |
| Daily SASM Timeline | Reconfiguration Supplemental Ancillary Service Market (SASM) allows QSEs to modify their Ancillary Services (AS) during the Operating Day. Reconfiguration SASMs are expected to be run daily for Operating Hours 13 thru 24. The timeline is as follows: Time 08:45 = Determine type and amount of A/S to procure. Time 09:00 = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time 09:15 = Notify QSEs with awards Time 09:30 = Validate COPs and A/S schedules |
| 1 | QSEs must have valid AS Offers of an amount equal to or greater than the requested reconfiguration amount; IF: - There are not sufficient AS Offers to cover the total requested amount; THEN: - Cancel the SASM, - Post message on MIS public utilizing Notice Builder. (Refer to Desktop Guide Resource Desk Section 2.8.7). Typical MIS Posting: ERCOT is cancelling the Daily Reconfiguration SASM due to insufficient AS Offers. |
| 2 | IF: - The reconfiguration SASM is not approved and published; THEN: - QSEs will retain their original AS Supply Responsibility and should update their COPs accordingly. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| LOG | Log all actions taken. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard | EOP-001-0 R4.1, 4.2, R4.4 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | If 1375 MW of PRC is not restored within 75 minutes, reduce MW loading on Resource(s) to bring reserves up, if available. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC ≥ 1375 MW; THEN: - Transmission Operator will restore firm load. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load have been instructed to be restored; THEN: - When instructed by the Real-Time Operator to recall Load Resources - Send XML message to recall Load Resources, (see Desktop Guide Resource Desk Section 2.1) - Make EEA 3 to EEA 2 posting to MIS Public using Notice Builder. - Use preformatted notice |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Send XML message to recall 10 MIN/30 MIN ERS (see Desktop Guide Resource Desk Section 2.9) - Make EEA 2 to EEA 1 posting to MIS Public using Notice Builder. - Use preformatted notice |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Terminate EEA 1 by posting to MIS Public using Notice Builder. - Use preformatted notice “EEA 1 to Normal” |
| ### Recall Non-Spin and Cancel Watch |  |
| 1 | WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 2800 MW; THEN: - Coordinate with the Real Time Operator and recall half of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.2). WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Real Time Operator and recall all of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.2) - . |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outagesUpdated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |
| 3.1 7.2 | 1.0 / 8 1.0 / 9 | Updated step ONTEST Updated step 1 of Implement EEA Level 1 | August 29, 2012 |
| 2.2 7.2 8.1 | 1.0 / 1 1.0 / 10 1.0 / 4 | Added Hotline Call Communication Updated Implement EEA Level 1 step 2, Implement EEA Level 2 step 1 and ERS Business Hour Changes Updated 1st Note, step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.3 3.4 3.6 3.7 4.1 5.1 7.3 | 1.0 / 9 1.0 /12 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 11 1.0 / 9 | Non-Spin deployment messages are now automated Non-Spin deployment messeages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Updated steps 1 & 2 Updated steps Note, Procurement Timeline & 1. Added new procedure, Daily Reconfiguration SASM Updated step 1 of Cancel Watch | March 1, 2013 |