## Power Operations Bulletin # 622

ERCOT has posted/revised the Shift Supervisor Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.2	Capacity and Reserve Monitoring

Procedure Purpose:  To monitor capacity for SCED dispatch and total system capacity for providing Ancillary Services.

| Protocol Reference | 6.3.2(2) | 6.5.9.1(1)(a) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R3.1, R4.2 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-002-2 R5 | IRO-005-3.1a R1.4, R1.5 |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Capacity Monitoring |  |
| 1 | Monitor the Excel MAI: IF: - Load forecast is reasonable AND “Adj. Max Capacity Room” shows insufficient capacity; THEN: Verify that HRUC has identified the insufficient capacity situation. |
| 2 | IF: - HRUC has not identified the insufficient capacity; THEN: - Have RUC Operator verify that HRUC is using a reasonable forecast AND update if necessary, - Ensure Resource commitments are being made, if needed. |
| 3 | Triggers to deploy Non-Spin MONITOR: The Generation Area Status Page and the OpsMon Dashboard IF: - Avail_CAP_30Min < 0; THEN: - Verify that the Resource Desk Operator has deployed half of available Non-Spin. IF: - Avail_CAP_30Min < -300, OR - PRC is < 2500 MW; THEN: - Verify that the Resource Operator has deployed all of available Non-Spin, IF: - Additional capacity is required, THEN: - Verify the RUC Operator is aware of the requirement to commit additional Resources for the next hour. |
| 4 | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS_Dev folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue a VDI, instructing resources to be removed from service, - Priority should be on Resources that resolve congestion. |

## 3.3	Disseminating Information to System Security Response Group (SSRG)

Procedure Purpose: To communicate information concerning disturbances or unusual occurrences to appropriate parties in the Interconnection.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.8 |  |  |  |
| NERC Standard | CIP-001-2a R1, R2, R3 | EOP-004-1 OE-417 |  |  |

| Version: 1 | Revision: 6 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Threats can be viewed at the following links: http://www.esisac.com/SitePages/Home.aspx, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert levels are listed in the Security Alert Plan. |
| NOTE | - The SSRG e-mail exploder list is used to disseminate information to the SSRG members of the ERCOT Region when an SSRG conference call is not necessary. - This information is intended for use within the industry and not for public release. - At the beginning of each e-mail state the follow “This information is intended for use within the industry and not for public release” - At the bottom of each e-mail, be sure to include a Confidentiality Notice and your signature. - The Reliability Coordinator Information System (RCIS) is used to disseminate information to other RCs in other Interconnections. - Do not list the entity name on the SSRG e-mails or on the RCIS. |
| NOTE | The only notification that is required is for suspected sabotage (cyber or physical). However, some entities make notifications on the following: - Copper thefts - Substation break-in - Vandalism - Malicious mischief - Suspicious photos |
| 1 | IF: - Notified by a QSE or TO of a disturbance or unusual occurrence; THEN: - Verify the following: - Is the occurrence considered “theft of property”? (proceed to Step 2) - Is the occurrence being investigated as a “suspected sabotage event” (proceed to Step 3). |
| 2 | IF: - Theft of property can be reasonably determined and the incident is not related to a suspected sabotage event; THEN: - Verify that local Law Enforcement Agencies have been notified, - Send an e-mail to the ‘SSRG’ distribution list, stating in the e-mail that the event is currently not considered as an act of suspected sabotage. |
| 3 | IF: - The entity has determined the event to be a suspected sabotage event or if the entity is unable to make that determination without further investigation/information; THEN: - Verify that the FBI has been notified, - Send an e-mail to the ‘SSRG’ distribution list, stating in the e-mail that the event is considered an act of suspected sabotage OR further investigation/information is needed to determine if event is an act of suspected sabotage, - Notify TOs and QSEs via Hotline with information you have - A separate call needs to be made to HHGT TO, - Post on the RCIS using “CIP Free Form” (see Desktop Guide Shift Supervisor Section 2.2), - Coordinate with the Manager, System Operations and/or Control Room Operations Manager to determine if procedure 3.4 SSRG Conference Calls is necessary and for any NERC and DOE reporting requirements. Typical Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT notified the System Security Response Group (SSRG) of a suspected sabotage event [give information]. Please notify your SSRG representative.” |
| 4 | WHEN: - Updates are received; THEN: - Send an updated e-mail to the ‘SSRG’ distribution list, - Update RCIS as needed |
| Physical | For suspected physical sabotage at the ERCOT facilities, refer to ERCOT Guideline GL7.8.1 located under the “Sabotage Event Recognition” tab in each procedure manual. RCIS and SSRG postings will also be required. |
| Cyber | When notified by Cyber Security of a reportable event at ERCOT, collect the information to post under “CIP Free Form” on the RCIS. |

## 3.4	SSRG Conference Calls

Procedure Purpose: To communicate information concerning disturbances or unusual occurrences to appropriate parties in the ERCOT Region by making a SSRG conference call.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | CIP-001-2a R1, R2, R3 | EOP-004-1 |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT will initiate a conference call with QSEs and TOs using the ERCOT conference bridge: - The Manager, System Operations and/or Control Room Operations Manager, will provide an SSRG conference call number, and the associated date and time of the call, to the Shift Supervisor, - Notifying all QSEs and TOs via a hotline call and instructing them to notify their SSRG designee of the scheduled SSRG conference call - Send e-mail to the “1 SSRG (System Security Response Group)” distribution list, providing them the information needed to participate. |
| Threat & Emergency Classifications | Threats and emergencies can be classified as, but are not limited to, the following four SSRG event-types: 1. Internal to ERCOT ISO: Physical Security: Verifiable attacks or sabotage, or threats of attacks or sabotage that could jeopardize the operation of physical equipment within the electrical boundaries of the ERCOT grid that have a direct effect on the reliability of the ERCOT grid. This could be, but is not limited to, generation equipment, transmission equipment, and communication equipment. b. Cyber Security: Verifiable loss of control of the ERCOT EMS or MMS that is identified by EMMS Production Support as an actual or probable act of sabotage or the loss of control by any of the market participants EMS Systems that is reported to ERCOT as an act of sabotage. 2. External to ERCOT ISO: a. Physical Security: Verifiable attacks or sabotage, or threats of attacks or sabotage that could jeopardize the operation of physical equipment in any electrical sector outside of the boundaries of ERCOT. b. Cyber Security: Verifiable loss of control over the EMS System of any participant in the electrical sector outside of the boundaries of ERCOT that is identified as an actual or probable act of sabotage. 3. Pandemic 4. Other unforeseen business continuity events (not to include grid instability) |
| NOTE | - The SSRG conference call may be used for System Security Response Group Notifications and as warranted by the Manager, System Operations and/or Control Room Operations Manager. - When there is a change in the Threat Alert Level as identified on the Electric Sector Information Sharing and Analysis Center (ESISAC) website, www.esisac.com, - To disseminate information and develop plans related to system emergencies and business continuity threats, - To conduct a quarterly test with the minimum objective of reviewing and updating the contact list (test to be conducted in February, May, August and November) - Hot line call should allow time for all SSRG members to be notified and participate in SSRG conference call. |
| Management Notification | When there is a change in the Threat Alert Level or other emergency events occur and an SSRG conference call is required, NOTIFY: - ERCOT Manager, System Operations and/or Control Room Operations Manager. - ERCOT Director of Security or designee. Refer to SharePoint and/or Desktop Guide Shift Supervisor Section 2.5. |
| QSE Notification | Using the Hotline: - Notify QSEs of the SSRG conference call. - Provide the time and phone number for the SSRG conference call. - Instruct them to notify their SSRG representative of the SSRG conference call. Typical Script: “This is [first and last name] at ERCOT. There will be an SSRG conference call today at [time] CPT. The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. Please notify your SSRG representative. The conference call number is 1-866-642-1665. Participants pass code is [code]. Any questions? Thank you.” |
| TO Notification | Using the Hotline: - Notify TOs of the conference call. - Provide the time and phone number for the conference call. - Instruct them to notify their SSRG representative of the conference call. Typical Script: “This is [first and last name] at ERCOT. There will be an SSRG conference call today at [time] CPT. The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. Please notify your SSRG representative. The conference call number is 1-866-642-1665. Participants pass code is [code]. Any questions? Thank you.” |
| Send E-mail | Send an e-mail to “1 SSRG” to make notification of the SSRG conference call. Typical Subject line for e-mail: SSRG conference call Typical Script for e-mail: An SSRG conference call has been schedule for today at [time] CPT. The topic will be [quarterly test call, physical security, cyber security, pandemic or other topic]. The conference call number is 1-866-642-1665. Participant pass code is [code]. Participation is mandatory. Include signature on email. |
| Log | Log all actions taken. |

## 3.5	Review Outage List

Procedure Purpose:  Verify known outages for the current day.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | Navigate to the Outage Scheduler or associated RUC displays in the MMS. Outage Scheduler>Outage Overview>OS Today’s Outages Market Operation>Reliability Unit Commitment>*RUC Displays>NDP Displays>Outaged Equipment Summary Alternatively, navigate to the Transmission Outages in the Market Information System. - MIS; Grid; Transmission; Transmission Outages; Approved and Accepted Transmission Outages - MIS; Grid; Transmission; Transmission Outages; Proposed Transmission Outages - MIS; Grid; Transmission; Transmission Outages; Rejected Transmission Outages |
| 2 | Open OS Today’s Outages |
| 3 | Review the list of generation and transmission outages schedule for the current operating day. |
| 4 | Using the Outage Scheduler, verify if resources or facilities reported as Forced Outages are included in the outage list. |
| 5 | If Forced Outages are not listed, notify the Transmission and Security Operator. |
| 6 | Verify with the Transmission and Security and RUC Operator the results of studies for the hours and nodes where these resources and facilities are scheduled to be out of service. |
| 7 | If errors or problems are detected, consult with the Outage Coordinator. |

## 3.6	Monitoring W-N Stability and N-H Voltage Limits

Procedure Purpose: To collect data on the West – North dynamic stability limit and the North – Houston VSAT voltage stability limit for the NERC Reliability Metric.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-004-2 R1 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North stability and the N-H voltage are IROLs; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. |
| NERC | Ensure that the transmission system is operated so that instability, uncontrolled separation, or cascading outages will not occur as a result of the most severe single Contingency and specified multiple Contingencies. |
| 1 | Monitor W-N stability and N-H voltage limits. |
| 2 | If the W-N stability or N-H voltage stability exceed the limit at any time: - Log it under log type “Exceeding Limits”. - Include the date and time of the violation - The system conditions that caused the violation. - Run a System Security Analysis (Real Time Snapshot) Study near the highest flow. (usually run by the Operations Support Engineer) - Save the snapshot in the STNET directory. If the W-N stability limit or N-H voltage stability limit is exceeded for more than 30 consecutive minutes, notify the Manager, System Operations and/or Control Room Operations Manager immediately. |
| 3 | Notify by e-mail (including data from step 2) - Shift Supervisors - Ops Support Engineering - Operations Analysis |

## 3.7	Monitoring Transmission Congestion

Procedure Purpose:  Monitoring transmission congestion to ensure ERCOT remains in a secure state.

| Protocol Reference | 6.3(3) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| TCM | VERIFY: - Constraints with a 2% shift factor or greater are activated at 98%. IF: - A constraint is unsolved in SCED; ENSURE: - All appropriate steps have been taken to resolve (T/S desk section 4.1 Managing Constraints in SCED step 2) IF: - Constraint remains unsolved in SCED; ENSURE: - The Operations Support Engineer is developing a TOAP or MP. IF: - A post-contingency overload reaches 125%; ENSURE: - The Operations Support Engineer has validated whether it is an IROL. |
| LMP Map | Monitor the real-time LMP map: IF: - Any LMP appears unreasonable; THEN: - Notify Manager, System Operations or Control Room Operations Manager, and - Ensure transmission congestion is solvable and not being over-constrained. |

## 4.1	Resource Testing and In-Service Approvals

Procedure Purpose: This procedure provides direction and guidelines for conducting various required testing and approval processes for resources and transmission elements. This procedure does not include testing for the Net Dependable Capacity (NDC) on wind generation.

| Protocol Reference | 3.3.1 | 8.1.1.2.1.1(4) | 8.5.1.1 | 8.5.1.2(1) |
| --- | --- | --- | --- | --- |
|  | 8.5.1.2(3) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 |  |  | Effective Date: March 1, 2013 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Step |  | Action |  |  |  |  |  |
| ### Unit Testing |  |  |  |  |  |  |  |
| NOTE |  | QSEs will submit test requests to shiftsupv@ercot.com. If e-mail is down, a fax will be accepted at (512) 248-6858. Test request forms are located on the ERCOT website under ‘Operating Procedures’. |  |  |  |  |  |
| 1 |  | As requests for unit tests are received, make every reasonable effort to accommodate testing. Reasons for not accommodating testing: - Unit has best shift factor to manage congestion for an outage. Without unit, contingency may reach max shadow price and become unsolvable, - The request exceeds 7 days, - A pattern of repeated requests for the same unit(s) indicate that abuse of the testing privilege may be taking place. If any request is refused for this reason, notify the Manager, System Operations and/or Control Room Operations Manager. |  |  |  |  |  |
| CAUTION |  | If deployment of the testing unit is necessary to maintain system security, direct the test be canceled and deploy as needed. |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT recognizes the need of <Company Name> to test its unit on <date and time>. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | IF the request cannot be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT cannot accommodate the request of <Company Name>for a unit test on <date and time> for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| ### Approved Resources to be ONTEST |  |  |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to be ONTEST. |  |  |  |  |  |
| ### Turbine Governor |  |  |  |  |  |  |  |
| 1 |  | - At all times an All-Inclusive Generation Resource is on-line, its turbine governor must remain in service and be allowed to respond to all changes in system frequency. - When the governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT. - An All-Inclusive Generation Resource may not reduce governor response during abnormal conditions without ERCOT’s consent unless equipment damage is imminent. - Each Generation Entity shall conduct applicable generating governor speed regulation tests on each of its Generation Resources. |  |  |  |  |  |
| ### In Service Approval (or Approval to Energize) |  |  |  |  |  |  |  |
| 1 |  | IF: - A Market Participant makes a request to energize new or relocated equipment; THEN: - Review notification provided by Operations Support Engineering, - Approve the request if notification has been provided; IF: - The equipment has not been approved by Operations Support Engineering, THEN: - Delay the request and notify Operations Support Engineer. |  |  |  |  |  |
| ### Ancillary Service Testing Coordination |  |  |  |  |  |  |  |
| 1 |  | Ancillary Service Testing will be done in coordination with Operations Planning. When contacted by Operations Planning: - Ensure market and reliability conditions exist at all times, - Coordinate all Ancillary Service Testing with the Operations Support Engineer. |  |  |  |  |  |

## 5.2	Ancillary Service Requirements

Procedure Purpose:  To ensure A/S is posted by 0600.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month are correct. This should be verified before the Day-ahead Operator posts the new requirements. |
| 1 | Market Participation>Physical Market>AS Market>AS Plan Ensure the Ancillary Service Requirement and Load Forecast is posted prior to 0600. |
| Last Day of Month | Before 04:00 on the last day of the month, ensure the A/S requirements for the next month have been updated into the AS Plan. |

## 5.3	Notification of a Protective Relay or Equipment Failures

Procedure Purpose:  Be aware and respond if needed to protective relay system failures when notified by a QSE or TO.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 6.2.3 | 6.2.4 |  |  |
| NERC Standard | PRC-001-1 R2, R2.2 |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Protective Relay or Equipment Failure |  |
| NERC | “If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible.” |
| NOTE | Protective relay systems include: relays, associated communications systems, voltage and current sensing devices, station batteries, and DC control circuitry |
| 1 | When notified by a QSE or TO that a protective relay or equipment failure reduces system reliability: - Ask the QSE or TO how it reduces ERCOT Grid system reliability and if any corrective actions have been taken, - Ask the QSE or TO if notifications have been made to any other affected TOs, - Notify the Operations Support Engineer to verify that system reliability has been affected. If so, a corrective action must be taken within 30 minutes, - Determine if other TOs are affected by this failure and make notification by phone. |
| 2 | - After notification from a TO or QSE, NOTIFY by e-mail: - OPS Support Engineering - Operations Analysis - Shift Supervisors - The subject line of the e-mail should read “Protective Relay or Equipment Failure.” - Include in the e-mail: - Entity Name - Brief description - Contact information - Any significant information |
| 3 | If a TO or QSE e-mails a – “Mis-Operation Relay report that has occurred in the past, forward to the above identified e-mail address. |
| 4 | Log information. |
| ### Protective Relay Outages |  |
| NOTE | Protective relay maintenance that ERCOT ISO has been made aware of can be found on the Outage Calendar located on the System Operations SharePoint. |
| Planned Outage | IF: - Notified that a relay is going to be removed from service (Planned); THEN: - Verify information is on the Outage Calendar located on the System Operations SharePoint Site; IF: - Notification is posted; THEN: - Notify the Market Participant they can proceed with work; IF: - Notification is NOT posted; THEN: - The relay can’t be removed from service unless there are secondary/back up relays that will be functional and no system degradation will occur; - Make log entry of events. |
| Forced Outage | IF: - Notified that a primary relay has been removed from service (forced); THEN: - Ask if the secondary/back up relay is functional; IF: - There is no secondary/back up relay; THEN: - The equipment will need to be removed from service since it is no longer protected. - Make log entry of events. |

## 5.5	Supervise Coordination with SPP, MISO and CFE

Procedure Purpose:  To ensure proper notification and coordination takes place.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R4.2, R4.3 | IRO-005-3.1a R1.9 | IRO-014-1 R1.1 | TOP-002-2.1b R4 |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The ERCOT ISO is only connected to another RC through asynchronous ties. The coordination and communication that must take place with SPP, MISO and CFE is outlined below. It is the responsibility of the Shift Supervisor to ensure this coordination takes place. - DC-Tie Tagging Activities - EEA Levels - Outages on DC-Ties - BLT’s - Arming of the Monticello SPS - ERCOT System Blackout Communications with CFE will be coordinated through AEP Corpus (Turret phone button labeled AEP TO). |
| 1 | Confirm that the DC Tie schedules and E-Tags were properly verified. Ensure that the “after-the-fact checkout” is performed each night and e-mailed to the appropriate entities as outlined in the DC-Tie Procedures. |
| 2 | ERCOT’s EEA status must be communicated to the SPP Reliability Coordinator (Turret phone button labeled SPP RC) as outlined in the DC-Tie procedures. |
| 3 | All planned and forced outages that affect the DC-Ties shall be coordinated with the Tie Operator(s) and SPP (if SPP DC-Ties affected). A message must also be posted on the MIS Public using Notice Builder for planned outages on any commercial DC-Ties. |
| 4 | Notify the SPP or MISO Reliability Coordinator when a BLT is initiated between ERCOT and SPP or MISO, as outlined in the Transmission & Security procedures. |
| 5 | Notify the SPP Reliability Coordinator when the Monticello SPS arms. If the SPS activates, the DC-E will trip. |

## 5.6	Equipment Limitation and Rating Changes

Procedure Purpose:  To ensure line rating changes are documented and correct.

| Protocol Reference | 6.5.3(2) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Line Rating Changes |  |
| NOTE | Normally line rating changes can only be changed when a NOMCR is received. |
| 1 | IF: - Notified by a TO of an incorrect line rating; THEN: - Notify the Operations Support Engineer. |
| 2 | Make log entry. |
| ### TO Temporary Equipment Limitation Notifications |  |
| 1 | IF: - Notified by a TO of any limitations on the Transmission Facilities that may affect Dispatch Instructions; THEN: - Notify the Operations Support Engineer. |
| 2 | IF: - The Operations Support Engineer confirmed the Temporary Equipment Limitation Notifications may affect Dispatch Instructions; THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager to post on the MIS Secure Area the Transmission Facility limitations that may affect Dispatch Instructions. |
| 3 | Make log entry. |

## 5.7	Market Participant Backup Control Center Transfer

Procedure Purpose:  To provide internal notification.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: January 19, 2012 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | If notified by a QSE or TO that they will be transferring to their backup control center, or from their backup to primary, - Identify Market Participant and if they are a [QSE] or [TO] - Send e-mail to 1 ERCOT System Operators - Make log entry. |
| 2 | - If experiencing issues with communications, ICCP, etc. contact the Help Desk. |

## 5.8	Monitor Peaker Net Margin

Procedure Purpose: Monitor Peaker Net Margin (PNM) and re-set System-Wide offer cap (SWCAP), if needed.  The PNM is calculated in dollars per MW on a cumulative basis for all past intervals in the annual resource adequacy cycle.

| Protocol Reference | 4.4.11.1 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | ERCOT-MA>Market Participation>Physical Market>Market Operator Data>System-Wide Offer Cap Before midnight, check the PNM: IF: - PNM has exceeded $175,000; THEN: - Change the date to the next day on the above display and click on the “Approve” button. |
| 2 | Send e-mail to “1 ERCOT Market Operations Support” and “Shift Supervisors” making notification that a Market Notice needs to be prepared due to the SWCAP was re-set to the LCAP. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Regional Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R4.1, R5 | EOP-002-3.1 R3, R6.3, R7.2 | EOP-004-1 R1, R3.1 | IRO-014-1 R1.1.2 |
|  | IRO-015-1 R15 | TOP-002-2.1b R4 | DOE OE-417 |  |

| Version: 1 | Revision: 13 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template between 0300 – 0400 and again between 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - When Off-Line Non-Spin is deployed (provide times) - A special update is not needed; provide information next time report is updated. - Conditions change that required new notices to be issued or cancelled (e.g., OCN , Advisory, Watch, or Emergency Notice ) - Clarify whether Transmission Watch/Emergency is due to a planned or forced outage - Do NOT update report for DAM delays. - A projected reserve capacity shortage develops - Local reliability concerns arise including actual overloads or loss of load - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas restrictions, not expected to cause reliability issues - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Do Not use abbreviations, spell words out. Send updated report when conditions have returned to normal. |  |
| Weather Information | The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Physical Responsive Reserve ≤ 1750 MW and trending downward - Critical - Physical Responsive Reserve ≤ 1375 MW and trending downward Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - High - EEA Level 2 in effect - Physical Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.8 Hz - Critical - EEA Level 3 in effect |  |
| ### Texas RE Event Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations and/or Control Room Operations Manager - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis process, events include the following: Category 1 Events: - An unexpected outage, contrary to design, of three or more elements caused by a common disturbance. For example: - The loss of a combination of NERC-defined elements or facilities - The loss of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); combined cycle units count as one unit - Unplanned evacuation from a control center facility with BPS SCADA functionality for 30 minutes or more - Failure or misoperation of SPS/RAS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BPS emergency - Unintended BPS system separation that results in an island of 100 MW to 999 MW. Excludes BPS radial connection, and non-BPS (distribution) level islanding - The loss of generation of 1,000 MW – 1,399 MW Category 2 Events: - Complete loss of all BPS control center voice communication system for 30 minutes or more - Complete loss of SCADA, control or monitoring functionally for 30 minutes or more - Loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - Voltage excursions equal to or greater than 10% lasting more than 15 continuous minutes due to a BPS emergency Category 3 Events: - Loss of load or generation of 1,400 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Loss of load or generation from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Loss of generation of 10,000 MW or more - Loss of load of 10,000 MW or more |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations and/or Control Room Operations Manager when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". |  |
| OE-417 Reporting Events | DOE OE-417 initial reports are to be completed within 1 hour, forms can be downloaded at: ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc. Electronic forms are preferred. OE-417 reports are required for the following events: - System-wide voltage reduction of 3 % or more - Public appeal to reduce the use of electricity for purposed of maintaining the continuity of the electric power system - Load shedding of 100 MW or more implemented under emergency operational policy - Uncontrolled loss of 300 MW or more of firm system loads form more than 15 minutes from a single incident - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Fuel supply emergencies that could impact system adequacy or reliability - Loss of electric service to more than 50,000 customers for 1 hour or more - Complete operation failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system |  |
| NERC IROL and Preliminary Disturbance Report EOP-004-1 | NERC Preliminary Disturbance reports are to be completed within 24 hours, forms can be downloaded at: http://www.nerc.com/page.php?cid=5¦66 NERC Disturbance reports are required for the following events: - Loss of bulk power transmission component that significantly affects the integrity of system operations, which resulted in actions such as: - Modification of operating procedures - Modification of equipment to prevent reoccurrence of event - Identification of valuable lessons learned - Identification of non-compliance with NERC standards or policies - Identification of a disturbance that is beyond recognized criteria (i.e. three-phase fault with breaker failure, etc) - Frequency or voltage going below the under-frequency or under-voltage load shed points - The occurrence of system separation or system islanding or both - Loss of generation of 1,000 MW or more - IROL violation - Any action taken by a GOP, TOP, BA, or LSE that results in: - Sustained voltage excursions equal to or greater than ±10 percent - Major damage to power system components - Failure, degradation, or misoperation of system protection, SPS, RAPs, or other operating system that do not require operator intervention, which did result in, or could have resulted in, a system disturbance. - Firm load shedding of 100 MW or more to maintain the continuity of the BES - Loss of firm load demands totaling more than 200 MW or 50 percent of the total customers for ≥ 15 minutes |  |
| 1 | When required to file a report (If Manager, System Operations and/or Control Room Operations Manager is unavailable): Forward the TO or QSE report or the Director of Cyber Security’s report to: - NERC (esisac@nerc.com), - NERC 24-hour Emergency Hotline (404) 446-9770), NERC System Awareness (systemawareness@nerc.net), fax (404) 446-9770) - DOE (doehqeoc@oem.doe.gov, fax (202) 586-8485) - “NERC and DOE Disturbance Reporting” e-mail list. |  |
| ### RCIS Reporting |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - Enter temperatures from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations and/or Control Room Operations Manager. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | WHEN: - Alerts for GMDs are issued for K-7 or higher; THEN: - Instruct the Transmission Operator to make Hotline call to TOs, AND - Post message on MIS Public |  |
| 3 | WHEN: - The GMD alert has expired; THEN: - Instruct the Transmission Operator to make Hotline call to TOs, AND - Post message on MIS Public |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |
| ### Special Protection Systems (SPSs) |  |  |
|  | IF: - A Monthly SPSs report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Shift Supervisors |  |

## 6.2	Requests for Public Appeal

Procedure Purpose: Provide instructions to initiate public appeals to conserve electricity when needed.

| Protocol Reference | 6.5.9.4(5) | 6.5.9.4.2(3)(g) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R3.1, R4.2, R5 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, R8 | OE-417 |  |

| Version: 1 | Revision: 2 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| 1 | An appeal through the public news for voluntary load curtailments can be made at any time or in no case later than Level 2 of the EEA. This can be coordinated with the Manager of System Operations and/or Control Room Operations Manager. |  |
| 2 | When notified by the Manager of System Operations and/or Control Room Operations Manager that an appeal through the public news media has been made, ensure the Transmission and Real-Time Operators make a Hotline call to notify TOs and QSEs. |  |
| 3 | The Manager of System Operations and/or Control Room Operations Manager will coordinate the recall of the media appeal with Manager of Communications. |  |
| 4 | This is an event that will trigger an OE-417 Report. Coordinate with Manager of System Operations and/or Control Room Operations Manager to verify the report will be submitted on the event, see section 6.1 “NERC and DOE Reporting”. |  |

## 7.4	Hurricane/Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region (http://www.nhc.noaa.gov) |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure (7.1) and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure (6.1) and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. - Ensure OCN is issued. - Review the expected path of the hurricane/tropical storm and consult with the Operations Support Engineer to determine if multiple contingencies should be studied due to the possibility of transmission outages or loss of load. - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. Outages that could be critical are: - Getaways from power plants, in the affected areas, that need to remain on during the storm for reliability. - 345 KV transmission paths in the affected areas, OR - 345 KV transmission paths that will significantly impact the flow of power to and from the affected area. |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. - Ensure Advisory is issued. - If STP is in the path of the hurricane/tropical storm and the QSE is planning to take the unit offline, - Contact Operations Support to run studies to determine the impact and evaluate system conditions. - If necessary determine the generation needed to replace the loss of capacity from STP. - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored. - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early. - Report any fuel restrictions as per section 6.1 of this procedure. - Review emergency operating procedures. |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. - Ensure Watch is issued - If necessary, instruct the RUC Operator to commit additional Resources as per Operations Support recommendations. - Determine if the need to have a conference call bridge open with the most affected TOs. - Determine if the need for additional support staff from EMMS Production, ANA, Operations Support, and Operators. - Report any fuel restrictions as per section 6.1 of this procedure. |
| Emergency Notice | When Hurricane/Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. - Ensure Emergency Notice is issued |

## 7.5	Extreme Cold Weather

Procedure Purpose: To ensure ERCOT is prepared for Severe Cold Weather Operations

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1, R5 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Extreme cold weather notifications are called when temperatures are forecasted to remain 32°F or below in the following weather zones: - North Central (NORTH_C) - South Central (SOUTH_C) - Coast (COAST) |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure (7.1) and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure (6.1) and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When approaching extreme cold weather is approximately 5 days away: - Ensure OCN is issued - Continue to monitor the expected path of the approaching extreme cold front - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market allows - Review emergency operating procedures |
| Advisory | When approaching extreme cold weather is 3 days away: - Ensure Advisory is issued - Continue to monitor the expected path of extreme cold front - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early - Contact Operations Support to run studies to determine the impact of current and future outages - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market or if additional Ancillary Services will be needed - Review emergency operating procedures |
| Watch | When approaching extreme cold weather is 1 day away: - Ensure Watch is issued - Continue to monitor the expected path of extreme cold front - Review emergency operating procedures - Determine the need for additional support staff - Determine if additional Ancillary Services will be needed - Ensure maximizing generator availability is complete - Determine if Resources need to be committed early before freezing temperatures arrive - Consider if fuel switching is needed. |
| Emergency Notice | When extreme cold weather has arrived and is beginning to have an adverse impact on the ERCOT System: - Ensure Emergency Notice is issued - Implement emergency procedures as needed |

## 7.6	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for Extreme Hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1, R5 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| OCN |  | When extreme hot weather is forecasted approximately 5 days away: - Ensure OCN is issued - Continue to monitor the weather - Coordinate with Outage Coordination for the review of Planned and existing outages for the possibility of withdrawing or restoring equipment |
| Advisory |  | When extreme hot weather is forecasted approximately 3 days away: - Ensure Advisory is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of Planned and existing outages to be withdrawn, rejected, or restored |
| Watch |  | When extreme hot weather is forecasted approximately 1 day away: - Ensure Watch is issued - Continue to monitor the weather - Continue to coordinate with Outage Coordination for the review of Planned and existing outages to be withdrawn, rejected, or restored - Contact Operations Support to run studies to determine the impact of current and future outages - Review emergency operating procedures |
| Emergency Notice |  | When extreme hot weather has arrived and is beginning to have an adverse impact on the ERCOT System: - Ensure Emergency Notice is issued - Implement emergency procedures as needed |
| Log | Log all information in the Operator log and notify the ERCOT Manager, System Operations and/or Control Room Operations Manager of any issues. |  |

## 8.3	Possible Protocol or Operating Guide Violations

Procedure Purpose: Provide instructions for reporting that a QSE or TO may have violated an ERCOT Protocol or Operating Guides requirement.

| Protocol Reference | 6.5.7.9 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.1.2 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - It appears that a QSE or TO is in violation of the ERCOT Protocols or Operating Guides, THEN: - Confirm the ERCOT System Operator’s finding of a possible violation and that an attempt was made to resolve issue with the QSE or TO personnel. - Attempt to resolve the issue. - Obtain information from Market Operations Support and/or Operations Support personnel, as needed. IF resolution is reached, then LOG the event and this procedure is complete. |
| 2 | IF: - No agreement can be reached; THEN: - Review the incident to establish confidence that there has been a possible violation. Submit information to Manager System Operations and/or Control Room Operations Manager |
| 3 | Log the Incident Report in the Shift Supervisors log. |

## 8.6	Root Cause Analysis

Procedure Purpose:  To investigate and recommend corrective action on procedure violations.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The following events will trigger an investigation: - Possible violation of DCS Criteria - Frequency deviation of +/- .05 from scheduled frequency for greater than 30 minutes - High frequency events greater than 60.175 Hz. - Incorrect procurement/deployment of NSRS - Operating actions outside of the ERCOT Protocols, Guides, Operating Procedures or NERC Reliability Standards - Over constraining - A constraint that remains active with no corresponding congestion The Manager, System Operations and/or Control Room Operations Manager may direct the investigation of other events not listed above. |
| NOTE | The “rule of thumb” is to ask why until the most basic cause of the problem is revealed. |
| 1 | When an event occurs, notify the Manager, System Operations and/or Control Room Operations Manager via e-mail that an investigation has been initiated. Include the event, time, duration, and a summary of what occurred. |
| 2 | Preserve all data relevant to the event: - EMMS data - Operational logs - Applicable graphs and charts |
| 3 | Evaluate the following conditions: - Resources - Software performance - Man – Machine interface - Procedures - Management directives - Training - Computer (hardware) performance - External Distracters - Control Room conditions - Market conditions - System conditions - Human Performance - QSE input and communication - TO input and communication - ERCOT internal support and communication - Shift communication and team work |
| 4 | A preliminary report is due within three days. The report should include: - A summary - The chain of events and/or decisions that produced the outcome - The most basic root cause - Recommended steps to prevent future events from occurring. |
| 5 | Forward the report and related information to the Manager, System Operations and/or Control Room Operations Manager; keep one for the later discussion. |
| 6 | The Manager, System Operations and/or Control Room Operations Manager will review the report with the appropriate ERCOT staff and Shift Supervisor to identify the cause and recommend corrective action. |

## 9.2	Monthly Test of Non-Routinely used Telecommunications Facilities

Procedure Purpose: To ensure backup communications are tested monthly.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1.1 R2 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Primary Control Center |  |
| Phone Tests | On the first weekend of each month, between the hours of 0000 Saturday and 0500 Monday: - Test the Control Room Cell Phone by calling the ERCOT Helpdesk Cell Phone. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Standalone Satellite phone. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to Desktop Guide Common to Multiple Desks Section 2.7.4. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| SAT modem testing | Coordinate the following test with the DC Tie Operator at the alternate control center - Using the turret, call each programmed desk SAT Phone at the alternate control center - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| NXT Test | - Test NXT Communicator by activating the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log the results for each of the bulleted items above in the Shift Supervisors Operations Log. |
| Alternate Control Center |  |
| Phone Tests | - When working out of the alternate Control Room during the monthly scheduled dates: - Test Control Room Cell Phone with the ERCOT Helpdesk Cell Phone. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Satellite phone associated to the Operations Desk on each turret. It isn’t necessary to call a satellite number, just verify the phones are operational. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. - Test the Standalone Satellite phone operation located in the Control Room. It isn’t necessary to call a satellite number, just verify the phone is operational. Refer to Desktop Guide Common to Multiple Desks Section 2.7.5. - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| SAT modem testing | Coordinate the following test with the DC Tie Operator at the other control center - Using the turret, test call each programmed SAT Desk Phone at the other control center - If any issues are found, send e-mail to “shiftsupv” and back office will follow up. |
| NXT Test | - Log into the Bastrop ENS link when working out of the alternate Control Room in Bastrop, - Test NXT Communicator by activating the “SO ENS Test” scenario between the hours of 0800-2200. - If any issues are found, open help ticket and cc: “shiftsupv”. |
| Log | Log the results for each of the bulleted items above in the Shift Supervisors Operations Log. |

## 10.1		Loss of Primary Control Center Functionality

Procedure Purpose: Provide instructions for responding to conditions that cause the primary control center to become inoperable or uninhabitable and ensuring the safety of control room personnel.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Stanard | COM-001-1.1 R5 | EOP-008-0 R1.4 |  |  |

| Version: 1 | Revision: 2 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | It will be the responsibility of the Shift Supervisor to determine the risk and ensure the safety of Control Center personnel. |
| 2 | Upon confirmation of imminent danger to Control Center personnel immediately evacuate the Control Center to a secure area, taking the Control Center cell phone and a copy of this procedure with you. |
| NOTE | - After the Control Center has been evacuated the Shift Supervisor may: - Re-locate the entire shift to the Alternate Control Center (ACC). - Send a partial shift or contact extra personnel to report to the ACC. - Remain in the secure area in anticipation of a quick return to the Primary Control Center (PCC). - The Shift Supervisor may choose another course of action that will best maintain grid security depending on the circumstances causing the evacuation. |
| 3 | - The Shift Supervisor is responsible for the following notifications in the event of a Control Center evacuation. Information and instructions conveyed will be based on the Shift Supervisor’s decision regarding relocation to the ACC. - DC Tie Desk Operator at the ACC - ERCOT Security TCC1 – Ext. 3000 - ERCOT Security TCC2 – Ext. 6400 - ERCOT Security ACC (Bastrop) – Ext. 5000 - ERCOT Security MET – Ext. 7000 - Help Desk (to notify EMMS Support, Telecommunications) - Manager of System Operations and/or Control Room Operations Manager - Engineering Support These phone numbers have been programmed into the control room cell phone |
| NOTE | - The DC Tie Desk Operator at the ACC will be responsible for all notifications if there is a loss of the PCC and he/she has not been contacted by the Shift Supervisor. |

## 10.2		EMMS and Interface System Failures

Procedure Purpose: Provide guidance to the Shift Supervisor for coordinating with the ERCOT IT Help Desk if critical functions or systems fail such that system operators and/or participants are precluded for performing and complying with their obligations and therefore jeopardizing the security of the system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1.1 R5 | EOP-008-0 R1.4 |  |  |

| Version: 1 | Revision: 5 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step |  | Action |  |
| --- | --- | --- | --- |
| 1 |  | If any Control Room computer systems (ICCP, Web Portal, MIS, or API) events, failures, or incidents that affect normal operations occur, - DETERMINE criticality and impact to the reliability to the grid, - CONTACT the ERCOT Help Desk immediately from the Supervisor Help Desk button on the Turret Phone or extension 6804. If necessary, contact the on-call IT person first then contact the Help Desk. |  |
| NOTE |  | For a complete EMMS failure, see Real-Time Procedure Section 3.2, EMS Failure. |  |
| 2 |  | IF: - Any of the aforementioned systems fail and are effecting ERCOT systems or multiple Market Participants and will be unavailable for longer than 15 minutes; THEN: - Notify market participants of the problem and expected duration via Hotline, - Request additional assistance from other support staff. |  |
| 3 |  | When the problem is resolved, Notify all participants via Hotline of the problem resolution. |  |
| Log |  | Log the following: - Date - Time of event - Description of system alarms, events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| ## Data and/or Voice Communication Failures |  |  |  |
| 1 |  | Notify the Help Desk of the loss and REQUEST assistance to re-establish voice and/or data communications. - Telecommunications group will be responsible for voice communications. - EMMS Production group will be responsible for data communications |  |
| 2 |  | Use back-up communications if needed such as the Control Room cell phone, Standalone Satellite phone or the PBX Bypass phones to maintain communications with the other control room, TOs, QSEs, SPP and any other entities as needed. The list of phone numbers is located in the Phone Book at Shift Supervisor’s Desk and also programmed into the cell phone. |  |
| 3 |  | IF the criticality and impact of events or failures is such that Market Participants are, or will be affected before the problem can be resolved, THEN: - Instruct ERCOT System Operator to NOTIFY the other ERCOT Control Room and all market participants via Hotline of the problem and expected duration. If Hotline is unavailable utilize any of the following methods: - Control Room cell phone, PBX Bypass phones, or Standalone Satellite phone. - REQUEST additional assistance from other support staff, as needed. |  |
| NOTE |  | Steps 4 & 5 may be performed in any order. |  |
| 4 |  | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| 5 |  | When the problem is resolved, NOTIFY all participants via Hotline of the problem resolution. |  |
| ## Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms |  |  |  |
| NOTE |  | - Normal status for the Dynamic Rating, SCED Status, EMBP, SE, RTCA and RLC Status is indicated by each status box constant green on the “ERCOT & QSE Summary Page” in the PI system. - Failure of the PI server is indicated by abnormal status of Dynamic Rating, SE and RLC, accompanied by the PI system “flat-lining” - Dynamic Rating, SE and RLC status boxes flashing red AND PI flat-lining may indicate failure of the EMS. |  |
| Monitor |  | PERFORM the following as applicable to the indicated conditions: - IF only the Dynamic Ratings status box is flashing red, CONTACT the ERCOT Help Desk - TELL them the Dynamic Rating Alarm status in Processbook is flashing red and the dynamic ratings are not being sent to the SCADA in the EMS. - REQUEST they notify the on-call EMMS Production person of the situation. - IF only the RLC status box is flashing yellow/red, CONTACT the ERCOT Help Desk - TELL them the RLC Alarm status in Processbook is not green - Greater than 5 minutes but less than 10 minutes turns - Yellow - Greater than 10 minutes turns - Red - DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the SCED Status box is flashing red, - Follow the Managing SCED Failures in the Real Time Desk Procedure. - If SCED failure can’t be resolved CONTACT the ERCOT Help Desk and DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the EMBP box is flashing red, - Determine the reason Emergency Base Point are being issued, - Remove the Emergency Base Point flag when condition allow, - If EMBP can’t be resolved CONTACT the ERCOT Help Desk and DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the SE status box is flashing red, CONTACT the Operations Support Engineer - TELL them the SE Alarm status in Processbook is flashing red - IF only the RTCA status box is flashing yellow or red, CONTACT the Operations Support Engineer - RTCA executes every 5 minutes, if RTCA doesn’t complete within the desired threshold the display changes colors - Greater than 7 minutes but less than 10 minutes turns - Yellow - Greater than 10 minutes turns - Red - TELL them the RTCA Alarm status in Processbook is flashing yellow/red - Greater than 15 minutes, inform QSEs for STP and CPSES. |  |
| ## Building Security and Fire Alarms |  |  |  |
| NOTE | The Shift Supervisor or designee will ensure staff members adhere to emergency evacuation procedures and evacuate all team members from the Control Room if an emergency evacuation is required. |  |  |
| 1 | IF: - Building security or fire alarm sounds, THEN: - Contact Security’s Emergency Number if Security has not already made communications with the Control Room. |  |  |
| 2 | IF: - It is determined it is a drill, THEN: - Retrieve the ‘orange’ bag for the employee roster, - Account for each operator by marking them present and return form to Security staff at front desk (if able). IF: - If unable to return roster in a reasonable timeframe, CONTACT: - Security and request them to retrieve roster during the next patrol. |  |  |
| 3 | IF: - Control Room personnel are in danger or ordered to be evacuated, THEN: - Transfer control of the Grid to the Alternate Control Center (see “Loss of Primary Control Center Functionality” procedure Section 4.1 in the DC Tie Desk Procedure), - Request additional assistance from other support staff, - Evacuate the Control Room to a safe area for Zone #1, - Retrieve the ‘orange’ bag for the employee roster, - Account for each employee by marking them present at the rally point. |  |  |
| 4 | Notify the Manager, System Operations and/or Control Room Operations Manager as soon as practical. |  |  |
| ## Failure of the Emergency Generator |  |  |  |
| 1 | If the Facilities emergency generator fails to start, you will be notified by the Facilities Staff. |  |  |
| 2 | If the Facilities Staff or the Shift Supervisor determines that it will be more than 20 minutes before the emergency generator can be started, the Shift Supervisor may consider initiating the “Loss of Primary Control Center Functionality” procedure. |  |  |
| 3 | The Shift Supervisor or his/her delegated representative should notify the Manager, System Operations and/or Control Room Operations Manager that the controls have been transferred to the other control center. |  |  |
| 4 | REQUEST additional assistance from other support staff as needed. |  |  |
| NOTE | See Desktop Guide Shift Supervisor Section 2.1. |  |  |

# 11.	Supervisory Responsibilities

Procedure Purpose:  To keep current on all activities.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ## Review Shift Logs |  |  |
| 1 | REVIEW shift logs entries using the following guidelines: - Review multiple days’ worth of shift logs when returning from multiple rest days or vacation periods. - Review previous two shifts logs when accepting a shift in mid-rotation. |  |
| ## Review New Communications from Manager and/or Control Room Operations Manager |  |  |
| NOTE |  | Periodically, the ERCOT Manager, System Operations and/or Control Room Operations Manager will issue new operating instructions, operating memos, and other relevant communications to all System Operators. These types of communications are used to clarify or temporarily modify existing procedures. The Shift Supervisor is required to review these communications to ensure that the new instructions are known and understood by all desks in the shift. This task is especially crucial when returning from vacation periods, or several rest days. This review of Manager, System Operations and/or Control Room Operations Manager issued communications includes verification of e-mail and hardcopy communications or instructions. Clarification of new instructions, if needed, must be addressed directly to the Manager, System Operations and/or Control Room Operations Manager. |
| 1 |  | REVIEW all communications received from the Manager, System Operations and/or Control Room Operations Manager including e-mails, letters, and memorandums. |
| 2 |  | DETERMINE if new or revised operating instructions and operating memos were issued since the last verification of communications was made. |
| 3 |  | IF new or revised operating instructions and operating memos were issued, VERIFY which system operator positions and operating procedures may be affected. |
| ## Deliver Oral Shift Report to Entering Shift Supervisor |  |  |
| 1 | OUTLINE comments on the following areas: - Forced Outages - System Reserves - System Conditions - Market Conditions - Forecasted Congestion - System Disturbances, if any occurred - New or modified operating procedures - Shift Staffing information including staff assigned to alternate control center |  |
| 2 | REQUEST understanding and acknowledgement from entering Shift Supervisor. |  |
| ## Coordinate Adjustments to Shift Personnel Schedules |  |  |
| 1 | ADJUST system operator’s shift schedules for: - Scheduled vacation leave periods - Schedule or unscheduled sick periods - Training needs - Special assignments - Other unscheduled leaves of absence |  |
| 2 | COORDINATE system operator replacements for any coordinated leave. |  |
| ## Implement ERCOT Personnel and Company Standards |  |  |
| 1 | IMPLEMENT the policies described in the ERCOT Employee Corporate Standard Manual as needed. |  |
| 2 | ASSIST system operators in observing the standards described in the ERCOT Employee Corporate Standard Manual as needed. |  |
| 3 | DISCUSS any violations of the standards described in the ERCOT Employee Corporate Standard Manual with the system operators as needed. |  |
| 4 | DISCUSS any continuous and persistent non-compliance of a system operator with the standards described in the ERCOT Employee Corporate Standard Manual with the Manager, System Operations and/or Control Room Operations Manager as needed. |  |
| 5 | EXECUTE any remedial actions recommended or instructed by the Manager, System Operations and/or Control Room Operations Manager. |  |

| ## Communicate Procedure Changes |  |
| --- | --- |
| 1 | When changes to operating procedures are approved, INFORM the System Operators and have them review the change(s). |
| 2 | VERIFY that each affected System Operator understands the new or revised procedures. |
| 3 | VERIFY that each affected System Operator has signed the log sheet (located on the Shift Supervisor desk) that states that each Operator is aware and understands the new or revised operating instructions. |
| ## Identify Training Needs of System Operators |  |
| NOTE | - Under performance by a system operator is generally remedied by additional training. Clear indications of underperformance obtained from periodic performance reviews, and on the job-performance observations should indicate to the Shift Supervisor the need to consider training options. |
| 1 | - REVIEW performance review results and periodic job performance observation notes at least once every three months. |
| 2 | IDENTIFY training needs of a system operator or group of system operators in any of the following areas: - System Operations - Employee standards - General skills required in performing assigned system operator duties - New or modified operating procedures or instructions - Other areas not covered by Operating Procedures, Operating Guidelines, or established system operator training |
| 3 | - REVIEW record of training needs of each system operator in the crew. |
| 4 | - SCHEDULE required training for each system operator with ERCOT Training Department. |
| 5 | - FOLLOW progress of system operators training. |
| 6 | - DISCUSS effectiveness of training program related to system operator job performance with Manager, System Operations and/or Control Room Operations Manager and ERCOT Training Department at least once every six months. |
| 7 | - MAKE recommendations on system operator training program as needed. |
| ## Official Copies of Manuals and Guides |  |
| NOTE | Employees who want their own personal copies are responsible for making them themselves. |
| 1 | Ensure that only the official updated copy of the Protocols Manual, Operating Guide, and Operating Procedures Manual is kept at each Operating Desk. |
| 2 | Personal copies of Protocols Manual, Operating Guide, and Operating Procedures Manual ARE NOT allowed at the duty desk. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |