## Power Operations Bulletin # 623

ERCOT has posted/revised the Transmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.2	Alarm Processing and Acknowledgment

Procedure Purpose: To monitor and acknowledge system alarms.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-002-2 R6, R8 | IRO-003-2 R2 | IRO-005-3a R1.1, R1.2 | TOP-002-2.1b R8 |
|  | TOP-006-2 R2, R5 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Alarm Displays for ERCOT are primarily used to show changes in equipment status. The alarms are categorized based on alarm criticality and prioritization on the Alarm Summary Display: |
| Categories | Tab 1: 345 KV Transmission Equipment Status Tab 2: 138 KV Transmission Equipment Status Tab 3: Generator Breaker, AVR, CAPS, REACTOR and SPS Status Tab 4: RLC alerts Tab 5: Transmission Line Overloads - Voltage Violations - Critical Alarms Tab 6: QKNET alarms Tab 7: ICCP status Tab 8: All other alarms |
| 1 | Monitor the Alarm Summary Display pages 3, 6 and 7 as necessary to confirm system reliability status. |
| 2 | Take appropriate action as system conditions warrant. |
| 3 | Coordinate with the Real-Time Operator to clear the alarms approximately every 24 hours or as needed. |

## 3.5	Geo-Magnetic Disturbance Notification

Procedure Purpose:  To provide notification and increase situational awareness when a GMD storm is advancing.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-005-3.1a R3 |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Geomagnetic Disturbance Reference Document can be found in Section 2.13 of the Common to Multiple Desks Desktop Reference Guide. |
| 1 | WHEN: - Notified by the Shift Supervisor that a K-7 or higher GMD storm is expected; THEN: - Using the Hotline, issue an Advisory to all TOs, - Post message on MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory due to a [state K-Index Alert] geomagnetic disturbance storm alert that has been issued for [date and hours]. ERCOT is instructing you to increase your situational awareness in the following areas: - Monitor reactive reserves - Monitor for unusual voltage and /or MVAR swings - Prepare for possible false SCADA/EMS indications if telecommunications systems are disrupted Report to ERCOT if you suspect any issues due to a GMD. [TO] please repeat this back to me. That is correct, thank you.” Typical MIS Posting Script: Advisory issued for a geomagnetic disturbance storm of K-7 or higher. |
| 2 | Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Cancel | WHEN: - Notified by the Shift Supervisor that a K-7 or higher GMD storm has expired; THEN: - Using the Hotline, cancel the Advisory for all TOs, - Cancel message on MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the [state K-Index Alert]. [TO] please repeat this back to me. That is correct, thank you.” |
| 2 | Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Log | Log actions taken |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11 | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.2.2 |  |  |  |
| NERC Standard | IRO-003-2 R1 | IRO-005-3a R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-002-2 R6, R8 |
|  | IRO-004-2 R3 | TOP-001-1a R1, R2, R5 | TOP-002-2.1b R6, R8, R10 | TOP-004-2 R1, R6, R6.6 |
|  | TOP-006-2 R5 | TOP-008-1 R1, R2, R4 | EOP-003-1 R6 |  |

| Version: 1 | Revision: 20 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |  |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |  |
| Unknown State | When in an unknown operating state (any state for which valid operating limits have not been determined), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |  |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is beyond “First Contingency Criteria”; THEN: - Issue a Watch, - Make a Hotline call and post Watch message on MIS Public using Notice Builder. |  |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. Error! Hyperlink reference not valid.A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |  |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) - Unit specific dispatch instructions (Override HDL/LDL or VDI) - Non-Spin may be used as necessary. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP , - A hardcopy of the SPSs are maintained in the control room by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |  |
| Phase Shifters | Phase shifters can be used to help with congestion management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – Mitigate local congestion and increase W/N transfers - Big Lake – Mitigate local congestion and increase W/N transfers - Firerock ETT – Mitigate local congestion and increase W/N transfers - Nelson Sharp – Valley import during outages and flow in/out of Corpus Christi - Hamilton Road – Control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – Control Laredo import issues during outages - Thomaston – Control flow into Cuero, Yoakum and Victoria Areas Refer to OpsMon Display 08 HRUC Phase Shifter Position |  |
| Constraint Shift Factor Cut Off | Basecase and post-contingency constraints which do not have absolute generator shift factors for units greater than or equal to 2% are not activated in SCED. See Section 4.5 Mitigation Plan for additional details. |  |
| ### Review Planned Outage Notes |  |  |
| 1 | Review daily outage notes: IF: - Outage notes recommend slower moving Resources to be lowered to maintain system security; THEN: - Take a real-time snap shot to determine where Resource(s) are needed before outage is taken - Use the manual override to step down Resource(s) - Once Resource(s) are down to where snap shot showed, - Give approval for switching, - Release manual overrides, and - Activate SCED constraint (when necessary). - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions due to XXXX outage. |  |
| 2 | IF: - An outage requires a Resource to be On-line to solve a voltage issue and having the Resource On-line causes a post-contingency overload; THEN: - Manually override the Resources to its LSL - Notify QSE of action - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions due to XXXX outage. |  |
| Log | Log actions taken. |  |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |  |
| 1 | IF: - A major topology change has occurred; THEN: - Re-run RTCA and VSAT/TSAT. |  |
| Log | Log actions taken. |  |
| ### Post-Contingency Overloads |  |  |
| 1 | WHEN: - Post-contingency overloads are approaching 98% of the Emergency Rating; THEN: - Determine if the SCADA is of similar magnitude to the pre-contingency value. - Example: Review the MW and MVAR flows |  |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate. - Make log entry. |  |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP exist - Verify that a PST cannot be used to resolve congestion |  |
| 4 | IF: - Post-contingency overloads of 98% or greater with at least a 2% shift factor exist ; THEN: - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint if needed (minimum of 95%, excluding W-N), - If experiencing oscillation issues, notify the Operations Support Engineer to investigate - If constraint needs to be controlled before the next SCED run: - Manually run RTCA after activating the constraint, - Manually execute the SCED process - Refer to “Managing Binding and Exceeded Constraints”. |  |
| 5 | IF: - Constraints with pre-contingency or post-contingency flows which exceed the rating of the overloaded Transmission Element are not activated in SCED; THEN: - Acknowledge the constraint and list a reason using the drop down box - The comment field can be used for additional information |  |
| 6 | IF: - A Qualifying Facility (QF) needs to operate below its LSL, or be ordered off-line to solve congestion; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public using Notice Builder. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |  |
| 7 | IF: - Post-contingency overloads of 98% or greater of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 98% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”. |  |
| 8 | IF: - Congestion can not be fully resolved and does not have a MP or TOAP; THEN: - REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.5 Mitigation Plan). |  |
| 9 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. IF: - A transmission condition has been identified causing unreliable operation or overloaded elements, AND firm load is shed, THEN: - Issue an Emergency Notice, - Make a Hotline call and post Emergency Notice message on MIS Public using Notice Builder. |  |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |  |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A QSGR is needed for voltage support or an unsolved contingency; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running, - Notify QSE as time permits - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |  |
| Log | Log actions taken. |  |
| ### Post-Contingency Overloads on Private Use Networks (PUNs) |  |  |
| 1 | IF: - Post-contingency overloads greater than 98% of the Emergency Rating exist; THEN: - Contact the PUNs QSE to determine if the post-contingency is real (review MW, MVAR flows and facility ratings), - If real, give the QSE the opportunity to correct or have a plan to mitigate if the contingency were to occur.. |  |
| 2 | IF: - It is determined that the PUN has no way to mitigate or correct THEN: - Direct the QSE to take action such as lower/raise generation or load (directs only, do not override HDL/LDL or activate constraint in SCED). |  |
| 3 | - Acknowledge the post-contingency overload in TCM - Make log entry of actions taken |  |
| ### Managing Constraints in SCED |  |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |  |
| Input Displays | Each constraint activated in TCM is automatically passed to SCED DSI and can be verified on the following MMS displays: - EMS/TCM Constraint List, - EMS/TCM Constraint: Generator Shift Factors |  |
| Output Displays | Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows on the following displays: - DSP Constraint Summary, - DSP Suggestion Plan (if need for exceeded constraints). |  |
| 1 | Verify that the SCED executions are reducing the flows on each constraint that is binding. |  |
| 2 | If a constraint is violated in SCED, which is when it has reached its max shadow price, review the following bullets to determine the next action: - Confirm that pre-determined relevant RAPs are properly modeled in the EMS, - Ensure curtailed units are following base points (RLC Output Data display), - Verify that units with large shift factors (SF button on TCM display) do not have a status of ONTEST (RLC Output Data display), - Redistribute A/S to increase capacity available to SCED (see separate procedure below), - Determine if a unit carrying Off-line Non-Spin is needed to solve congestion, - Ask Resource Operator to deploy Non-Spin for the specific unit - The telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Determine if additional units need to be committed/decommitted, - Determine if there is a non-cascading conflicting constraint that is preventing the constraint to solve, - Override Resource that is in conflict to optimal output for both constraints - Release the constraint that prevents resolving the more severe post-contingency overload, - Create a “suggestion plan” for the constraint if can’t determine course of action from shift factors |  |
| 3 | At times, it may be necessary to manually override HDL/LDL, these reasons could include the following: - Manually dispatching slower moving Resources before an outage to better manage congestion caused by the outage - Conflicting constraints - Unsolved contingencies IF: - An override is necessary; THEN: - Notify QSE of override - Consider doing the override in steps as to not exceed ramp rate - Post message on MIS under Operational Information Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. NOTE: - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - DO NOT override a Resource ONRR |  |
| 4 | IF: - All applicable steps above have been completed, AND constraint is still exceeded in SCED (max shadow price); THEN: - Instruct Operations Support Engineer to develop a mitigation plan, AND - Contact Manager, System Operations and/or Control Room Operations Manager to investigate further |  |
| NOTE | ERCOT-MA>Market Operation>Real-Time Market>SCED Displays>External Input Data>EMS/TCM Constraint: Generator Shift Factors OR EMP Applications>TCM-Transmission Constraint Manager>Related Displays>Message Log for CAM IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk to issue a ticket to EMMS Production to fix immediately. |  |
| Log | Log all action taken including the following: - Reason for doing a manual override - Any security violations that were ≥ 125% of the Emergency Rating |  |
| ### Redistribute A/S to Increase Capacity available to SCED |  |  |
| 1 | RLC Unit Input Data display IF: - A/S needs to be removed from a specific unit in order to increase capacity to SCED; THEN: - Determine which A/S to remove - Instruct the QSE to remove the A/S by updating their telemetry to free that capacity to SCED - Notify Resource Operator with undeliverable A/S type, amount and approximate hours. |  |
| LOG | Log all actions taken |  |
| ### Unsolved Contingencies |  |  |
| 1 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Operations Support Engineer to investigate |  |
| LOG | Log all action taken including the following: - Reason for unsolved contingency - Actions taken to resolve |  |
| ### Model Inconsistencies/Updates |  |  |
| 1 | IF: - Any inconsistencies in ratings, impedance changes, etc. are found; THEN: - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required, correct it through the NOMCR process. |  |
| 2 | IF: - There is a difference in line ratings between ERCOT and a TO; THEN: - The most limiting rating will be used until the correct rating can be determined - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required correct it through the NOMCR process. |  |
| LOG | Log all actions taken |  |
| ### QSE Requests to Decommit a Resource |  |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |  |
| ### Managing Congestion during SCED Failure |  |  |
| 1 | IF: - SCED fails; THEN: - Coordinate with Real-Time Operator and initiate the Emergency Notice Hotline call. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |  |

## 4.4	North-Houston Voltage Stability Limit

Procedure Purpose:  Maintain Transmission Stability between the North and Houston.

| Protocol Reference | 3.10.7.6 (3) | 6.5.9.1(1)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-003-1 R1 | IRO-002-2 R6, R8 | IRO-003-2 R1 | IRO-004-2 R3 |
|  | IRO-005-3a R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-008-1 R1 | TOP-002-2.1b R10 |
|  | TOP-004-2 R1, R2, R6, R6.6 | TOP-006-2 R5 | TOP-007-0 R3, R4 | TOP-008-1 R1 |

| Version: 1 | Revision: 13 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. If necessary, the System Operator has the authority to direct load shedding before this IROL has been exceeded. |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| VSAT | - Ensure VSAT has solved in the last 30 minutes, - Update RTMONI with new limit each time it changes to give transparency to Market Participants. |
| NOTE | When an unexpected change to system conditions occur between 1700 – 0900 that result in a large limit change from the day-ahead GTL posting: - Declare a Watch by posting on MIS - Make Hotline call to TOs - Notify Real-Time operator to make hotline call - Notify Operations Support Engineer to post the new GTL Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch because the posted North - Houston GTL limit has been updated on the MIS due to an unexpected change on the system. [TO] please repeat this back to me. That is correct, thank you.” Typical MIS Posting Script: “A Watch has been issued due to ERCOT updating the posted North - Houston GTL limit on the MIS due to an unexpected change on the system.” |
| North-Houston 345kV Circuit Outage | IF: - Any of the 345kV lines going into the Houston area has a forced outage; THEN: - Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor Step in this procedure. |
| Monitor | Monitor each of the following Reliability Margins: - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TOs in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| ≤400MW | - Activate the appropriate constraint, - Post message on MIS Public using Notice Builder. Typical MIS Posting Script: “ERCOT is constraining for the North-Houston voltage stability limit.” |
| ≤300MW | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL - Instruct Resource Operator to deploy Non-Spin in the Coast Weather Zone (WZ_COAST) - Issue a Transmission Watch by making a Hotline call and posting on MIS Public using Notice Builder - Notify Real-Time Operator to make Hotline notification to QSEs Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North-Houston interface. Non-Spin is being deployed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| NOTE | When the Non-Spin Resource is on-line, they must change their Non-Spin schedule to 0 in order for SCED to dispatch them. |
| ≤200MW | VDI QSGR in the Houston area that were not bid in as Non-Spin. Override LDLs as needed. - Determine QSGR in the Coast Weather Zone (WZ_COAST) - Choose “COMMIT” as the Instruction Type from Resource level |
| ≤100MW | - Instruct the Resource Desk Operator to deploy Load Resources providing RRS in Houston - Issue a Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder - Notify Real-Time Operator to make Hotline notification to QSEs Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice for the North-Houston interface. Load Resources in the Houston area are being deployed to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| 0MW | - Instruct Centerpoint to drop firm load in 100 MW blocks. - Continue Transmission Emergency Notice by making a Hotline call and posting on MIS Public using Notice Builder, - Notify Shift Supervisor to make NXT notification and RCIS posting. Typical Script for Centerpoint: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is directing Centerpoint to drop [*** MW] of firm load for the North – Houston interface. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” Typical Hotline Script: “At [xx:xx], ERCOT is continuing the Transmission Emergency Notice for the North-Houston interface. Firm Load is being shed in the Houston area to help mitigate the issue. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Cancel | Make appropriate cancellations when back to normal operations. |
| Log | Log all actions taken. |

## 4.5	SPS, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 5.5.2 | 6.5.1.1(a),(c),(e) |  | 6.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.5.2(1) | 6.5.7.1.10 | 6.5.7.1.11(1),(4) | 6.5.7.8 |
|  | 6.5.9 | 6.5.9.1(1)(d) |  | 7.1 |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-003-1 R6, R8 | IRO-003-2 R1 | IRO-005-3a R1.1,R1.2, R1.3, R1.7, R1.10, R3, R5, R9, R12, R13, R16, R17 | IRO-006-5 R1, R3, R4, R5, R6 IRO-006-TRE-1 |
|  | IRO-002-2 R6, R8 | IRO-004-2 R3 | PRC-001-1 R6 | TOP-001-1a R1, R2, R5 |
|  | TOP-002-2.1b R6, R8, R10 | TOP-004-2 R1, R6, R6.6 | TOP-006-2 R3, R5 | TOP-008-1 R1, R2, R4 |

| Version: 1 | Revision: 11 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP |
| NOTE | Special Protection Schemes (SPS) (identified as RAS in EMS) OR Remedial Action Plans (RAP) - EXAMINE the results of RTCA, - If the background has a color indicating a SPS or RAP, - Refer to Desktop Guide Transmission Desk Section 2.7 for explanation of colors and for actions to be taken based on the color of the background. |
| Directives | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log all actions taken. |
| ### Special Protection Systems (SPS) (Identified as RAS in EMS) |  |
| NOTE | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE | Use caution when the tolerance setting is <100% in RTCA. If the post-contingency loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the contingency associated with the SPS will show in the Transmission Constraint Manager (TCM) display. When this occurs, the result will be a light blue highlighted background identifying the device ID on the TCM display. In this scenario, congestion management is not needed until the criteria in Desktop Guide Transmission Desk Section 2.7, is met. |
| Monitor | Each SPS will be displayed on the “Real Time Values” spreadsheet, as the SPS activation threshold increases the display changes color as follows: - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 1 | Typically SPSs are to solve post-contingency overloads on the Transmission System. IF: - The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an SPS; THEN: - Utilize congestion management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the SPS will not mitigate all the overloaded elements automatically; Example: (Light blue or Salmon highlighted background and above 100% loading) THEN: - As system conditions warrant, activate congestion management techniques to relieve the overload. |
| 3 | IF: - No reliability issues will arise as a result of a SPS’s operation; THEN: - At the Operator’s discretion, allow the SPS to perform its function. |
| 4 | IF: - An SPS operates; THEN: - Notify affected TO to reset SPS as system conditions warrant |
| SPS Posting | All SPSs are considered in-service unless otherwise notified by the TO. IF: - An SPS is taken out of service; THEN: - Post the information on MIS Public using Notice Builder. WHEN: - The SPS is placed back in service, THEN: - Cancel the message. Typical MIS Posting Script: The [name] SPS has been taken out of service. |
| Status Change | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated, - “OPS Support Engineering” - “1 ERCOT System Operators” - “DAMTeam” |
| Basecase continuous SPS Triggering | Continual triggering of a SPS during basecase operations should be managed utilizing manual constraints created in TCM (only applies to manual reset of SPS controls causing a reliability issue). IF: - An SPS is continually triggered during Basecase operations; THEN: - Verify that an associated manual constraint exists for this SPS in TCM, and activate the manual constraint in SCED. IF: - A manual constraint does not exist for this SPS in TCM; THEN: - Coordinate with the Operations Support Engineer to build a manual constraint for the SPS action in TCM. |
| LOG | Log all actions taken. |
| ### Remedial Action Plan (RAP) |  |
| 1 | IF: - A RAP exists for the contingency; THEN: - Review the RAP with the associated TO, - Notify the Shift Supervisor of the anticipated actions. |
| 2 | IF: - A RAP is used to alleviate the identified problem regardless of the contingency listed on the RAP; THEN: - Make log entry. |
| 3 | IF: - A RAP exists for the contingency AND does not solve the contingency OR the pre-RAP overload exceeds the 15 MN rating; THEN: - RTCA does not pass the 15MN (15 minute) rating to TCM, only the EMGY (2-hour emergency) rating. To properly constrain for RAP-associated elements, the % Rating column in TCM may need to be increased so that the constraint limit matches the 15MN value. - Increase the value in the % Rating column in TCM to loosen the constraint (maximum 100% of 15MN value). |
| 4 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the RAP will not mitigate all the overloaded elements automatically; Example: (Light blue or Yellow highlighted background and above 100% loading) THEN: - As system conditions warrant, activate congestion management techniques to relieve the overload. |
| 5 | IF: - The contingency anticipated by the RAP takes place; THEN: - Direct the implementation of the RAP, - Respond to requests made by the TO in accordance with the RAP, - If necessary, continue to use additional congestion management methods, - When the contingency clears, notify the TO as soon as possible. |
| LOG | Log all actions taken. |
| ### Pre-Contingency Action Plan (PCAP) |  |
| CAUTION | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. |
| 1 | WHEN: - RTCA shows a post-contingency overload and a PCAP exists to resolve it; THEN: - Review the PCAP with the associated Transmission Operator, - Notify the Shift Supervisor of the anticipated actions, - Direct the execution of the PCAP with the associated Transmission Operator. Typical Script to appropriate TO: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing [TO] to implement the ****PCAP and [open/close] [breaker(s)]. [TO] please repeat this back to me. That is correct, thank you.” |
| NOTE | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 2 | IF: - Any PCAPs are still in use (reviewed each day between 0000 and 0500), AND - It is determined, in concurrence with the Shift Supervisor that it is no longer needed; THEN: - Direct the associated Transmission Operator to return the system to: - Its normal status, OR - Its status prior to implementation of the PCAP. |
| 3 | IF: - A PCAP is used to alleviate the identified problem regardless of the contingency listed on the PCAP; THEN: - Make log entry. |
| LOG | Log all actions taken. |
| ### Mitigation Plan (MP) |  |
| NOTE | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. - A MP is developed when SCED cannot fully resolve the constraint, OR - A MP is developed when there are not absolute shift factors greater than or equal to 2% - If a MP is used to alleviate the identified problem regardless of the contingency listed on the MP, make a log entry. |
| SCED unable to fully resolve constraint | IF: - SCED is unable to resolve a constraint; THEN: - Keep constraint active in SCED, - Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the constraint; THEN: - Keep constraint active in SCED, - Coordinate with Operations Support Engineer to develop a MP - If constraint exists due to an outage, a TOAP should be developed (see TOAP procedure), - Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes and the constraint remains violated in SCED. |
| < 2% Absolute Shift Factors | IF: - A constraint exists for which there are no generator shift factors greater than or equal to 2%; THEN: - DO NOT activate the constraint in SCED - Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the constraint; THEN: - Coordinate with the Operations Support Engineer to develop MP - If contingency exists due to an outage, a TOAP should be developed (see TOAP procedure) - Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes. |
| TO Issue | IF: - Notified by a TO that it will take more time to implement the MP than is identified on the MP; THEN: - Notify the Operations Support Engineer to restudy and modify MP, - Log actions taken |
| Issue Watch | When issuing a Transmission Watch for an unsolved post-contingency overload (and waiting on MP or TOAP to be developed: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Post message on MIS Public using Notice Builder Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission Watch due to the post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] is being developed. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. Typical MIS Posting Script: At [xx:xx] a Transmission Watch was issued due to the post-contingency overload of [constraint name], a [mitigation plan/temporary outage action plan] is being developed. |
| Cancel Watch | When the MP or TOAP has been developed, cancel the Watch: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Cancel message on MIS Public using Notice Builder Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Transmission Watch for post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] has been developed. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Contingency Occurs | IF: - The anticipated contingency takes place; THEN: - Direct (if necessary) the implementation of the MP or TOAP to the associated TO, - Respond as quickly as possible to requests made by the TO in accordance with the MP, - If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP. |
| LOG | Log all actions taken. |
| ### Temporary Outage Action Plan (TOAP) |  |
| NOTE | TOAPs are temporary since they are outage related - A TOAP is developed when there is not absolute shift factors greater than or equal to 2%, OR - A TOAP is developed when SCED cannot fully resolve the constraint |
| Planned Outage | IF: - A post-contingency overload is due to a planned outage on a transmission line(s) or a transmission facility; THEN: - Locate the TOAP in the Outage Notes, - Follow the same process as a MP outlined above. |
| Forced Outage | IF: - A post-contingency overload is due to a forced outage or planned outage not recognized by Outage Coordination on a transmission line(s) or a transmission facility; THEN: - Follow the same process as a MP outlined above. |
| LOG | Log all actions taken. |

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15 | 6.3.1 (1) | 6.3.2(2) | 6.5.1.1(a)&(c) |
| --- | --- | --- | --- | --- |
|  | 6.5.5.1(2) &(3) | 6.5.6 | 6.5.7 | 6.5.7.7 |
|  | 6.5.9.1(1)(c) | 6.6.7.1 | 6.7.6 |  |
| Guide Reference | 2.2.4 | 2.7.2(h)(ii) | 2.7.4.1(1) | 2.7.4.3 |
| NERC Standand | EOP-001-0.1b R4.2 | IRO-002-2 R6, R8 | IRO-005-3.1a R1.2, R1.3, R1.4 | NUC-001-2 R4.2 |
|  | TOP-002-2.1b R8, R10 | TOP-004-2 R6.2 | TOP-006-2 R2 | VAR-001-2 R1, R2, R4, R6, R7, R8, R9, R10, R12 |
|  | VAR-002-1.1b R3.1 |  |  |  |

| Version: 1 | Revision: 14 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "Seasonal Voltage Profiles" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS) Secure site. Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Comanche Peak Voltage Table | For Comanche Peak: - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. |
| STP Voltage Table | For South Texas Project: - Plant Configuration; - Maximum kV; - Minimum kV. - Normal line up, through 12/31/2015; - 362.25; - 340. - Alternate line up, through 12/31/2015; - 362.25; - 347. - Alternate without Unit Auxiliary Transformer, through 12/31/2015; - 362.25; - 355. - All line ups, after 12/31/2015; - 362.25; - 331. The STP Switchyard Facilities’ steady state voltage, with both STP units off-line, should be maintained within the ranges above. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is the STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated in the voltage tables; THEN: - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate QSE. |
| ### Voltage Issues |  |
| NOTE | - Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Desktop Guide Transmission Section 2.9. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damages is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implemented and studies are performed showing that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 345 – 359. 138; 131.1 – 144.9; 138 – 144. 69; 65.55 – 72.45; 69 – 71.5. |
| 1 | WHEN: - Indicated by SCADA alarms, RTCA OR - Notified by a TO of voltage concerns; THEN: - Ensure the appropriate TO has utilized all Static Reactive Power Resources (capacitors, reactors, change transformer taps). |
| 2 | IF: - All Static Reactive Power Resources have been utilized and there is still an issue; THEN: - Coordinate with the appropriate TO, AND - Instruct the appropriate QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script to appropriate QSE: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me. That is correct, thank you.” |
| 3 | IF: - Voltage response is still unacceptable; THEN: - Notify QSE to place Static devices in service in the area needed. |
| Exceed URL | ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL as displayed on the EMS RTNET UNIT MVAR display Min and Max columns for the resources current output level. IF: - Instructing a QSE’s Generation Resource to exceed its Unit Reactive Limit (URL); THEN: - Issue a VDI to the QSE for exceeding the URL (Exceed URL VDI). The VDI must include the following: - Resource name - Specific voltage set point. - Start time - End time - Choose “HOLD X VOLTAGE LEVEL” as the Instruction Type from Resource level - Notify Operations Support Engineer of instruction, they will be providing analysis to Settlements. |
| Reduce MW | IF: - MW output must be reduced to follow a voltage support instruction to avoid violating the CURL or URL; THEN: - Issue a VDI to the QSE providing Voltage Support Service (VSS VDI). The VDI must include the following: - Resource name - MW level at time of instruction - MW level Resource needs to move to for Voltage Support - Start time - End time - Choose “STAY AT/ABOVE X MW/MVAR LEVEL” or “STAY AT/BELOW X MW/MVAR LEVEL” as the Instruction Type from Resource level - Notify Operations Support Engineer of instruction, they will be providing analysis to Settlements. |
| NOTE | The Change columns on the UNIT_MVAR display indicate how many MVAR the CURL or URL is being exceeded by at this time. If the Change columns are both zero (0), the CURL or URL is not being exceeded. |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| NOTE | The North – Houston VSAT voltage stability limit is an IROL; the actual flow MUST NOT exceed the limit for more than 30 minutes. This is a violation of the NERC Reliability Standards. Please refer to procedure section 4.4. |
| Valley Import | WHEN: - VSAT runs and provides an updated limit for the North-Houston and Valley Import; THEN: - Update RTMONI. |
| 1 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margins listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) - Confirm VSAT indicates either “Normal” or “Pending” Reliability Margin Table. Scenario Name; Margin. O-DFW_L; 200MW. O-CORP_L; 75MW. O-VAL_L; 75MW. O-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. For N-H_G and N_H_L: Refer to section 4.4 North-Houston Voltage Stability Limit of this procedure. |
| 2 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the current Reliability Margin pre-contingency value is less than the Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 3. |
| 3 | Determine the contingency status in RTCA (solved/unsolved). IF: - Solved, - Have Operations Support Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Operations Support Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct RUC Operator to commit additional resources in the weak bus area that are available. |
| 4 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 5 | Determine if the current Reliability Margin pre-contingency value is greater than the Margin Value from the table above. IF: - The current Reliability Margin pre-contingency value is greater than the Margin; THEN: - No further action is required. OR IF: - The current Reliability Margin pre-contingency value is less than the Margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 3. If no additional generation is available, continue. |
| 6 | IF: - No additional generation is available; THEN: - Notify Operations Support Engineer to create a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT. |
| NOTE | Operations Support will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > AVR AND PSS Status |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, - Notify the appropriate TO of the change in status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “OPS Advanced Network Applications” - “1 ERCOT System Operators” |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R3.1, R3.3, R5 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-3.1a R1.5 |

| Version: 1 | Revision: 12 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted, QSEs should be notified via Hotline call (see 2b for typical script). - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC falls < 2300 MW; THEN: - Using the Hotline, notify all TOs to implement EEA 1. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is declaring EEA 1 due to Physical Responsive Capability is below 2300 MW. [TO] please repeat this back to me. That is correct, thank you” After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 2. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | The Load Management Program step below is only to be considered on weekdays (except holidays) during the summer months (June to September) between 1330 and 1900 hours due to restrictions in TO Load Management Program contracts. |
| Load Management Program | Monitor predicted load increase over the next hour and into the peak hours as indicated in the prevailing ERCOT Load Forecast. * Only applies during the summer months (June to September) IF: - The current time is AT LEAST 13:30 BUT NOT AFTER 16:00, and - It is predicted that this event will proceed to EEA level 2; THEN: - Using the Hotline, contact all TOs with Load Management Programs, requesting implementation of their Load Management Programs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; This call applies to the following Transmission Operators: Oncor, Centerpoint, AEP, and TNMP. At [xx:xx], ERCOT is requesting that these TOs deploy all available capacity from their Load Management Programs due to continued increased load growth. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC falls < 1750MW; THEN: - Using the Hotline, notify all TOs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. - If the energy conservation call has not been made previously, it can be combined with this call (see step Media Appeal below). Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2; - [Load Resources and/or ERS Resources] have been deployed, - Reduce customer loads by using distribution voltage reduction measures, if deemed beneficial - *Request deployment of Load Management Programs [TO] please repeat this back to me. That is correct, thank you” * Only applies during the summer months (June to September) and if not already deployed in EEA 1. After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 3. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Media Appeal | - Unless already in effect, verify with the shift supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify TOs, via Hotline, that a media appeal for conservation is in effect. Typical Hotline Script: “This is ERCOT Operator [first and last name]; ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Using the Hotline, notify all TOs to implement EEA 3 and any measures associated with EEA 1 and 2, if not already implemented - *Request deployment of Load Management Programs * Only applies during the summer months (June to September) and if not already deployed. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3. ERCOT is directing all Transmission Operators to shed their share of [amount] MW. Transmission Operators are to report to ERCOT when this is complete. [TO] please repeat this back to me. That is correct, thank you”. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 7.5	Block Load Transfer

Procedure Purpose:  To transfer loads, located in ERCOT to a Non-ERCOT system or from a Non-ERCOT system to ERCOT during emergencies conditions.

| Protocol Reference | 6.5.9.5 | 6.5.9.5.1 | 6.5.9.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.4 |  |  |  |
| NERC Standard | EOP-001-0.1b R3.2, R4.2, R7.2, & R7.4 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Restoration of service to outage customers using BLT’s will be accomplished as quickly as possible if the transfers will not jeopardize the reliability of the ERCOT Interconnection. - BLTs that are comprised of looped systems may be tied to the non-ERCOT Control Area’s electrical system(s) through multiple interconnection points at the same time. Transfers of looped configurations are permitted only if all interconnection points are registered and netted under a single Electric Service Identifier (ESI ID) and represented by a single TSP or DSP or netted behind Non-Opt-in Entity (NOIE) metering points. |
| ### ERCOT picks up Load for Non-ERCOT System |  |
| 1 | IF: - ERCOT is requested to pick up load for CFE, MISO or SPP; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists - If BLT is registered (refer to Desktop Guide Common to Multiple Desks Section 2.5): - Issue VDI to the QSE listed (if no QSE listed, no VDI needed) - If BLT is not registered, proceed to step 2 - Determine the amount of load being transferred into ERCOT - Issue VDI to QSE (if applicable) - Choose QSE level tab - Choose [Proper QSE from Desktop Guide] for Participant Name - Choose “OTHER For QSE” for Instruction Type - In text, state “BLT from SPP, MISO or CFE to ERCOT” - Send e-mail to “BLT” distribution list with the above information - Include in e-mail whether BLT is modeled or not |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists - If no issues, allow the BLT - Determine the amount of load being transferred into ERCOT - Send e-mail to “BLT” distribution list with information - Include in e-mail that BLT is not registered - Include in e-mail whether BLT is modeled or not |
| 3 | For BLTs that are deployed in an emergency and are not modeled in the Network Operations Model, the responsible TO will notify ERCOT as soon as practicable after deployment. |
| 4 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Terminate the BLT. |
| ### Non-ERCOT System picks up Load for ERCOT |  |
| 1 | IF: - CFE, MISO or SPP picks up load for ERCOT; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists, - If BLT is registered (refer to Desktop Guide Common to Multiple Desks Section 2.5): - Issue VDI to the QSE listed (if no QSE listed, no VDI needed) - If BLT is not registered, proceed to step 2 - Determine the amount of load being transferred out of ERCOT - Issue VDI to QSE if applicable (if applicable) - Choose QSE level tab - Choose [Proper QSE from Desktop Guide] for Participant Name - Choose “OTHER For QSE” for Instruction Type - In text, state “BLT from ERCOT to SPP, MISO or CFE” - Send e-mail to “BLT” distribution list with the above information - Include in e-mail whether BLT is modeled or not |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists, - If no issues, allow the BLT, - Determine the amount of load being transferred out of ERCOT, - Send e-mail to “BLT” distribution list with information - Include in e-mail that BLT is not registered - Include in e-mail weather BLT is modeled or not |
| 3 | For BLTs that are deployed in an emergency and are not modeled in the Network Operations Model, the responsible TO will notify ERCOT as soon as practicable after deployment. |
| 4 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Terminate the BLT. |
| NOTE | If the Alamito Creek (ALMC) to Presidio (PRES) 69 kV transmission line trips, CFE will automatically pick up approximately 2 MW of load on the Presidio/Gonzales BLT. When AEP TO has informed you that this happened, follow step 1 above. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | September 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT)Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 2.1 2.3 3.4 4.1 4.2 7.4 10.1 | 1.0 / 1 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 13 1.0 / 5 1.0 / 3 1.0 / 2 | Updated Scope Changed TSP to TO Updated database load script Changed insecure state to emergency condition Updated 1st Note, steps 6 & 8 in Post Contingency Overloads, steps 2 & 3 in Managing Constraints in SCED, added Model Inconsistencies/Updates procedure Updated Notes 1 & 2, Steps 1 & 2 Changed insecure state to emergency condition Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 3.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.5 9.2 10.1 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 14 1.0 / 6 1.0 / 8 1.0 / 7 1.0 / 6 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 8 1.0 / 7 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated Operations Support Engineer Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, added 3rd Note, updated step 1 in Review Planned Outage Notes, steps 1, 2, 3, 4, 6, 7, 8, 9 & QSGR in Post Contingency Overloads, step 2, 4 & Log in Managing Constraints in SCED Updated Operations Support Engineer Updated Operations Support Engineer & step 1, 2 & 3 Updated Operations Support Engineer Updated Desktop Guide reference, 2nd Note, step 5 & SPS Posting & deleted step 4 in SPS, all steps in Mitigation Plan & Temporary Outage Action Plan Updated Desktop Guide reference Updated step 1 in Watch Updated TSP to TO, Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, changed TSP to TO, Desktop Guide reference & step 1 of Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Watch Updated step 1 in Implement EEA Level 1 & step 1 in Implement EEA Level 3 Updated script in step 1 in Restore Firm Load Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer & Desktop Guide reference Updated Desktop Guide reference Updated all steps in Telemetry Issues that could affect SCED and/or LMPs, step 1 in Backup/Alternate Control Center Transfer & Operations Support Engineer | March1, 2012 |
| 3.1 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.2 8.3 8.4 | 1.0 / 3 1.0 / 7 1.0 / 15 1.0 / 9 1.0 / 8 1.0 / 7 1.0 / 4 1.0 / 9 1.0 / 9 - / 8 1.0 / 8 1.0 / 5 1.0 / 4 1.0 / 0 1.0 / 4 1.0 / 2 1.0 / 4 | Updated step Gap Study Added TSAT Updated step 4 & deleted step 9 in Post-Contingency Overloads, clarified step 2 & 3 in Managing Constraints in SCED, Added Unsolved Contingencies Updated for TSAT tool, added Managing W-N during System Failures Updated step IROL and ‘instructing’ to ‘directing’ Updated step Status Change & ‘instructing’ to ‘directing’, updated step 3, 4 & log in RAP, added step 3 and log in PCAP, update Note, added TO Issue in MP Updated Opportunity Outage procedure Added Valley Import to VSAT procedure, deleted step 2 in PSS/AVR section Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather Added Load Management Programs in Implement EEA Added Load Management Programs in Restore EEA Updated for NPRR405 Changed ‘TDSP’ to ‘TO’ & T/S Operator to Real-Time Deleted Cold Weather Revised to 8.2 and changed Severe Cold Weather to Extreme Cold Weather Revised to 8.3, added OCN & Emergency Notice Revised to 8.4 and changed T/S Operator to Real-Time Operator | May 1, 2012 |
| 2.3 4.1 4.5 6.1 7.2 7.3 7.5 | 1.0 / 6 1.0 / 16 1.0 / 8 1.0 / 10 1.0 / 9 1.0 / 9 1.0 / 6 | Updated Database load with W-N active and Site Failover with W-N steps Added Constraint SF Cut Off step, updated step 2 & 3 in Managing Constraints in SCED Updated 2nd Note, added Basecase continuous SPS triggering step in SPS, updated step 1 in RAP, step Note, SCED unable to fully resolve constraint, & < 2% Absolute Shift Factors in MP, 1st Note in TOAP Updated step Valley Import Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT | June 1, 2012 |
| 1.3 3.3 4.1 4.4 5.1 6.1 7.1 7.2 7.3 8.3 9.2 | 1.0 / 1 1.0 / 8 1.0 / 17 1.0 / 9 1.0 / 5 1.0 / 11 1.0 / 10 1.0 / 10 1.0 / 10 1.0 / 3 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated step 2 Updated step Constraint SF Cut Off, Managing Congestion during SCED Failure Updated step ≤300MW Updated Maintenance Level 2 and 3 outages Updated STP Voltage Tables Updated all step 1’s Updated Load Management Program Updated step 1 Updated scripts Updated 4th note | July 16, 2012 |
| 2.3 4.4 | 1.0 / 7 1.0 / 10 | Added Note to step Database Load Updated step IROL | August 29, 2012 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.7 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 8 1.0 / 2 1.0 / 9 1.0 / 18 1.0 / 10 1.0 / 11 1.0 / 9 1.0 / 3 1.0 / 12 1.0 / 11 1.0 / 11 1.0 / 11 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 5 | Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated PUN section and added to make call to HHGT Added Hotline script and to make call to HHGT Added Hotline script and to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated step 1 and added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT | September 12, 2012 |
| 2.2 3.1 3.2 3.3 3.4 4.1 4.3 4.4 4.5 5.1 5.2 6.1 7.4 8.3 9.1 | 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 10 1.0 / 2 1.0 / 19 1.0 / 11 1.0 / 12 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 13 1.0 / 7 1.0 / 5 1.0 / 4 | Added Hotline Call Communication Moved protective relay section to 5.2 Updated step 3 Split VSAT/TSAT and SE/RTCA out into separate procedures Updated steps Immediate Action Updated step Unknown Operating State, all steps in Evaluate Real-Time Contingency Analysis Results, steps 1, 4 & 6 in Post-Contingency Overloads Added 1st Note Added 1st Note, Updated 2nd NOTE & step 0 MW Updated 2nd Note Updated Returning from Planned Outage Early Added new procedure Updated Exceed URL, Reduce MW, added NOTE & moved step 1 to section 3.3 and renumbered Added Note Word smith OCN, Advisory, & Watch Updated step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.5 4.1 4.4 4.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 0 1.0 / 20 1.0 / 13 1.0 / 11 1.0 / 14 1.0 / 12 1.0 / 7 | Updated step 3 Added procedure Updated Note, Constraint Shift Factor Cut Off, Post-Contingency Overloads steps 4-9 , QSGR & Managing Constraints in SCED step 2 & 4 Updated step VSAT Updated Special Protection Systems (SPS) (Identified as RAS in EMS) step 2, Remedial Action Plan (RAP) steps 1-5, & step 3 Pre-Contingency Action Plan (PCAP) Updated 2nd Note and steps 1-3 Voltage Issues Deleted step 2 per NPRR 480 Updated all step 1’s & added step 3 to clarify 6.5.9.5.2(1) | March1, 2013 |