- Power Operations Bulletin # 625

ERCOT has posted/revised the Real Time Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.6	Site Failovers and Database Loads

Procedure Purpose: To provide notice to the Market Participants when ERCOT performs site failovers and database loads.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Database Load | Approximately 5 - 30 minutes before database load, make the following Hotline call to QSEs: Typical Hotline Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a database load on its Energy & Market Management Systems. During this time, SCED Base Points will reflect accurate dispatch instructions. In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes. Any questions”? NOTE: Adjust script as needed for situation, such as EMS/MMS migration. |
| Site Failover Posting | The site failover message is already built in Notice Builder under “EMMS Site Failover”. |
| Site Failover | Approximately 5 - 30 minutes before site failover, make the following Hotline call to QSEs: Typical Hotline Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 30 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. Any questions?” |
| Site Failover with W-N Active | IF: - The West – North is active; THEN: - MP’s base points should remain the same during the failover, however to ensure the management of WGR’s is sustained, use the following script: Approximately 5 minutes before the site failover, make the following Hotline call to QSEs: Typical Hotline Script: “At [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 30 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. The West to North constraint is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output during this failover. A call will be made when we have completed the site failover. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Site Failover Complete | Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [XX:XX], the site failover is complete. Thank you.” |
| If EBPs are needed | IF: - Site Failover is taking longer than expected or - SCED is not solving with a valid solution and EBPs are needed; THEN: - Enter the EBP increment/decrement as needed to control frequency, - Notify Resource Operator to post a message on MIS Public , - Notify Transmission Operator to make Hotline call to TOs, - Make the following hotline call to QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice and Emergency Base Points will be issued. ERCOT will make another hotline call when the site failover is complete. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| If EBPs are needed and W-N was Active before Site Failover started | IF: - Site Failover is taking longer than expected or - SCED is not solving with a valid solution and EBPs are needed, AND - The West – North was active before the start of the Site Failover; THEN: - Enter the EBP increment/decrement as needed to control frequency, - Notify Resource Operator to post a message on MIS Public , - Notify Transmission Operator to make Hotline call to TOs, - Make the following hotline call to QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. ERCOT is issuing an Emergency Notice and Emergency Base Points will be issued. WGRs which were required to follow their Base Point instruction before the site failover are required to continue to stay at their current output. ERCOT will make another hotline call when the site failover is complete. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Site Failover Complete If EBPs were needed | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Emergency Notice, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [XX:XX], the site failover is complete, SCED basepoints are now valid and ERCOT is canceling the Emergency Notice. All QSEs should continue normal operations. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |

## 2.7	Switching Control Center

Procedure Purpose: To provide notice to the Market Participants when ERCOT is working from the Alternate Control Center.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Hotline Call | When transferring operations from primary site to alternate site (and vice versa). Make the following hotline call to QSEs: Typical Hotline Script for working from Alternate site: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the alternate control center until further notice, use the OPX numbers for Bastrop. [QSE], please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script for working from Primary site: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will be working from the primary control center until further notice, use the OPX numbers for Taylor. [QSE], please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| MIS Posting | Typical MIS Posting for working from Alternate site: ERCOT is working from alternate control center. Typical MIS Posting for working from Primary site: ERCOT is working from primary control center. |

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.3.2(2) | 6.5.7.6.2.2 | 6.5.9.1(1)(b) | 8.2 (2)(b)(vii) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.3.1.2 |  |  |  |
| NERC Standard | BAL-002-1 R2.4, R6 | BAL-005-0.2b R8 | BAL-007 (Field Trial) | EOP-002-3.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 13 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 611.5 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -611.5 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, - Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constants) |
| Base Point Deviation | IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) - If unit trip: - Time of unit trip, - Name of unit, - Approximate net MW on unit, - Approximate lowest TrueTime frequency (use 3 decimals), - Amount of RRS deployed (if any), AND - Approximate ERCOT load. |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: - QSE will request VDI(s) - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time - A VDI will be needed for each Resource IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per deployment for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - Manually run SCED IF: - Frequency goes above 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, - Enter manual offset (the offset will continue until removed). IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 10 MINUTES | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Operations Support Engineer to send an event notification to BAALfieldtrials@ercot.com. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Call QSE with instruction and follow up with an electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Call QSE with instruction and follow up with electronic VDI - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter “capacity surplus” in “other information” |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.80 Hz - Load Resource providing RRS – 59.70 Hz |
| Monitor/ Deploy | IF: - Frequency drops below 59.95 Hz, AND - Regulation Up service remains and is deploying; THEN: - Manually run SCED (do not run SCED more than once between SCED runs) IF: - Frequency drops below 59.95 Hz, AND - Out of Up Regulation; THEN: - Check the GTBD2[HDL] on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset - If using OpsMon Dashboard, do not enter an offset > than GTBD2[HDL] - If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - GTBD2[HDL] on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS does not have adequate up room; THEN: - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the “Manual RRS” to activate box, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - If room is available - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the “Manual RRS” to activate box, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. - Notify the Shift Supervisor of the need to possibly commit additional Resources. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available - Manually run SCED, - Log the event and notify Operations Support Engineer to send notification of the event to BAALfieldtrials@ercot.com. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available, manually run SCED. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED. |
| Stable | IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions taken. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data. |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Control>Generation Area Status>Current Frequency Deviation from Nominal IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Select Skip on the incorrect Frequency device, - Contact the Help Desk. |

## 3.2	Monitor Large Ramp Events

Procedure Purpose:  The ERCOT Large Ramp Alert System (ELRAS) is designed to monitor the probability of large wind output ramps in the ERCOT region and provide ERCOT Operators with further situational awareness.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The potential for a large ramp can be identified using the “Graphical Forecast” page of ELRAS in the Real-Time Viewing Mode. An example of the page is in figure 1 below. The “Graphical Forecast” page plots the probability of a ramp rate event starting at a given time during the next 6 hours. The graphical displays are broken up into three timeframes; 15-minute probabilities, 60-minute probabilities, and 180-minute probabilities, and Up and Down ramp rate events are split up for each time frame. These displays are interpreted by first looking at a particular interval on a given display. The value for that interval on that display is characterized as the probability of a given MW change occurring over a specified amount of time starting at the specified interval. For example, looking again at figure 1, the “Graphical Forecast” is showing a 50% probability of at least a 2,000 MW increase occurring over 180 minutes starting at 18:00. In other words, between 18:00 and 21:00 there is a 50% chance that the aggregate wind output will increase by at least 2,000 MW. For the purpose of this procedure, the forecasted ramp rates to be considered significant are those that are indicated in Red; 1,000 MW in 15-minutes, 2,000 MW in 60-minutes, and 4,000 MW in 180-minutes. In the event that one of these ramp rates is forecasted to have at least a 50% probability of occurring, determine if the system has the ramp rate to keep up with the wind ramp. |
| ### Down Ramp Event |  |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| 2 | IF: - There is a 50% probability of a projected system wide down-ramp of 4,000 MW within the next 180 minutes, OR - There is a 50% probability of a projected system wide down-ramp of 2,000 MW within the next 60 minutes; THEN: - Refer to the “180 min. HASL(COP) - LF or 60 min. HASL(COP) - LF” on the 60 to 180 minute OpsMon Dashboard to determine if system ramp rate capability is sufficient, AND - Make a Hotline call to provide situational awareness about a possible down-ramp event of 2,000 MW or greater within the next 60 minutes or 4,000 MW or greater within the next 180 minutes. IF: - System ramp rate is not sufficient; THEN: - Notify RUC Operator to procure Resources as needed. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN due to a 50% probability of a [4,000 MW down-ramp in the next 180 minutes] [2,000 MW down-ramp in the next 60 minutes]. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]. [QSE] please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | IF: - There is a 50% probability of a projected system wide down-ramp of 1,000 MW within the next 15 minutes; THEN: - Refer to the “HDL-Gen” on the 15 minute OpsMon Dashboard and the available Regulation UP Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Deploy Non-Spin as needed, and - Continue to monitor frequency and “HDL-Gen” |
| ### Up Ramp Event |  |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| 2 | IF: - There is a 70% probability of a projected system Wide up-ramp of 2,000 MW within the next 60 minutes; THEN: - Refer to the “60 min. LF - LSL(COP)” on the 60 to 180 minute OpsMon Dashboard to determine if system ramp rate capability is sufficient, AND - Make a Hotline call to provide situational awareness about a possible wind up-ramp event of 2,000 MW or greater within the next 60 minutes. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN due to a 70% probability of a 2,000 MW up-ramp in the next 60 minutes. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]. [QSE] please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | IF: - There is a 70% probability of a projected system wide up-ramp of 1,000 MW within the next 15 minutes; THEN: - Refer to the “Gen - LASL” on the 15 minute OpsMon Dashboard and the available Regulation DOWN Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Monitor frequency and run SCED as often as required. |
| Log | Log actions taken |

## 3.3	System Failures

Procedure Purpose:  To ensure that frequency is maintained in the event of an AGC failure.

| Protocol Reference | 6.5.9(1) | 6.5.9.1(2) | 6.5.9.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-005-0.2b R7 |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### SCED Failure |  |
| NOTE | When RLC sees that the SCED solution has not updated within the last 605 seconds, emergency base points (EBP) will automatically activate. This will have to be turned off manually by the operator when SCED recovers. After the EBP flag turns ON, enter increment/decrement MW and commit it, so that EBPs are actually sent out. Any time EBPs are activated, SCED solutions are being blocked from being communicated to MPs. |
| 1 | IF: - Any module of the SCED Workflow Controller fails; THEN: - Manually run the SCED process. |
| 2 | IF: - SCED still fails after manually running, AND - EBPs have automatically activated; THEN: - Contact the Help Desk, - Initiate an Emergency Notice Hotline call to QSEs, - If West – North (IROL) constraint is active, use script in step 3 - Notify Resource Operator to post a message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | Script to use if West – North IROL constraint was active when SCED failed: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. The West to North is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. |
| 5 | WHEN: - SCED is solving with a valid solution; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Emergency Notice, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], SCED base points are now valid and ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Log all actions taken and any issues with the Market Participants. |
| ### SCED Data Input Failure |  |
| 1 | IF: - SCED receives data input failures and gives erroneous results; THEN: - Manually activate EBP, - Contact the Help Desk, - Initiate the Emergency Notice Hotline call - If West – North (IROL) constraint is active, use script in step 2, - Notify Resource Operator to post the message on MIS Public, - Notify the Transmission Operator to make Hotline call to TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to data input failure to SCED. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 2 | Script to use if West – North IROL constraint was active when data failure occurred: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. The West to North is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 3 | Follow steps 4 and 5 above as needed. |
| ### RLC Failure |  |
| 1 | The Resource Limit Calculator (RLC) can fail independently of AGC. If RLC fails, SCED will not function (invalid results), even though it shows available. A RLC failure will be displayed to the Operator in the upper right corner of the RLC display as follows: - Process Status: RLC Up (Normal Operation) - Process Status: RLC Down (will be displayed in RED when failed) - RLC (PI Alarm) will be flashing RED. |
| NOTE | Regulation is functioning, RRS is not. LFC (AGC) will automatically switch to EBP mode. |
| 2 | IF: - RLC has failed; THEN: - Verify the status of AGC - IF AGC is also failed, proceed to the EMS (LFC and RLC) Failure procedure - Contact the Help Desk, - Initiate an Emergency Notice Hotline call to QSEs - If West – North (IROL) constraint is active, use script in step 3, - Notify Resource Operator to post the message on MIS Public - Notify Transmission Desk Operator to make Hotline call to TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to a SCED failure. ERCOT may issue Emergency Base Points until the issue is resolved. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | Script to use if West – North IROL constraint was active when RLC failed: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. The West to North is active; WGRs which are currently being curtailed and required to follow their Base Points are required to stay at their current output. ERCOT may issue Emergency Base Points until this issue has been resolved. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 4 | MONITOR: - Regulation Service (Up/Dn) margins to ensure frequency can be adequately maintained. IF: - It is determined that remaining Regulation Service (Up/Dn) is no longer sufficient to maintain system frequency; THEN: - Enter the EBP increment/decrement as needed to control frequency to recall deployed Regulation. |
| 5 | WHEN: - RLC is restored; THEN: - Remove the Emergency Base Point flag, - Initiate Hotline call to cancel the Emergency Notice, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel Emergency Notice with TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], SCED solutions are now valid and ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Log all actions taken. |
| ### LFC (AGC) Failure |  |
| NOTE | When LFC (AGC) is paused or suspended and RLC and SCED are functioning, then Regulation, RRS and EBP are not functioning. |
| 1 | IF: - LFC is not functioning as indicated by: - AGC is SUSPENDED or PAUSED OR - “Last AGC Cycle” time on Generation Area Status display is not updating; THEN: - Verify the status of RLC - If RLC is also failed, proceed to the next procedure “EMMS Failure” - If RLC is still functioning properly, - Contact Help Desk, - Continue with this procedure REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency control, THEN: - Direct selected QSE to go on constant frequency, - As time permits, issue electronic VDI, - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into ‘Monitor” mode. Typical Script for Constant Frequency: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing you to go on constant frequency until further notice due to an LFC failure. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs - Notify Resource Operator to post the message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to LFC failure and has placed a QSE on Constant Frequency to provide regulation. SCED Base Points are valid and should be followed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | MONITOR: - Frequency and capacity availability for QSE on constant frequency, AND/OR - The QSE on constant frequency notifies ERCOT of capacity issue; THEN: - Determine available capacity for SCED and enter an operator manual offset, OR if no SCED room - Issue electronic VDI(s) as needed, to Commit/Decommit additional generation to maintain Grid Reliability. - Choose “COMMIT or DECOMMIT” as the Instruction Type from Resource level - Enter “capacity or capacity surplus” in “other information” |
| 4 | WHEN: - ERCOT AGC Control is functioning properly; THEN: - Direct QSE to come off Constant Frequency by ending the electronic VDI, - Place ERCOT AGC back into “ON” mode, - Initiate Hotline to cancel the Emergency Notice to QSEs, - Notify Resource Operator to cancel the MIS posting, - Notify Transmission Operator to cancel the Emergency Notice with TOs. Typical Script for Constant Frequency: “This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning, ERCOT is directing you to end constant frequency. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning and ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Log all actions taken. |
| ### EMMS (LFC and RLC/SCED) Failure |  |
| NOTE | Regulation, RRS, UDBP, BP, EBP, and manual offset not functioning. |
| 1 | LFC (AGC): - AGC is SUSPENDED or PAUSED, - “Last ACE crossing zero” time on the Generation Area Status page is not updating, - AGC operation adversely impacts the reliability of the Interconnection, - SCED and EMS are not functioning, - Problem cannot be resolved quickly RLC: - Process Status: RLC Down will be displayed in RED in the upper right hand corner of the RLC display - RLC (PI Alarm) will be flashing RED. REFERENCE Display: EMP Applications>Generation Area Status>Nodal Operational Status>Resource Limits Data DETERMINE: - Which QSE has ample capacity to place on constant frequency Control; THEN: - Direct the selected QSE to go on constant frequency - As time permits, issue an electronic VDI - Choose “OPERATE AT CONSTANT FREQUENCY” as the Instruction Type from QSE Level - Place ERCOT AGC into “Monitor” mode Typical Script for Constant Frequency: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing you to go on constant frequency until further notice due to an LFC and SCED failure. Please repeat this back to me. That is correct, thank you”. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | THEN: - Initiate the Emergency Notice Hotline call to QSEs, - Notify Resource Operator to post the message on MIS Public, - Notify Transmission Operator to make Hotline call to TOs Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to an LFC and SCED failure. ERCOT has placed a QSE on Constant Frequency. All remaining QSEs should hold their Resources to their current output level until instructed by ERCOT. ERCOT may issue unit specific deployments to Resources as required. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | MONITOR: - Frequency and Capacity availability for QSE on constant frequency, AND/OR - The QSE on Constant Frequency notifies ERCOT that they are having control issues; THEN: - Determine which QSE has the most available Capacity, - Issue a unit specific instructions to assist the QSE on Constant Frequency, - Choose “Other For Resource” as the Instruction Type |
| 4 | IF: - There is no longer any available capacity to issue unit specific deployments; THEN: - Issue electronic VDI(s) as needed, to Commit/Decommit additional Generation to maintain Grid Reliability - Choose “COMMIT or DECOMMIT” as the Instruction Type from Resource level. - Enter “capacity or capacity surplus” in “other information” |
| 5 | WHEN: - AGC and RLC is restored; THEN: - Direct QSE to come off constant frequency by ending VDI, - Place ERCOT AGC back into “ON” mode, - Cancel VDI(s) for additional generation, if issued, - Initiate Hotline to cancel Emergency Notice to QSEs, - Notify Resource Operator to cancel MIS posting, - Notify Transmission Operator to cancel Emergency Notice with TOs. Typical Script for Constant Frequency: “This is ERCOT Operator [first and last name]. At [xx:xx], LFC is now functioning, ERCOT is directing you to end constant frequency. Please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At, [xx:xx], LFC is now functional and SCED solutions are valid. ERCOT is canceling the Emergency Notice. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Log all actions taken. |

## 3.4	Potential DCS Event

Procedure Purpose:  To meet NERC Recovery Criteria after a potential NERC Reportable DCS Event

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.4.2(2)(a)(ii) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-1 R2.4, R6.2 | EOP-001-0.1b R5 | EOP-002-3.1 R5, 6.1 |  |

| Version: 1 | Revision: 8 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NERC Recovery Criteria | Restore system frequency to the following limit within 15 minutes: - Scheduled Frequency if it was greater than or equal to scheduled Frequency prior to the disturbance, OR - Its pre-disturbance value if it was less than scheduled frequency prior to the disturbance. ERCOT shall fully restore the minimum Contingency Reserve requirement of ERCOT Region’s Largest Single Contingency (1375 MW) within 90 minutes. The 90 minute restoration period begins at the end of the Disturbance Recovery period which is when system frequency is restored as described above. ERCOT will restore Responsive Reserves to 2300 MW or greater, as soon as possible. |
| DCS | - A loss of Generation, equal to or greater than 1100 MW (consisting of a single generator or the total of multiple generators within 1 minute), or there is NO indication of a Generation loss and the magnitude of the event is determined to be greater than 1000 MW - Determine the magnitude of the event by using the “Raw ACE” tag, Analyze the change in this tag after a minimum of 30 seconds to avoid the initial overshoot. Example: If the “Raw ACE” pre-disturbance value is +150 MW, and post disturbance (30 seconds) value is -950 MW, then the total generation loss is 1100 MW. This constitutes a NERC Reportable DCS Event. - It can be assumed that a potential NERC Reportable DCS Event has occurred |
| NOTE | The steps below will need to happen quickly, let phones ring, or if available, another desk will take the calls. |
| 1 | IF: - ERCOT experiences a low frequency disturbance; THEN: - Immediately check to ensure that SCED sees the units correct telemetry (HSL of zero or Resource Status of “off”), Contact the QSE(s) if telemetry needs to be changed, - If SCED does not automatically execute within 60 seconds of the event, manually execute a SCED run, - Enter a manual off-set as necessary. |
| 2 | IF: - Frequency dropped below 59.7 Hz; THEN: - Load Resources have deployed on UFR. |
| NOTE | If Load Resources are deployed it may become necessary to periodically execute SCED manually and/or use the manual offset to control frequency. |
| 3 | WHEN: - System frequency has been restored; THEN: - Make Hotline call to QSEs to recall Load Resources. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is recalling all Load Resources. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| PRC Below 2300 | IF: - PRC < 2300 MW; THEN: - Implement EEA (see section 5.3). |
| Log | Make log entry. |

## 3.7	Responding to North to Houston Interface Issues

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.9.1(1)(e) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R2, R4.2 | EOP-003-1 R1 | IRO-002-2 R6, R8 | IRO-003-2 R1 |
|  | IRO-004-2 R3 | IRO-005-3.1a R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 R1 | TOP-002-2.1b R10 |
|  | TOP-004-2 R1, R2, R6, R6.6 | TOP-006-2 R5 | TOP-007-0 R3, R4 | TOP-008-1 R1 |

| Version: 1 | Revision: 3 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Issue Watch & Deploy Non-Spin | WHEN: - Notified by the Transmission Operator that Non-Spin needs to be deployed in the Houston area for the North-Houston Interface; THEN: - Using the hotline, issue a Watch, - Resource Operator will deploy the Non-Spin Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North to Houston interface. ERCOT will be deploying Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| Issue Emergency Notice & Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the hotline, issue the Emergency Notice Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT has issued an Emergency Notice for the North to Houston interface and has issued you an electronic directive for the deployment of specific Load Resources to alleviate the condition. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Using the hotline, cancel the Emergency Notice, Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Emergency Notice for the North to Houston interface and has issued you an electronic directive for the recall of Load Resource deployments. ERCOT is reminding everyone that a Watch is still in effect until further notice. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Using the hotline, cancel the Watch, Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the North to Houston interface. ERCOT has recalled Non-Spin to specific resources to alleviate the condition. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Log | Log the actions taken. |

## 4.1	Managing SCED

Procedure Purpose: To ensure that a SCED solution has solved and that the solution is reasonable.

| Protocol Reference | 3.8.3 | 6.3.2(2) | 6.5.7.1.13(3) | 6.5.7.6.2.1(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.7.6.2.2 | 6.5.7.6.2.1(1) | 6.5.7.6.2.1(4) | 6.5.1.1(b) |
|  | 6.5.5.2(6) | 6.5.7.6.2.3 | 6.5.9.1(2) |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Workflow Controller Messages |  |
| NOTE | The SCED Workflow Controller provides three color coded messages as indicated in the following: - GREEN – Informational (i) and Success (s) - BLUE – Warning (w) - RED – Error (e) and Fatal Error (f) |
| 1 | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>Workflow>SCED Workflow Messages Monitor SCED Workflow Controller logs for “Warning” and “Error” messages. |
| 2 | IF: - The log indicates an “Error” or “Fatal Error”; THEN: - Contact the Help Desk and notify all Control Room staff, - Attempt to resolve the issue, refer to Desktop Guide Real Time Desk Section 2.5, - Refer to Section 3.2 “Managing SCED Failures” in this procedure. |
| ### SCED Solution Time Parameter |  |
| NOTE | Typically SCED should produce a solution within 20 seconds. It is highly desirable to have at least 3 executions of SCED in any 15 minute period. |
| Automatic Trigger | Verify that SCED is automatically triggered: - Periodically every 5 minutes - About 60 seconds after RRS is automatically deployed by LFC IF: - SCED is not automatically executed (but has not failed); THEN: - Manually execute SCED, - Immediately notify the Shift Supervisor and Operations Support Engineer, - Continue to manually execute SCED approximately every 5 minutes until the condition is corrected. |
| Manual Trigger | SCED may be manually triggered when the following is identified: - Frequency deviates +/-0.05 Hz for more than 5 minutes - Generation Resource trips and Frequency is > 59.91 Hz - When approximately 50% of Regulation has been deployed - Approximately 60 seconds after Generation Resources providing RRS have been deployed. - As frequently as needed after Load Resources providing RRS have been deployed. |
| LOG | Log all actions taken as necessary. |
| ### Quick Start Generation Resource |  |
| QSGR | A Generation Resource that in its cold-temperature state can come On-Line within ten minutes of receiving ERCOT notice and has passed an ERCOT Quick Start Generation Resource test that establishes an amount of capacity that can be deployed within a ten minute period. |
| COP | The QSE for a QSGR that is available for deployment by SCED shall set the COP Resource Status ON, the COP LSL and HSL values to the expected sustainable LSL and HSL for the QSGR for the hour. If the QSGR is providing Non-Spin, then the A/S Resource Responsibility for Non-Spin shall be set to the Resource’s Non-Spin responsibility in the COP. If the Resource’s Non-Spin responsibility is greater than the difference between HSL and LSL, then the QSGR that is available for deployment by SCED shall set the COP LSL to zero. |
| Telemeter | The QSGR that is available for deployment by SCED shall telemeter a Resource Status of ON and an LSL of zero prior to receiving a deployment instruction from SCED. This status is necessary in order for SCED to recognize that the Resource can be Dispatched. The status of the breaker shall be open and the output of the Resource shall be zero in order for the State Estimator to correctly assess the state of the system. After being deployed for energy by SCED, the Resource shall telemeter an LSL equal to or less than the Resource’s actual output until the Resource has ramped to its physical LSL. After reaching its physical LSL, the QSGR shall telemeter an LSL that reflects its physical LSL. The QSGR that is providing Off-Line Non-Spin shall always telemeter an Ancillary Service Resource Responsibility for Non-Spin to reflect the Resource’s Non-Spin obligation and shall always telemeter an Ancillary Service Schedule for Non-Spin of zero to make the capacity available for SCED. A QSGR with a telemeter breaker status of open and a telemeter Resource Status of ON shall not provide Regulation or Responsive Reserve Service. |
| QSGR Decommitment | Please refer to Desktop Guide Common to Multiple Desks for the QSGR decommitment process. |
| QSGR Qualification Test | WHEN: - Conducting a QSGR qualification test for Operations Analysis; THEN: - Issue a VDI - Choose “OTHER_RES” as the Instruction Type from Resource level - Enter “QSGR Qualification Test” in “Other Information” |
| ### Generation Resource Shut-down/Start-up Process |  |
| Shutdown/ Startup | Shut-down: - A QSE representing a Generation Resource that is not actively providing A/S may only use a Resource Status of SHUTDOWN through telemetry that the Resource is operating in a shutdown sequence requiring manual control and is not available for Dispatch. Start-up: - A QSE representing a Generation Resource that is not actively providing A/S may only use a Resource Status of STARTUP through telemetry that the Resource is operating in a start-up sequence requiring manual control and is not available for Dispatch. |
| NOTE | QSEs can manage basepoint deviations by adjusting their telemetered ramp rate. |
| NOTE | When a Resource is carrying “Off-Line” Non-spin and that Non-Spin is being recalled, the QSE would continue to show the Non-Spin responsibility on the Resource that is shutting down. |
| ### Combine Cycle Generation Resources |  |
| NOTE | WHEN: - Combine Cycle Generation Resources are changing configuration creating basepoint deviations THEN: - QSEs will need to manage their telemetered HSL for proper basepoints. |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to their telemetry (Resource status, Resource limits, A/S responsibilities, etc.) |
| QSE Override | IF: - The QSE cannot fix the issue in a timely manner; THEN: - Ask the Market Participant to over-ride the bad telemetry. |
| QSE unable to Override | IF: - For some reason, the QSE cannot override the bad telemetry; THEN - Request the Operations Support Engineer to override the bad telemetry, - Manually run SCED, if needed. |

## 5.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1, R5 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 12 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT Procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within first contingency criteria are not likely or possible due to Forced Outages or other conditions - Loss of communications or a control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from the Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - A transmission condition has been identified that requires Emergency Energy from any of the CFE DC-Ties - Conditions have developed that require additional Ancillary Services in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require operations with active transmission violations - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request - ERCOT varies from time-line for DAM/DRUC |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution and/or Emergency Base Points are issued - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum Reliability Standards during the Operating Period utilizing every Resource practically obtainable from the Market - ERCOT forecasts an inability to meet applicable Reliability Standards and has exercised all other reasonable options - A transmission condition has been identified causing unreliable operation or overloaded elements - A Single Severe Contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements for which no practicable Resource solution exists - ERCOT has determined a fuel shortage exists that would affect Reliability - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED) - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Generic Script |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Notify QSEs: Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public. - For “free form” messages, the “Notice Priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Log all actions taken. |
| ### Specific Scripts |  |
| NOTE | - At times, the Transmission operator takes the lead on the issuance of Hotline calls for specific procedures they have. The following scripts are to help guide you when specific procedures don’t exist for the Real-Time operator. |
| State Estimator Not solved In 30 MIN | - Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. . [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory due to ERCOTs State Estimator has not solved in the last 30 minutes. This is for your information only, no action is required. [QSE] please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. - Typical Hotline Script for cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory, ERCOTs State Estimator is now functional. [QSE] please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| RTCA Not solved In 30 MIN | - Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is issuing an Advisory due to ERCOTs Real-Time Contingency Analysis has not solved in the last 30 minutes. This is for your information only, no action is required. [QSE] please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script for cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory, ERCOTs Real-Time Contingency Analysis is now functional. [QSE] please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| VSAT Not solved In 30 MIN | Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Advisory due to ERCOTs Voltage Security Assessment Tool has not solved in the last 30 minutes. This is for your information only, no action is required. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script for cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name], at [xx:xx], ERCOT is canceling the Advisory, ERCOTs VSAT tool is now functional. [QSE] please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| GMD K-7 or Higher | Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory due to a [state K-Index Alert] geomagnetic disturbance storm alert that has been issued for [date and hours]. Report to ERCOT if you suspect any issues due to a GMD. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Advisory for the geomagnetic disturbance storm. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Qualifying Facility Directed to Operate below LSL | Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Emergency Notice for directing a Qualifying Facility [offline or operate below its LSL]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| West to North GTL Change | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch because the posted West to North Generic Transmission Limit has been updated on the MIS due to an unexpected changed on the system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the Generic Transmission Limit change. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| North to Houston GTL Change | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch because the posted North to Houston Generic Transmission Limit has been updated on the MIS due to an unexpected changed on the system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for the Generic Transmission Limit change. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Transmission Watch | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission Watch due to the post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] is being developed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script cancellation: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Transmission Watch for post-contingency overload of [constraint name]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |

## 5.2	Notifications for Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for the purpose of providing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.9.4.1 | 6.5.9.4(5) | 6.5.7.6.2.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.1(1) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-1 R2.4 | EOP-001-0.1b R3.1 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005-3.1a R1.4, R1.5, R4 |

| Version: 1 | Revision: 8 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at Management’s discretion, may issue an appeal through the Public News Media for voluntary energy conservation at any time. |
| ### Advisory |  |
| Issue Advisory | IF: - PRC < 3000 MW; THEN: - Using the Hotline, issue an Advisory, AND - Instruct the Resource Operator to post a message on MIS Public. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory due to Physical Responsive Capability falling below 3000 MW. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Cancel Advisory | WHEN: - PRC > 3000 MW; THEN: - Using the Hotline, cancel the Advisory, AND - Instruct the Resource Desk Operator to cancel MIS message. Typical script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Advisory for Physical Responsive Capability. Physical Responsive Capability is now above 3000 MW. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Ensure that all actions taken have been logged. |
| ### Watch |  |
| Issue Watch | IF: - PRC < 2500 MW, THEN: - Using the Hotline, issue a Watch, AND - Instruct the Resource Desk Operator to post a message on MIS Public. Typical script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to Physical Responsive Capability falling below 2500 MW. Suspend all Resource testing and update telemetered Resource Status Codes. ERCOT is reminding you, that you can schedule available interchange into ERCOT across the DC Ties. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Cancel Watch | WHEN: - PRC > 2800 MW, AND the Non-Spin has been recalled; THEN: - Using the Hotline, cancel the Watch, AND - Instruct the Resource Desk Operator to cancel MIS posting. Typical Hotline Script: ““This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. At this time, the Advisory is still in effect. Approved Resource testing may resume as scheduled. [QSE] please repeat this back to me. ” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Ensure that all actions taken have been logged. |

## 5.3	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT System to reduce the chance of Cascading Outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R3.1, R3.3, R5 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-3.1a R1.5 |

| ### Version: 1 | Revision: 12 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls < 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls < 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | Confidentiality requirements regarding Transmission Operations and System Capacity information will be lifted, as needed to restore reliability. |
| Pilot Project 30 MIN ERS | For the 30-Minute Emergency Response Service (ERS) pilot project, ERCOT may deploy 30-MIN ERS only during an EEA Level 1, 2, or 3, or during a Load-shed test. ERCOT will conduct unannounced ERS testing of Pilot Resources by way of a VDI to all QSEs representing Pilot Resources. |
| Pilot Project WS ERS | The weather-sensitive ERS is a pilot project that is also a 30-Minute product like the 30 MIN ERS. Weather-Sensitive ERS are only available June – September and for business hours 2 and 3. |
| INFO | 10-MIN ERS can only be deployed a maximum of 8 hours per contract period unless renewed (only 10 MIN ERS can be renewed). - Contract Periods: - February - May - June – September - October – January For current deployment data, refer to the Real Time Values Spreadsheet “ERS Tab” |
| Media Appeal | Public media appeals may be enacted prior to EEA. When a media appeal for voluntary energy conservation is enacted, QSEs should be notified via Hotline call (see EEA 2 for typical script). |
| TCEQ | It is ERCOTs responsibility (External Communications) to contact the Texas Commission on Environmental Quality (TCEQ) to notify them that ERCOT is in an emergency. This will be dependent on the situation and communications from QSEs regarding any emissions limitations they have in responding to our dispatch instructions. ERCOT will then communicate TCEQ’s response to our generic request to consider enforcement discretion to the QSEs. The QSEs will still have to contact TCEQ themselves to get the discretion for their particular unit(s). If a QSE needs contact information for the TCEQ, see the following link: - http://www.tceq.texas.gov/assets/public/response/power-emergency/enforcement-discretion.pdf |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Select the activate EEA flag in EMS, - Determine whether system conditions warrant the deployment of 30 MIN ERS. Refer to the ERS tab on the Real-Time Values Spreadsheet for amounts in each business hours and number of times deployed: - Consider the peak hour, deploy all 30 MIN ERS if needed to prevent PRC from falling < 1750 MW, - When deploying the 30 MIN ERS, also deploy the weather-sensitive ERS if available for the current business hour. - Using the Hotline, notify all QSEs to implement EEA 1. Typical Hotline Script when not deploying ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is declaring EEA 1, QSEs are to perform their necessary steps for EEA 1. Report to ERCOT any loss of generation or issues, and ERCOT is reminding you that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR Typical Hotline Script when deploying 30 MIN ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is declaring EEA 1, QSEs are to perform their necessary steps for EEA 1. ERCOT is directing QSEs to deploy all 30 MIN ERS Resources with an obligation in the current time period until further notice. Report to ERCOT any loss of generation or issues, and ERCOT is reminding you that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR if it is between HE 14:00 and HE 20:00 use this script Typical Hotline Script when deploying 30 MIN ERS including weather-sensitive ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is declaring EEA 1, QSEs are to perform their necessary steps for EEA 1. ERCOT is directing QSEs to deploy all 30 MIN ERS Resources with an obligation in the current time period until further notice this also includes all weather-sensitive ERS. Report to ERCOT any loss of generation or issues, and ERCOT is reminding you that you can schedule available interchange into ERCOT across the DC-Ties. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | IF: - Generation Resource (that are not bid in for Non-Spin) have a unit status of OFF and can be brought On-line within the timeframe of the emergency; THEN: - Issue a VDI to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) - Enter “capacity” in “other information” |
| 3 | IF: - A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: - Issue a VDI to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) - Enter “capacity” in “other information” |
| TCEQ | IF: - ERCOT has contacted TCEQ to make them aware of the emergency and determine if they would consider enforcement discretion requests; THEN: - Make Hotline call to QSEs with this information. Typical Hotline Script if TCEQ is accepting enforcement discretion requests: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; ERCOT had contacted the TCEQ to make them aware of the emergency. TCEQ is accepting enforcement discretion requests. You will need to contact them to receive discretion for your particular units. Any questions?”” Typical Hotline Script if TCEQ is NOT accepting enforcement discretion requests: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; ERCOT had contacted the TCEQ to make them aware of the emergency. TCEQ is not accepting enforcement discretion requests at this time. Any questions?” |
| 4 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 60 Hz; THEN: - Determine whether system conditions require the deployment of Load Resources and/or ERS Resources by considering the following: - Consider MW needed for peak hour, deploy 10 MIN ERS if needed to prevent an EEA 3 event, - Deploy Group 1 and/or 2 Load Resources as needed, - Deploy 30 MIN ERS if needed and not already done in EEA 1 - Using the Hotline, notify all QSEs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. |
| Load Resources | IF: - Deploying Load Resources, the Resource Operator must complete the XML deployment of the Load Resources before the Hotline call is made. - PRC < 1750 MW, deploy Group 1 - PRC < 1375 MW, deploy both Groups 1 and 2 simultaneously Typical Hotline Script for deploying LR Group One: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2 and has deployed Group 1 Load Resources. Implement all measures associated with EEA 1, if not already implemented. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline Script for deploying LR both Groups: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2 and has deployed all Load Resources. Implement all measures associated with EEA 1, if not already implemented. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ERS Resources | IF: - Deploying ERS, the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. - Deploy all ERS Resources as a single block. Typical Hotline Script for deploying 10 MIN ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2. ERCOT is directing QSEs to deploy all 10 MIN ERS Resources with an obligation in the current time period until further notice. Implement all measures associated with EEA 1 if not already implemented. [QSE] please repeat this back to me..” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR Typical Hotline Script for deploying 30 MIN ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2. ERCOT is directing QSEs to deploy all 30 MIN ERS Resources with an obligation in the current time period until further notice. Implement all measures associated with EEA 1 if not already implemented. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR if it is between HE 14:00 and 20:00 use this script: Typical Hotline Script for 30 MIN ERS including weather-sensitive ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is declaring EEA 2, ERCOT is directing QSEs to deploy all 30 MIN ERS Resources including weather-sensitive ERS with an obligation in the current time period until further notice. Implement all measures associated with EEA 1 if not already implemented. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR Typical Hotline Script for deploying 10 MIN and 30 MIN ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2. ERCOT is directing QSEs to deploy all 10 MIN and 30 MIN ERS Resources with an obligation in the current time period until further notice. Implement all measures associated with EEA 1 if not already implemented. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR if it is between HE 14:00 and 20:00 use this script: Typical Hotline Script for deploying 10 MIN and 30 MIN ERS including weather-sensitive ERS: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is declaring EEA 2, QSEs are to perform their necessary steps for EEA 1. ERCOT is directing QSEs to deploy all 10 MIN and 30 MIN ERS Resources including all weather-sensitive ERS with an obligation in the current time period until further notice. Implement all measures associated with EEA 1 if not already implemented [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| When ERS Business Hours Change | IF: - ERS Resources are deployed, and additional ERS Resources are needed and available due to business hour changes; the Resource Operator must complete the XML deployment of the ERS before the Hotline call is made. THEN: - Deploy the next business hour Typical Hotline for deploying 10 MIN ERS Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA 2. ERCOT is directing QSEs to deploy all [10 MIN or 30 MIN] ERS Resources with an obligation in the current time period until further notice. All previously deployed ERS Resources are to remain deployed consistent with their obligation until recalled. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical Hotline for deploying 30 MIN ERS Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA 2. ERCOT is directing QSEs to deploy all [10 MIN or 30 MIN] ERS Resources with an obligation in the current time period until further notice. All previously deployed ERS Resources are to remain deployed consistent with their obligation until recalled. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR if it is between 14:00 and 20:00 use this script Typical Hotline for deploying 30 MIN ERS including weather-sensitive Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA 2. ERCOT is directing QSEs to deploy all 30 MIN ERS Resources including weather-sensitive ERS with an obligation in the current time period until further notice. All previously deployed ERS Resources are to remain deployed consistent with their obligation until recalled. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR Typical Hotline for deploying 10 MIN and 30 MIN ERS Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA 2. ERCOT is directing QSEs to deploy all 10 MIN and 30 MIN ERS Resources with an obligation in the current time period until further notice. All previously deployed ERS Resources are to remain deployed consistent with their obligation until recalled. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. OR if it is between 14:00 and 20:00 use this script Typical Hotline for deploying 10 MIN and 30 MIN ERS including weather-sensitive Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is in EEA 2. ERCOT is directing QSEs to deploy all 10 MIN and 30 MIN ERS Resources including weather-sensitive ERS with an obligation in the current time period until further notice. All previously deployed ERS Resources are to remain deployed consistent with their obligation until recalled. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| NOTE | All Load Resources, 10 MIN ERS, 30 MIN ERS, and weather-sensitive ERS must be deployed before firm load. |
| Media Appeal | - Unless already in effect, verify with the Shift Supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify QSEs, via Hotline, that a media appeal for conservation is in effect. Typical Hotline Script: “This is ERCOT Operator [first and last name]; ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. |
| 2 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Using the Hotline, notify all QSEs to implement EEA 3 and any measures associated with EEA 1 and 2, if not already implemented. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3, [MW Amount] of firm load is being shed. Implement all measures associated with EEA 1 and 2, if not already implemented. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 5.4	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Restore Firm Load |  |
| RESERVES | If 1375 MW of PRC is not restored within 75 minutes, reduce MW loading on Resource(s) to bring reserves up, if available. |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - PRC ≥ 1375 MW; THEN: - Using the Hotline, notify all QSEs of firm load restoration. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is restoring firm load. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Move From EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exists to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load has been instructed to be restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 3 to EEA 2 - Coordinate with the Resource Desk and recall Load Resources Typical Hotline Script for Load Resource recall: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 3 to EEA 2. QSEs are to recall all Load Resources at this time. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |
| NOTE | Once Load Resources are recalled, they have 3 hours to return to service. |
| ### Move From EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Using the Hotline, notify all QSEs of the reduction from EEA 2 to EEA 1 - Coordinate with the Resource Desk and recall the 10 MIN and/or 30 MIN, including the weather-sensitive ERS Resources. Typical Hotline Script for ERS recall: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is moving from EEA 2 to EEA 1. QSE’s are to recall [10 MIN], [30 MIN], [30 MIN including weather-sensitive], [both 10 MIN and 30 MIN] or [both 10 MIN and 30 MIN including weather-sensitive] ERS Resources at this time. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | Once ERS Resources are recalled, they have 10 hours to return to service. |
| ### Move From EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Uncheck the EEA flag in EMS and make inactive, - Using the hotline, notify all QSEs of the termination of EEA. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is terminating EEA 1. A Watch still remains in effect. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Cancel Watch |  |
| 1 | WHEN: - PRC is ≥ 2800 MW, AND - Non-Spin has been recalled; THEN: - Cancel Watch Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. At this time, Resource testing may resume. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |

## 5.5	Restoration of Primary Control Center Functionality

Procedure Purpose: To be performed once the Real-Time Operator has arrived at ACC.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| ### Version: 1 | Revision: 3 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| Restoring Frequency Control | WHEN: - SCED is functional; THEN: - Remove the QSE that was directed on constant frequency by ending the VDI. - Put ERCOT AGC into “ON” mode. |
| Return to Normal QSE Notification | When ready to resume normal operations: - Check with RUC Operator on desk status to include in hotline call if appropriate - Place the following Hotline call to the QSEs: - Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is canceling the Emergency Notice and is resuming normal operations from the [alternate/primary] control center. [Select QSE], Please repeat that back for me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Make log entries as needed. |

## 6.1	Hurricane/Tropical Storm

Procedure Purpose: To ensure ERCOT is prepared for an approaching

Hurricane / Tropical Storm

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 3 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Hurricane / Tropical Storm notifications are called when there is a probability of landfall in the ERCOT Region. (http://www.nhc.noaa.gov) |
| OCN | When an approaching Hurricane / Tropical Storm is approximately 5 days away. Using the Hotline, issue an OCN to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [Tropical Storm/Hurricane] [Name] due to a probability of making landfall in the ERCOT Region. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the Storm. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Advisory | When an approaching Hurricane / Tropical Storm is approximately 3 days away. Using the Hotline, issue an Advisory to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is currently projected to impact the ERCOT Region. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. - Direct Plant Operators to prepare for projected severe weather conditions and review procedures for operating in the lead due to possible high voltage concerns - Notify ERCOT if relocating personnel to backup control centers ERCOT will continue to monitor the Storm [QSE] please repeat this back to me.”” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Watch | When approaching Hurricane / Tropical Storm is 1 day away. Using the Hotline, issue a Watch to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for [Tropical Storm/Hurricane] [Name] in the Gulf of Mexico which is projected to make landfall near [Place] at [time]. QSEs are instructed to: - Notify all Resources of conditions - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. - Make available, any Resources that can be returned to service and keep COPs and HSLs updated ERCOT will continue to monitor the Storm. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Emergency Notice | When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the ERCOT System. Using the Hotline, issue an Emergency Notice to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to [Tropical Storm/Hurricane Name] having an adverse impact on the ERCOT System [specify condition]. QSEs are instructed to: - Be prepared to reduce Generator output due to anticipated load loss and respond to voltage support issues as requested, - Keep COPs and HSLs current. ERCOT will continue to monitor [Tropical Storm/Hurricane Name]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

## 6.2	Extreme Cold Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for extreme cold weather operations.

| Protocol Reference | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1, R5 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 6 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Extreme cold weather notifications are called when the daily temperatures are forecasted to remain 32°F or below in the following weather zones: - North Central (NORTH_C) - South Central (SOUTH_C) - Coast (COAST) |
| OCN | When approaching extreme cold weather is up to 5 days away, using the Hotline issue an OCN to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for an extreme cold weather system approaching in the next 5 days with temperatures anticipated to remain 32°F or below in the three largest weather zones. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance or returning from outage early, - Review and implement weatherization and emergency operating procedures, including winterization procedures. Notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the extreme cold weather system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Advisory | When approaching extreme cold weather is 3 days away, using the Hotline issue an Advisory to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme cold weather system approaching in the next 3 days with temperatures anticipated to remain 32°F or below in the three largest weather zones. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance or returning from outage early, - Review and implement weatherization and emergency operating procedures, including winterization procedures. Notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the extreme cold weather system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Watch | When approaching extreme cold weather is 1 day away, using the Hotline issue a Watch to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme cold weather system approaching tomorrow. Temperatures are expected to remain 32°F or below in the three largest weather zones. QSEs are instructed to : - Make available, any Resources that can be returned to service and keep COPs and HSLs updated, - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Prepare for higher than usual loads and the possible need for additional Ancillary Services, - Review and implement weatherization and emergency operating procedures, including winterization procedures. Notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the extreme cold weather system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Emergency Notice | When extreme cold weather has arrived and is beginning to have an adverse impact on the ERCOT System, using the Hotline issue an Emergency Notice to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme cold weather system is beginning to have an adverse impact on the ERCOT System such as [state what the adverse impacts are]. QSEs are instructed to: - Make Resources available that can be returned to service and keep COPs and HSLs updated, - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the extreme cold weather system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

## 6.3	Extreme Hot Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for Extreme Hot weather operations.

| Protocol Reference | 6.3.2(3)(a)(i) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1, R5 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 5 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step |  | Action |
| --- | --- | --- |
| NOTE |  | Extreme Hot weather notifications are issued when: Temperatures are forecasted to be 103°F or above in the North Central and South Central weather zones. – OR – Temperatures are forecasted to be 94°F or above in the North Central and South Central weather zones during the following months (October – May). |
| OCN |  | When extreme hot weather is forecasted approximately 5 days away. using the Hotline issue an OCN to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance, - Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the weather system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Advisory |  | When extreme hot weather is forecasted approximately 1 to 3 days away, using the Hotline issue an Advisory to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance, - Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the weather system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Watch |  | When extreme hot weather is projected for next day or current day and ERCOT has reliability concerns, using the Hotline issue a Watch to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme hot weather with forecasted temperatures to be above [103°F or 94°F] in the North Central and South Central weather zones [today or tomorrow]. ERCOT is expecting statewide power supplies to be very tight. QSEs are instructed to: - Make available any Resources that can be returned to service and keep COPs and HSLs updated, - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review and implement weatherization and emergency operating procedures and notify ERCOT of any changes or conditions that could affect System Reliability. ERCOT will continue to monitor the weather and will convey information and directives as conditions warrant. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Emergency Notice |  | When extreme hot weather has arrived and is beginning to have an adverse impact on the ERCOT System, using the Hotline issue an Emergency Notice to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme hot weather system is beginning to have an adverse impact on the ERCOT System such as [state what the adverse impacts are]. - Make Resources available that are able to return to service and keep COPs and HSLs updated - Prepare for higher than usual loads and the possibility of deploying Load Resources and/or ERS Resources. ERCOT will continue to monitor the extreme hot weather system and will convey information and directives as conditions warrant. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |  |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |  |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |  |

## 6.4	Other Significant Weather Events

Procedure Purpose:  Monitor severe weather conditions which can arise with little or no warning that could possibly impact the ERCOT Grid.

| Protocol Reference | 6.5.9.3.1 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.2.1 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1, R5 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 5 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Significant weather events can consist of, but are not limited to the following: - Tornados - Strong straight line winds - Hail - Severe lightning - Flooding |
| OCN/ Advisory/ Watch | When a significant weather event that could or does impact the ERCOT Region, make the proper notification. Using the Hotline, issue a notification to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a [OCN/Advisory/Watch] due to [type of weather event] in the [location on the grid]. If you experience any issues as a direct result of the weather event, notify ERCOT. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all information in the Operator logs and notify the Shift Supervisor of any issues. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated Nerc Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Udated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.33.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |