- Power Operations Bulletin # 627

ERCOT has posted/revised the Resource Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.3	Notifications for Diminishing Reserves

Procedure Purpose:  Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 3.17.3(2) | 6.5.9.4.1 | 6.5.9.4(5) | 6.5.7.6.2.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.1(1) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-0 R2.4 | EOP-001-0 R3.1 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005-2 R1.4, R1.5, R4 |

| Version: 1 | Revision: 10 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at management’s discretion, may issue an appeal through the public news media for voluntary energy conservation at any time. - System conditions may dictate operating beyond the scope of this procedure. The System Operator has the authority to issue and/or keep a notification in effect as he/she deems necessary. |
| ### Advisory |  |
| Issue Advisory | IF: - PRC falls < 3000 MW; THEN: - Coordinate with the Real-Time Operator, AND - Post message on MIS Public Typical MIS Posting: “ERCOT is issuing an Advisory for Physical Responsive Capability less than 3000 MW.” |
| Cancel Advisory | WHEN: - PRC > 3000 MW; THEN: - Coordinate with Real-Time Operator, AND - Cancel message on MIS Public. |
| Log | Make log entry. |
| ### Watch |  |
| Issue Watch | IF: - PRC falls < 2500 MW; THEN: - Coordinate with the Real-Time Operator, AND - Post message on MIS Public Typical MIS Posting: “ERCOT is issuing a Watch for Physical Responsive Capability less than 2500 MW”. |
| Cancel Watch | WHEN: - PRC > 2800 MW; THEN: - Coordinate with Real-Time Operator, AND - Cancel message on MIS Public. |
| Log | Make log entry. |

## 3.5	System Failures

Procedure Purpose: To ensure Market Participants are notified via MIS Public using Notice Builder of any SCED/RLC/LFC (AGC) failures.

| Protocol Reference | 6.5.9.2 | 6.5.9.1(2) | 6.5.9.2(3) | 6.5.9.2(4) |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | WHEN: - Notified by the Real-Time Operator of a SCED/RLC/LFC(AGC) failure; THEN: - Post the following message on MIS Public Typical MIS posting: “ERCOT has issued an Emergency Notice due to the failure of [SCED/RLC Failure], and/or [LFC].” |
| 2 | WHEN: - Notified by the Real-Time Operator that SCED/RLC/LFC(AGC) has been restored; THEN: - Cancel message on MIS Public |
| Log | Make log entry of actions taken. |

## 5.1	Supplemental Ancillary Service Market

Procedure Purpose:  To “Open” and/or “Execute” a Supplemental Ancillary Service Market for A/S insufficiencies due to increased amounts above Day-Ahead requirement, infeasible (stranded) caused by congestion, or failure to provide by the QSE.

| Protocol Reference | 3.16 (4) | 5.2.2.2 | 6.4.8.1 | 6.4.8.1.1 |
| --- | --- | --- | --- | --- |
|  | 6.4.8.1.2 | 6.4.8.1.3 | 6.4.8.2 | 6.4.8.2.2 |
|  | 6.5.9(4) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - ERCOT may not buy more of one A/S in place of the quantity of a different service. - A QSE may not self-arrange for A/S procured in response to Emergency Conditions. - See Desktop Guide Common to Multiple Desks Section 2.15 if the savecase function fails when running a SASM |
| ### Procurement of Ancillary Services due to DAM Failure |  |
| Procurement Timeline | If the Day-Ahead Market fails to run for the next day, the ancillary services have to be procured through SASM. The SASM must be executed in the Adjustment Period for the next day (which starts at 1800). The SASM timeline is as follows Time X = Notify QSEs of time the SASM will begin Time X + 30min = Determine amount of A/S to be procured Time X + 35min = Execute SASM Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs forA/S Resource Responsibility |
| 1 | IF: - The Day-Ahead Market fails to run for the next day; THEN: - Verify that the RUC Operator has issued an Emergency Notice by making a Hotline call to the QSEs, - Procure adequate Ancillary Services for the next operating day through a SASM, (Refer to Desktop Guide Resource Desk Section 2.8.4) |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor about the remaining A/S insufficiencies. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| ### ERCOT Increases the Amount of Ancillary Services |  |
| A/S Plan Increase Timeline | If the AS plan is increased above that specified in the Day-Ahead, QSEs have 30 minutes (after notification by ERCOT) to Self-Arrange the additional AS Obligations. The timeline is as follows: Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - More Ancillary Services are needed for one or more Operating Hours than were provided in the Day-Ahead; THEN: - Issue a Watch by making a Hotline to QSEs - Post message on MIS Public - Notify Transmission Operator to make Hotline call to TOs - Procure more Ancillary Services through a SASM (Refer to Desktop Guide Resource Desk Section 2.8.3). Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services requirement above what was procured in the Day-Ahead Market due to [state the reason]. At [xx:xx] ERCOT will open a SASM to procure the additional Ancillary Services for hours [hours] for operating day [day]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor about the remaining A/S insufficiencies. |
| 3 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| 5 | ONCE: - Ancillary Service has been procured; THEN: - Cancel the Watch by making Hotline call to QSEs - Cancel MIS posting - Notify Transmission Operator to make Hotline call to TOs Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Watch for increasing the system wide A/S requirement. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| ### Replacement of Ancillary Service Due to Infeasibility/Failure to Provide |  |
| NOTE | - Undeliverable/Infeasibility is when a QSE can not provide their A/S because ERCOT has asked them to move it due to congestion - Failure to provide is all other reasons |
| Undeliverable /Insufficient A/S Timeline | If the SASM is being executed to replace A/S capacity, either due to transmission constraints or QSE failure-to-provide, the previous 30 minute window for QSE self-arrangement of A/S is not needed. ERCOT will proceed directly to the SASM execution and procure A/S from existing offers. The timeline is as follows: Time X = Determine type and amount of A/S to procure. Time X + 5min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 15min = Notify QSEs with awards Time X + 30min = Validate COPs and A/S schedules |
| NOTE | For A/S that is Infeasible, a QSE has two (2) hours to notify ERCOT: - It will be substituted on another Resource - They will replace the A/S through a trade with another QSE - All or Part of the A/S needs to be replaced For an A/S shortage that is due to Failure to Provide, a QSE must notify ERCOT within an acceptable timeframe, but no longer than two (2) hours: - It will be substituted on another Resource, - They will replace the A/S through a trade with another QSE - The A/S needs to be replaced |
| 1 | IF: - A QSE is unable to provide the A/S capacity allocated to a specific Resource; THEN: - Determine if the infeasible/insufficient amount is significant enough to replace through SASM IF: - It is determined that a SASM should be run; THEN: - Execute SASM (Refer to Desktop Guide Resource Desk Section 2.8.1 or 2.8.2). |
| 2 | IF: - SASM did not procure the amount of A/S requested; THEN: - Notify the Shift Supervisor of the remaining A/S insufficiencies. |
| 3 | IF: - A QSE is unable to provide their SASM awards; THEN: - Determine if there is time to open an additional SASM, AND - Send failure to provide notification. |
| 4 | Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE and Resource name (if known) you are replacing the AS for - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 5 | Send information in an email to the following distribution list: - SASM |
| ### Daily Reconfiguration SASM |  |
| Daily SASM Timeline | (Refer to Desktop Guide Resource Desk Section 2.8.7) Reconfiguration Supplemental Ancillary Service Market (SASM) allows QSEs to modify their Ancillary Services (AS) during the Operating Day. Reconfiguration SASMs are expected to be run daily for Operating Hours 13 thru 24. The timeline is as follows: Time 08:45 = Determine type and amount of A/S to procure. Time 09:00 = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time 09:15 = Notify QSEs with awards Time 09:30 = Validate COPs and A/S schedules |
| 1 | QSEs must have valid AS Offers of an amount equal to or greater than the requested reconfiguration amount; IF: - There are not sufficient AS Offers to cover the total requested amount; THEN: - Do not publish the SASM, - Post an Operational Information message, low priority, on MIS Public - Send email to SASM distribution list - QSEs will retain their original AS Supply Responsibility and should update their COPs accordingly Typical MIS Posting: The Daily Reconfiguration SASM will not be occurring due to insufficient AS Offers. |
| 2 | IF: - There are NO participating QSEs in the reconfiguration SASM process; THEN: - Do not proceed with SASM process - Post an Operational Information, low priority, message on MIS Public - Send email to SASM distribution list Typical MIS Posting: The Daily Reconfiguration SASM will not be occurring due to zero participating QSEs. |
| 3 | IF: - There ARE participating QSEs in the reconfiguration SASM THEN: - Proceed with the reconfiguration SASM - Prepare email with the following information: - SASM ID (use YYYYMMDDHHMMSS format) - Delivery Date - Delivery Hour - QSE - AS type(s) - MW amounts you are replacing - Total MW amount SASM has awarded - Verify PVT transferred |
| 4 | Send information in an email to the following distribution list: - SASM |
| LOG | Log all actions taken. |

## 5.2	SASM Failure/Timeline Deviation

Procedure Purpose:  To manage SASM software failure or timeline deviation.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Failure of the SASM Software |  |
| 1 | IF: - The SASM workflow controller fails during any stage of the run; THEN: - Press the Abort button to cancel the current run, - Press the Shut Down button, - Press the Start Up button, - Press the Run All button to restart the sequence. |
| 2 | IF: - The SASM workflow controller continues to fail; NOTIFY: - Notify the appropriate ERCOT personnel. |
| ### Timeline Deviations |  |
| NOTE | - There is no definitive time by which a SASM needs to start, however the SASM process must be completed at least 2 hours before the start of the Operating Hour (Example: for A/S needed in HE 14, SASM must be completed by HE 11). The SASM timeline depends on the triggering of the event. - SASM process from opening a SASM market to the COP update is approximately 1 hour for an A/S plan increase. For replacement due to undeliverable/insufficient A/S, the timeline is 30 minutes. |
| A/S Plan Increase Timeline | Time X = Notify QSEs and open SASM market Time X + 30min = Verify SASM market has closed Time X + 35min = Execute SASM (and Price Run/Sensitivity Analysis if needed) Time X + 45min = Notify QSEs with awards Time X + 60min = Validate COPs and A/S schedules |
| 1 | IF: - SASM Workflow Controller fails or needs to be restarted and cannot meet the timelines above; THEN: - Using the Hotline, notify the Market Participants that the SASM will be delayed. - Notify the Help Desk and appropriate support personnel. Typical Hotline Script: “This is ERCOT Operator [first and last name]. ERCOT is making notification that SASM has not met its timeline. ERCOT will manually commit A/S as needed. Any questions”? |

## 7.1	Market Notices

Procedure Purpose:  Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R4.1, R5 | IRO-005-2 R1.10 |  |

| Version: 1 | Revision: 11 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within first contingency criteria are not likely or possible because of Forced Outages or other conditions - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day - When extreme hot weather is projected for next day or current day - A transmission condition has been identified that requires emergency energy from any of the CFE DC-Ties - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system. - ERCOT varies from time-line for DAM/DRUC |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution and/or Emergency Base Points are issued - Loss of Primary Control Center functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market - ERCOT forecasts an inability to meet applicable reliability standards and it has exercised all other reasonable options - A transmission condition has been identified causing unreliable operation or overloaded elements - A Severe Single Contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists - ERCOT has determined a fuel shortage exists that would affect reliability - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED) - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact on the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Scripts |  |
| Hotline | Hotline calls are usually made by Real-Time Operator, the scripts below are for reference if needed: Notify QSEs of Notice: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [QSE] please repeat this back to me. That is correct, thank you.” Notify Transmission Operator to make Hotline call to TOs: Typical script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me. That is correct, thank you.” All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | - All notices must be posted on MIS Public - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0 R3.1, R3.3, R5 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-2 R1.5 |

| Version: 1 | Revision: 11 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA. When a media appeal for voluntary energy conservation is enacted QSEs should be notified via Hotline call (Real-time Operator has the responsibility). - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. - QSEs need to contact the Texas Commission on Environmental Quality (TCEQ) for enforcement discretion on air permitting requirements after ERCOT has made contact with TCEQ. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Deploy all available Non-Spin (if not previously deployed) (see Desktop Guide Resource Desk Section 2.2). - Determine whether system conditions require the deployment of the 30 MIN ERS (see Desktop Guide Resource Desk Section 2.9). - Make EEA 1 posting to MIS Public - Use preformatted notice “EEA Level 1” |
| 2 | IF: - Generation Resource (that are not bid in for Non-Spin) have a unit status of OFF and can be brought On-line within the timeframe of the emergency; THEN: - Issue a VDI to commit the Resource (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) IF: - ERS is deployed; THEN: - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 3 | IF: - A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: - Issue a VDI to commit the Resource (see Desktop Guide Common to Multiple Desks Section 2.3) - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) |
| 4 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 60.00Hz; THEN: - Determine whether system conditions require the deployment of Load Resources and/or ERS Resources by considering the following: - If at peak hour, will the 10 MIN ERS be sufficient and have they already been deployed in the current contract period - If not at peak hour, will half of Load Resources be sufficient, or the 30 MIN ERS - Deploy Load Resources and/or ERS; - Notify the Real-Time Operator when XML message has been completed. Load Resources/ERS must be deployed first before hotline call is made, - Desktop Guide Resource Desk (Section 2.1 for Load Resources; Section 2.9 for ERS). - Make EEA 2 posting to MIS Public - Use preformatted notice “EEA Level 2” IF: - Extending Current Deployments of Load Resources; THEN: - Deploy either “Group 1” or “BOTH” Load Resources (see Desktop Guide Resource Desk Section 2.1). |
| ERS Business Hour Changes | IF: - ERS Resources are deployed, and additional ERS Resources are needed and available due to business hour changes; THEN: - Deploy next business hour - Take into consideration the time requirement for the 10 MIN and 30 MIN ERS - Notify the Real-Time Operator when XML message has been completed. ERS must be deployed before hotline call is made. |
| 2 | IF: Went straight to EEA Level 2; THEN: - Ensure tasks in EEA Level 1 are complete. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Make EEA 3 posting to MIS Public - Use preformatted notice “EEA Level 3” |
| 2 | Verify and log that all measures have been implemented. |

## 7.3	Restore EEA Levels

Procedure Purpose:  To restore the ERCOT grid to normal state as system conditions warrant while recovering from an EEA event.

| Protocol Reference | 6.5.9.4.3 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3(8) |  |  |  |
| NERC Standard | EOP-001-0 R4.1, 4.2, R4.4 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| RESERVES | If 1375 MW of PRC is not restored within 75 minutes, reduce MW loading on Resource(s) to bring reserves up, if available. |
| ### Restore Firm Load |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC ≥ 1375 MW; THEN: - Transmission Operator will restore firm load. |
| ### Move from EEA Level 3 to EEA Level 2 |  |
| 1 | IF: - Sufficient Regulation Service exist to control to 60 Hz, AND - PRC is ≥ 1750 MW, AND - All firm load have been instructed to be restored; THEN: - When instructed by the Real-Time Operator to recall Load Resources - Send XML message to recall Load Resources, (see Desktop Guide Resource Desk Section 2.1) - Make EEA 3 to EEA 2 posting to MIS Public - Use preformatted notice |
| ### Move from EEA Level 2 to EEA Level 1 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All Load Resources have been instructed to be restored; THEN: - Send XML message to recall 10 MIN/30 MIN ERS (see Desktop Guide Resource Desk Section 2.9) - Make EEA 2 to EEA 1 posting to MIS Public - Use preformatted notice |
| ### Move from EEA Level 1 to EEA 0 |  |
| 1 | IF: - The system can maintain PRC ≥ 2300 MW, AND - All uncommitted units secured in EEA 1 can be released, AND - Emergency energy from the DC Ties is no longer needed; THEN: - Terminate EEA 1 by posting to MIS Public - Use preformatted notice “EEA 1 to Normal” |
| ### Recall Non-Spin and Cancel Watch |  |
| 1 | WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 2800 MW; THEN: - Coordinate with the Real Time Operator and recall half of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.2). WHEN: - Avail_CAP_30Min ≥ 1000, AND - PRC is ≥ 3000 MW; THEN: - Coordinate with the Real Time Operator and recall all of the Non-Spin by sending a Zero MW XML message (Refer to Desktop Guide Resource Desk Section 2.2). |

## 8.1	Weekly Hotline Test

Procedure Purpose: To perform a weekly communication test of the ERCOT Hotline phone system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 7.1.3(3) |  |  |  |
| NERC Standard | COM-001-1.1 R2 | EOP-005-1 R5 |  |  |

| Version: 1 | Revision: 5 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | In the event of a failure of the Forum Conference Client software, the most recent printout of the Hotline log may be used to perform a manual roll call of the QSEs. |
| NOTE | Insure all Invalid Hotlines “Lost Souls” are cleared prior to the hotline call. |
| NOTE | Confirm with Shift Supervisor the threat alert level, which can be viewed at the following links: http://www.esisac.com/SitePages/Home.aspx, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert level are listed in the Security Alert Plan. |
| 1 | Each Monday between 0630 and 1100 test the ERCOT Hotline and when working out of the Alternate Control Center during the monthly scheduled dates. |
| 2 | Using the Hotline, notify all QSEs/TOs of the purpose of the call. - When QSEs have answered the Hotline, print Hotline participants. Typical Hotline Script: “This is ERCOT Operator [first and last name]. ERCOT is conducting the weekly [QSE/TO] Hotline test. ERCOT is currently at threat alert level [state alert level]. The following notices are currently in effect: - List OCNs, Advisories, Watches and/or Emergency Notices in effect. - State “None” if none are in effect. This ends the test of the ERCOT Hotline. That is all.” |
| 3 | IF: - Not every QSE answered the Hotline; THEN: - Contact them using their OPX line or LD line to inquire why they were not on the Hotline Call; - Inquire why they were not on the Hotline call; - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| 4 | Place printout in the appropriate folder in the file in the back of the room. |
| LOG | Log all actions. |

## 9.1	Respond to Miscellaneous Issues

Procedure Purpose: To minimize telemetry issues that could have an impact on LMPs.

| Protocol Reference | 6.3.2(3) | 3.10.7.5 | 3.10.7.5.1 | 3.13.7.5.2 |
| --- | --- | --- | --- | --- |
|  | 6.5.7.1.5 | 6.5.7.1.13(4) |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: June 1, 2013 |
| --- | --- | --- |

| Step |  |  | Action |  |
| --- | --- | --- | --- | --- |
| ### Telemetry Issues that could affect SCED and/or LMPs |  |  |  |  |
| Notification of Telemetry Issue |  |  | IF: - There is a telemetry issue, THEN: - Ensure the appropriate Control Room personnel are aware of the issue, and - Instruct the QSE to correct the issue. |  |
| QSE Override |  |  | IF: - The QSE cannot fix the issue in a timely manner, THEN: - Ask the QSE to override the bad telemetry. |  |
| QSE unable to Override |  |  | IF: - For some reason, the QSE cannot override the bad telemetry, NOTIFY: - Shift Supervisor and Operations Support Engineer The Operations Support Engineer will work with the QSE and/or the ANA group to override the bad telemetry; however it may be necessary for the Real-Time operator to make manual adjustments in SCED until the issue is resolved. |  |
| ### Backup/Alternate Control Center Transfer |  |  |  |  |
| 1 |  |  | When notified by a QSE that they will be transferring to or from their backup/alternate control center, - Identify the [QSE] in the email notification - Send e-mail to “1 ERCOT System Operators” - Make log entry. |  |
| ### QSE Issues |  |  |  |  |
| 1 |  | If a QSE is not satisfied with ERCOT Operations responses to their issues, refer them to their Wholesale Client Representative for clarification/resolution. |  |  |
| 2 |  | If the System Operator believes the issue is with ERCOT systems applications (ICCP down, etc.), notify the ERCOT Help Desk. |  |  |
| 3 |  | If a QSE is having an issue with ERCOT system applications (unable to access the portal, outage scheduler, etc.), instruct them to call the ERCOT Help Desk. |  |  |
| 4 |  | As time permits, log and notify the Shift Supervisor of any actions taken and unresolved issues. |  |  |
| ### Missing Data from MIS Postings |  |  |  |  |
| 1 |  | IF: - A call is received about data missing or data being incorrect, THEN: - Transfer call to the Help Desk, and - Notify the Shift Supervisor and Operations Support Engineer. |  |  |
| Log |  | Log the information. |  |  |
| ### Courtesy Hotline calls for ERCOT Application Issues |  |  |  |  |
| 1 |  | WHEN: - Notified from IT support of application(s) issues that are causing Market Participants an inability to submit data to ERCOT; THEN: - Make a courtesy hotline to inform them. Typical Hotline script: “This is ERCOT Operator [first and last name]. This is a courtesy call to inform you that ERCOT is experiencing application problems which is causing QSEs issues with submittals. |  |  |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |  |  |  |
| 1 | WHEN: - Notified by a QSE of a change in status with any PSS or AVR; THEN: - Transfer call to the ERCOT Transmission Operator. |  |  |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outagesUpdated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |
| 3.1 7.2 | 1.0 / 8 1.0 / 9 | Updated step ONTEST Updated step 1 of Implement EEA Level 1 | August 29, 2012 |
| 2.2 7.2 8.1 | 1.0 / 1 1.0 / 10 1.0 / 4 | Added Hotline Call Communication Updated Implement EEA Level 1 step 2, Implement EEA Level 2 step 1 and ERS Business Hour Changes Updated 1st Note, step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.3 3.4 3.6 3.7 4.1 5.1 7.3 | 1.0 / 9 1.0 /12 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 11 1.0 / 9 | Non-Spin deployment messages are now automated Non-Spin deployment messeages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Updated steps 1 & 2 Updated steps Note, Procurement Timeline & 1. Added new procedure, Daily Reconfiguration SASM Updated step 1 of Cancel Watch | March 1, 2013 |
| 3.3 3.5 5.1 5.2 7.1 7.2 7.3 8.1 9.1 | 1.0 / 10 1.0 / 4 1.0 / 12 1.0 / 4 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 5 1.0 / 4 | Removed notice builder reference Removed notice builder refernece Updated steps 1 & 5 in ERCOT Increased the amount of A/S & steps in Daily Resonfiguration SASM Updated step 1 Updated Scripts Removed notice builder reference & Updated Scripts Removed notice builder reference Updated Script Updated Script | June 1, 2013 |