- Power Operations Bulletin # 635

ERCOT has posted/revised the Shift Supervisor Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Resource Testing and In-Service Approvals

Procedure Purpose: This procedure provides direction and guidelines for conducting various required testing and approval processes for resources and transmission elements. This procedure does not include testing for the Net Dependable Capacity (NDC) on wind generation.

| Protocol Reference | 3.3.1 | 8.1.1.2.1.1(4) | 8.5.1.1 | 8.5.1.2(1) |
| --- | --- | --- | --- | --- |
|  | 8.5.1.2(3) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 |  |  | Effective Date: July 15, 2013 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Step |  | Action |  |  |  |  |  |
| ### Unit Testing |  |  |  |  |  |  |  |
| NOTE |  | QSEs will submit test requests to shiftsupv@ercot.com. If e-mail is down, a fax will be accepted at (512) 248-6858. Test request forms are located on the ERCOT website under ‘Operating Procedures’. |  |  |  |  |  |
| 1 |  | As requests for unit tests are received, make every reasonable effort to accommodate testing. Reasons for not accommodating testing: - Unit has best shift factor to manage congestion for an outage. Without unit, contingency may reach max shadow price and become unsolvable, - The request exceeds 7 days, - A pattern of repeated requests for the same unit(s) indicate that abuse of the testing privilege may be taking place. If any request is refused for this reason, notify the Manager, System Operations and/or Control Room Operations Manager. |  |  |  |  |  |
| CAUTION |  | If deployment of the testing unit is necessary to maintain system security, direct the test be canceled and deploy as needed. |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT recognizes the need of <Company Name> to test its unit on <date and time>. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | IF the request cannot be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT cannot accommodate the request of <Company Name>for a unit test on <date and time> for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| ### Approved Resources to be ONTEST |  |  |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to be ONTEST. |  |  |  |  |  |
| ### Turbine Governor |  |  |  |  |  |  |  |
| 1 |  | - At all times an All-Inclusive Generation Resource is on-line, its turbine governor must remain in service and be allowed to respond to all changes in system frequency. - When the governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT. - An All-Inclusive Generation Resource may not reduce governor response during abnormal conditions without ERCOT’s consent unless equipment damage is imminent. - Each Generation Entity shall conduct applicable generating governor speed regulation tests on each of its Generation Resources. |  |  |  |  |  |
| ### In Service Approval (or Approval to Energize) |  |  |  |  |  |  |  |
| 1 |  | IF: - A Market Participant makes a request to energize new or relocated equipment; THEN: - Review notification provided by Operations Support Engineering, - Approve the request if notification has been provided; IF: - The equipment has not been approved by Operations Support Engineering, THEN: - Delay the request and notify Operations Support Engineer. |  |  |  |  |  |
| ### Ancillary Service Testing Coordination |  |  |  |  |  |  |  |
| 1 |  | Ancillary Service Qualification Testing will be done in coordination with Operations Analysis and EMMS Production Support. IF: - A QSE requests an Ancillary Service Qualification Test; VERIFY: - A Wholesale Account Manager is in the notification or Direct the QSE representative to notify their Wholesale Account Manager to start the process. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Operations Analysis and EMMS Production Support. When contacted by Operations Analysis: - Wholesale Account Manager will notify QSE of scheduled test, - Ensure reliable conditions exist at all times. |  |  |  |  |  |
| Log |  | Log all actions taken. |  |  |  |  |  |
| ### Coordinated Reactive Tests |  |  |  |  |  |  |  |
| 1 |  | Coordinate Reactive Tests will be done in coordination with Operations Analysis, the Transmission Operator (TO), and the Qualified Scheduling Entity (QSE). IF: - A QSE makes a request for a Coordinate Reactive Test; VERIFY: - Operations Analysis is aware so that coordination can occur with the TO. |  |  |  |  |  |
| NOTE |  | A minimum of 48 hours’ notice of the proposed test date is required. Requests shall be made between 0800 and 1700 on Business Days so that Operations Analysis is available for coordination to occur with ERCOT and the TO. ERCOT Operations and the TO confirms with the QSE the agreed upon test time and date or a rejection of the test time and date within 24 hours of the receipt of the request. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Operations Analysis and the Transmission Operator (TO). WHEN: - Notified by Operations Analysis; VERIFY: - TO and QSE are aware, - Ensure reliable conditions exist at all times. |  |  |  |  |  |
| Log |  | Log all actions taken. |  |  |  |  |  |

## 5.1	Providing Technical and Operational Support

Procedure Purpose: Technical and operational support duties for the Shift Supervisor

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-003-1 R3 |  |  |  |

| Version: 1 | Revision: 2 | Effective Date: July 15, 2013 |
| --- | --- | --- |

The Shift Supervisor is responsible for ensuring operations are in compliance with ERCOT Protocols, NERC Reliability Standards, Operating Guides, and Operating Procedures.  The Shift Supervisor must have a very good understanding of the ERCOT Protocols, Operating Guides, and NERC Reliability Standards.

The Shift Supervisor may consult with Operations Support, Operations Analysis, Market Operations, or any resource he deems necessary to resolve and clarify market related issues.  He/She will assist the System Operators in resolving market issues.

The Shift Supervisor, representing the RC function, has the authority to veto any planned outages to analysis tools, including final approval for planned maintenance such as database loads, site failovers, etc.  This authority to veto also applies to Market Participants planned outages of telemetering, control equipment, and associated communication channels when reliability of the grid is in jeopardy.

The Shift Supervisor also monitors and ensures that adequate coordination between the ERCOT Region, MISO, SPP and CFE is maintained.  To this effect the Shift Supervisor monitors the communications and coordination between the DC-Tie Operator, MISO, SPP and CFE.

The Shift Supervisor is responsible for running primary operations from the Alternate Control Center once per month.  This is to ensure all desks are functional in the case of an emergency.

The Shift Supervisor has the authority to coordinate additional support to assist during emergencies, system and weather related disturbances, and high demand periods as deemed necessary.  Support may be required from Operations Support, Operations Analysis, Market Operations, Outage Coordinators, and System Operators assigned to the Alternate Control Center.  The Shift Supervisor also has the authority to assign temporary duties to this additional support staff.

Finally, other Shift Supervisor duties may require the on-shift Shift Supervisor to leave the Control Center from time to time.  On these occasions, the Shift Supervisor may delegate his duties to another system operator on a temporary basis.  The Shift Supervisor shall remain in contact and accessible to the control center via available communication means.

## 5.2	Ancillary Service Requirements

Procedure Purpose:  To ensure A/S is posted by 0600.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 1 | Effective Date: March 1, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month are correct. This should be verified before the Day-ahead Operator posts the new requirements. |
| 1 | Market Participation>Physical Market>AS Market>AS Plan Ensure the Ancillary Service Requirement and Load Forecast is posted prior to 0600. |
| Last Day of Month | Before 04:00 on the last day of the month, ensure the A/S requirements for the next month have been updated into the AS Plan. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Regional Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R4.1, R5 | EOP-002-3.1 R3, R6.3, R7.2 | EOP-004-1 R1, R3.1 | IRO-014-1 R1.1.2 |
|  | IRO-015-1 R15 | TOP-002-2.1b R4 | DOE OE-417 |  |

| Version: 1 | Revision: 15 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template between 0300 – 0400 and again between 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - When Off-Line Non-Spin is deployed for capacity (provide times) - A special update is not needed; provide information next time report is updated. - Conditions change that required new notices to be issued or cancelled - OCN , Advisory, Watch, or Emergency Notice - Clarify whether Transmission Watch/Emergency is due to a planned or forced outage - Do NOT update report for DAM delays or tool outages. - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas restrictions, not expected to cause reliability issues - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Do Not use abbreviations, spell words out. Send updated report when conditions have returned to normal. |  |
| Weather Information | The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Physical Responsive Reserve ≤ 1750 MW and trending downward - Critical - Physical Responsive Reserve ≤ 1375 MW and trending downward Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - High - EEA Level 2 in effect - Physical Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.8 Hz - Critical - EEA Level 3 in effect |  |
| ### Texas RE Event Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations and/or Control Room Operations Manager - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis process, events include the following: Category 1 Events: - An unexpected outage, contrary to design, of three or more elements caused by a common disturbance. For example: - The loss of a combination of NERC-defined elements or facilities - The loss of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); combined cycle units count as one unit - Unplanned evacuation from a control center facility with BPS SCADA functionality for 30 minutes or more - Failure or misoperation of SPS/RAS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BPS emergency - Unintended BPS system separation that results in an island of 100 MW to 999 MW. Excludes BPS radial connection, and non-BPS (distribution) level islanding - The loss of generation of 1,000 MW – 1,399 MW Category 2 Events: - Complete loss of all BPS control center voice communication system for 30 minutes or more - Complete loss of SCADA, control or monitoring functionally for 30 minutes or more - Loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - Voltage excursions equal to or greater than 10% lasting more than 15 continuous minutes due to a BPS emergency Category 3 Events: - Loss of load or generation of 1,400 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Loss of load or generation from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Loss of generation of 10,000 MW or more - Loss of load of 10,000 MW or more |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations and/or Control Room Operations Manager when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". |  |
| OE-417 Reporting Events | DOE OE-417 initial reports are to be completed within 1 hour, forms can be downloaded at: ftp://ftp.eia.doe.gov/pub/electricity/eiafor417.doc. Electronic forms are preferred. OE-417 reports are required for the following events: - System-wide voltage reduction of 3 % or more - Public appeal to reduce the use of electricity for purposed of maintaining the continuity of the electric power system - Load shedding of 100 MW or more implemented under emergency operational policy - Uncontrolled loss of 300 MW or more of firm system loads form more than 15 minutes from a single incident - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Fuel supply emergencies that could impact system adequacy or reliability - Loss of electric service to more than 50,000 customers for 1 hour or more - Complete operation failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system |  |
| NERC IROL and Preliminary Disturbance Report EOP-004-1 | NERC Preliminary Disturbance reports are to be completed within 24 hours, forms can be downloaded at: http://www.nerc.com/page.php?cid=5¦66 NERC Disturbance reports are required for the following events: - Loss of bulk power transmission component that significantly affects the integrity of system operations, which resulted in actions such as: - Modification of operating procedures - Modification of equipment to prevent reoccurrence of event - Identification of valuable lessons learned - Identification of non-compliance with NERC standards or policies - Identification of a disturbance that is beyond recognized criteria (i.e. three-phase fault with breaker failure, etc) - Frequency or voltage going below the under-frequency or under-voltage load shed points - The occurrence of system separation or system islanding or both - Loss of generation of 1,000 MW or more - IROL violation - Any action taken by a GOP, TOP, BA, or LSE that results in: - Sustained voltage excursions equal to or greater than ±10 percent - Major damage to power system components - Failure, degradation, or misoperation of system protection, SPS, RAPs, or other operating system that do not require operator intervention, which did result in, or could have resulted in, a system disturbance. - Firm load shedding of 100 MW or more to maintain the continuity of the BES - Loss of firm load demands totaling more than 200 MW or 50 percent of the total customers for ≥ 15 minutes |  |
| 1 | When required to file a report (If Manager, System Operations and/or Control Room Operations Manager is unavailable): Forward the TO or QSE report or the Director of Cyber Security’s report to: - NERC (esisac@nerc.com), (404) 446-9780 - NERC 24-hour Emergency Hotline (404) 446-9780), NERC System Awareness (systemawareness@nerc.net), fax (404) 446-9770) - DOE (doehqeoc@oem.doe.gov, fax (202) 586-8485) - “NERC and DOE Disturbance Reporting” e-mail list. |  |
| ### RCIS Reporting |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| NOTE |  | NXT notification should be coordinated with the Shift Engineer. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - Enter temperatures from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations and/or Control Room Operations Manager. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | WHEN: - Alerts for GMDs are issued for K-7 or higher; THEN: - Instruct the Transmission Operator to make Hotline call to TOs, AND - Post message on MIS Public |  |
| 3 | WHEN: - The GMD alert has expired; THEN: - Instruct the Transmission Operator to make Hotline call to TOs, AND - Post message on MIS Public |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |
| ### Special Protection Systems (SPSs) |  |  |
|  | IF: - A Monthly SPSs report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Shift Supervisors |  |

## 10.2		EMMS and Interface System Failures

Procedure Purpose: Provide guidance to the Shift Supervisor for coordinating with the ERCOT IT Help Desk if critical functions or systems fail such that system operators and/or participants are precluded for performing and complying with their obligations and therefore jeopardizing the security of the system.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-001-1.1 R5 | EOP-008-0 R1.4 |  |  |

| Version: 1 | Revision: 6 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step |  | Action |  |
| --- | --- | --- | --- |
| 1 |  | If any Control Room computer systems (ICCP, Web Portal, MIS, or API) events, failures, or incidents that affect normal operations occur, - DETERMINE criticality and impact to the reliability to the grid, - CONTACT the ERCOT Help Desk immediately from the Supervisor Help Desk button on the Turret Phone or extension 6804. If necessary, contact the on-call IT person first then contact the Help Desk. |  |
| NOTE |  | For a complete EMMS failure, see Real-Time Procedure Section 3.1 Frequency Control Operating Procedure and 3.3 System Failures. |  |
| 2 |  | IF: - Any of the aforementioned systems fail and are effecting ERCOT systems or multiple Market Participants and will be unavailable for longer than 15 minutes; THEN: - Notify market participants of the problem and expected duration via Hotline, - Request additional assistance from other support staff. |  |
| 3 |  | When the problem is resolved, Notify all participants via Hotline of the problem resolution. |  |
| Log |  | Log the following: - Date - Time of event - Description of system alarms, events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| ## Data and/or Voice Communication Failures |  |  |  |
| 1 |  | Notify the Help Desk of the loss and REQUEST assistance to re-establish voice and/or data communications. - Telecommunications group will be responsible for voice communications. - EMMS Production group will be responsible for data communications |  |
| 2 |  | Use back-up communications if needed such as the Control Room cell phone, Standalone Satellite phone or the PBX Bypass phones to maintain communications with the other control room, TOs, QSEs, SPP and any other entities as needed. The list of phone numbers is located in the Phone Book at Shift Supervisor’s Desk and also programmed into the cell phone. |  |
| 3 |  | IF the criticality and impact of events or failures is such that Market Participants are, or will be affected before the problem can be resolved, THEN: - Instruct ERCOT System Operator to NOTIFY the other ERCOT Control Room and all market participants via Hotline of the problem and expected duration. If Hotline is unavailable utilize any of the following methods: - Control Room cell phone, PBX Bypass phones, or Standalone Satellite phone. - REQUEST additional assistance from other support staff, as needed. |  |
| NOTE |  | Steps 4 & 5 may be performed in any order. |  |
| 4 |  | RECORD the following in the shift log: - Date - Time of event - Description of events, failures, or incident - Actions taken and resolution - Time of system or function restoration |  |
| 5 |  | When the problem is resolved, NOTIFY all participants via Hotline of the problem resolution. |  |
| ## Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms |  |  |  |
| NOTE |  | - Normal status for the Dynamic Rating, SCED Status, EMBP, SE, RTCA and RLC Status is indicated by each status box constant green on the “ERCOT & QSE Summary Page” in the PI system. - Failure of the PI server is indicated by abnormal status of Dynamic Rating, SE and RLC, accompanied by the PI system “flat-lining” - Dynamic Rating, SE and RLC status boxes flashing red AND PI flat-lining may indicate failure of the EMS. |  |
| Monitor |  | PERFORM the following as applicable to the indicated conditions: - IF only the Dynamic Ratings status box is flashing red, CONTACT the ERCOT Help Desk - TELL them the Dynamic Rating Alarm status in Processbook is flashing red and the dynamic ratings are not being sent to the SCADA in the EMS. - REQUEST they notify the on-call EMMS Production person of the situation. - IF only the RLC status box is flashing yellow/red, CONTACT the ERCOT Help Desk - TELL them the RLC Alarm status in Processbook is not green - Greater than 5 minutes but less than 10 minutes turns - Yellow - Greater than 10 minutes turns - Red - DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the SCED Status box is flashing red, - Follow the Managing SCED Failures in the Real Time Desk Procedure. - If SCED failure can’t be resolved CONTACT the ERCOT Help Desk and DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the EMBP box is flashing red, - Determine the reason Emergency Base Point are being issued, - Remove the Emergency Base Point flag when condition allow, - If EMBP can’t be resolved CONTACT the ERCOT Help Desk and DIRECT them to notify the on-call EMMS Production person of the situation. - IF only the SE status box is flashing red, CONTACT the Operations Support Engineer - TELL them the SE Alarm status in Processbook is flashing red - IF only the RTCA status box is flashing yellow or red, CONTACT the Operations Support Engineer - RTCA executes every 5 minutes, if RTCA doesn’t complete within the desired threshold the display changes colors - Greater than 7 minutes but less than 10 minutes turns - Yellow - Greater than 10 minutes turns - Red - TELL them the RTCA Alarm status in Processbook is flashing yellow/red - Greater than 15 minutes, inform QSEs for STP and CPSES. |  |
| ## Building Security and Fire Alarms |  |  |  |
| NOTE | The Shift Supervisor or designee will ensure staff members adhere to emergency evacuation procedures and evacuate all team members from the Control Room if an emergency evacuation is required. |  |  |
| 1 | IF: - Building security or fire alarm sounds, THEN: - Contact Security’s Emergency Number if Security has not already made communications with the Control Room. |  |  |
| 2 | IF: - It is determined it is a drill, THEN: - Retrieve the ‘orange’ bag for the employee roster, - Account for each operator by marking them present and return form to Security staff at front desk (if able). IF: - If unable to return roster in a reasonable timeframe, CONTACT: - Security and request them to retrieve roster during the next patrol. |  |  |
| 3 | IF: - Control Room personnel are in danger or ordered to be evacuated, THEN: - Transfer control of the Grid to the Alternate Control Center (see “Loss of Primary Control Center Functionality” procedure Section 4.6 in the DC Tie Desk Procedure), - Request additional assistance from other support staff, - Evacuate the Control Room to a safe area for Zone #1, - Retrieve the ‘orange’ bag for the employee roster, - Account for each employee by marking them present at the rally point. |  |  |
| 4 | Notify the Manager, System Operations and/or Control Room Operations Manager as soon as practical. |  |  |
| ## Failure of the Emergency Generator |  |  |  |
| 1 | If the Facilities emergency generator fails to start, you will be notified by the Facilities Staff. |  |  |
| 2 | If the Facilities Staff or the Shift Supervisor determines that it will be more than 20 minutes before the emergency generator can be started, the Shift Supervisor may consider initiating the “Loss of Primary Control Center Functionality” procedure. |  |  |
| 3 | The Shift Supervisor or his/her delegated representative should notify the Manager, System Operations and/or Control Room Operations Manager that the controls have been transferred to the other control center. |  |  |
| 4 | REQUEST additional assistance from other support staff as needed. |  |  |
| NOTE | See Desktop Guide Shift Supervisor Section 2.1. |  |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |