- Power Operations Bulletin # 636

ERCOT has posted/revised the Transmission and Security Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.3	System Updates

Procedure Purpose: To provide notice to the Market Participants when ERCOT is performing updates to their Energy and Market Management Systems.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| EMS Changes | Approximately 5 - 30 minutes before a database load, local failover, or EMS migration, make the following Hotline call to TOs: Typical Hotline Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a [database load] [local failover] [migration] on its Energy & [Market] Management Systems. In the event ICCP is temporarily suspended, all systems should re-establish automatically within a few minutes. Any questions?” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| MMS Changes | Approximately 5 - 30 minutes before a MMS migration, make the following Hotline call to TOs: Typical Hotline Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a [migration] on its Market Management System. We do not except to miss a SCED run. Any questions?” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Site Failover | Approximately 5 - 30 minutes before site failover, make the following Hotline call to TOs: Typical Hotline Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT will perform a site failover of its Energy & Market Management Systems. During this time, market communications will be unavailable for about 30 minutes, and real-time communications will be unavailable for about 5 minutes. All systems should re-establish communications automatically. Any questions?” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Database Load With W-N | IF: - The West – North is > 70% and is expected to increase; THEN: - Activate the W-N before the database load. |
| Site Failover With W-N | IF: - The West – North is > 70% and is expected to increase; THEN: - Activate the W-N before the site failover. |
| Site Failover Complete | Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], the site failover is complete. Thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 | 5.5.1(5) | 5.5.2 | 6.3.2(2)&(3)(a) |
| --- | --- | --- | --- | --- |
|  | 6.4.6.1 | 6.5.1.1 | 6.5.2 | 6.5.5.2(1) |
|  | 6.5.3 | 6.5.7.1.10 | 6.5.7.1.11 | 6.5.7.1.13(3) |
|  | 6.5.7.8 | 6.5.7.8(1) | 6.5.9.1(1)(d) | 6.5.9 (2) |
|  | 6.5.9.2(3)(a) | 7.1 |  |  |
| Guide Reference | 2.2.2 |  |  |  |
| NERC Standard | IRO-003-2 R1 | IRO-005-3a R1.2, R1.3, R1.7, R3, R5, R13, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-002-2 R6, R8 |
|  | IRO-004-2 R3 | TOP-001-1a R1, R2, R5 | TOP-002-2.1b R6, R8, R10 | TOP-004-2 R1, R6, R6.6 |
|  | TOP-006-2 R5 | TOP-008-1 R1, R2, R4 | EOP-003-1 R6 |  |

| Version: 1 | Revision: 22 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |
| Unknown State | When in an unknown operating state (any state for which valid operating limits have not been determined), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is in an unreliable state (see Section 4.2 if a DC-Tie has a shift factor) THEN: - Issue a Watch - See Generic Script in Section 7.1 - Notify Real-Time operator to make hotline call to QSEs. |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) - Unit specific dispatch instructions (Override HDL/LDL or VDI) - Non-Spin may be used as necessary. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP , - A hardcopy of the SPSs are maintained in the control room by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |
| Phase Shifters | Phase shifters can be used to help with congestion management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – Mitigate local congestion and increase W/N transfers - Big Lake – Mitigate local congestion and increase W/N transfers - Firerock ETT – Mitigate local congestion and increase W/N transfers - Nelson Sharp – Valley import during outages and flow in/out of Corpus Christi - Hamilton Road – Control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – Control Laredo import issues during outages - Thomaston – Control flow into Cuero, Yoakum and Victoria Areas Refer to OpsMon Display 08 HRUC Phase Shifter Position and they are also with the shift factors in the EMS. |
| Constraint Shift Factor Cut Off | Basecase and post-contingency constraints which do not have generator shift factors for units greater than or equal to 2% as indicated in EMS are not activated in SCED. See Section 4.5 Mitigation Plan for additional details. |
| ### Review Planned Outage Notes |  |
| 1 | Review daily outage notes: IF: - Outage notes recommend slower moving Resources to be lowered to maintain system security; THEN: - Take a real-time snap shot to determine where Resource(s) are needed before outage is taken - Use the manual override to step down Resource(s) - Once Resource(s) are down to where snap shot showed, - Give approval for switching, - Release manual overrides, and - Activate SCED constraint (when necessary). - Post message on MIS Public Typical MIS Posting Script: ERCOT is taking manual actions due to XXXX outage. |
| 2 | IF: - An outage requires a Resource to be On-line to solve a voltage issue and having the Resource On-line causes a post-contingency overload; THEN: - Manually override the Resources to its LSL - Notify QSE of action - Post message on MIS Public Typical MIS Posting Script: ERCOT is taking manual actions due to XXXX outage. |
| Log | Log actions taken. |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |
| 1 | IF: - A major topology change has occurred; THEN: - Re-run RTCA and VSAT/TSAT. |
| Log | Log actions taken. |
| ### Post-Contingency Overloads |  |
| 1 | WHEN: - Post-contingency overloads are approaching 98% of the Emergency Rating; THEN: - Determine if the SCADA is of similar magnitude to the pre-contingency value. - Example: Review the MW and MVAR flows |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate. - Make log entry. |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP exist - Verify that a PST cannot be used to resolve congestion |
| 4 | IF: - Post-contingency loading is 98% or greater, and generator shift factors for units with at least a 2% shift factor as indicated in EMS exist; THEN: - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint if needed (minimum of 95%, excluding W-N), - If experiencing oscillation issues, notify the Operations Support Engineer to investigate - If constraint needs to be controlled before the next SCED run: - Manually run RTCA after activating the constraint, - Manually execute the SCED process - Refer to “Managing Binding and Exceeded Constraints”. |
| 5 | IF: - Constraints with pre-contingency or post-contingency flows which exceed the rating of the overloaded Transmission Element are not activated in SCED; THEN: - Acknowledge the constraint and list a reason using the drop down box - The comment field can be used for additional information |
| 6 | A list of Qualifying Facilities can be found in Desktop Guide Common to Multiple Desk section 2.19 IF: - A Qualifying Facility (QF) is needed to operate below its LSL, or be ordered off-line to solve congestion; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [TO] please repeat this back to me. If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| 7 | IF: - Post-contingency overloads of 98% or greater of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 98% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”. |
| 8 | IF: - Congestion can not be fully resolved and does not have a MP or TOAP; THEN: - REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.5 Mitigation Plan). |
| 9 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. IF: - A transmission condition has been identified causing unreliable operation or overloaded elements, AND firm load is shed, THEN: - Issue an Emergency Notice - See Generic Scripts in Section 7.1 - Notify Real-Time operator to make hotline call to QSEs. |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A QSGR is needed for voltage support or an unsolved contingency; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running, - Notify QSE as time permits - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard WGRs unless transmission constraint is active. |
| Log | Log actions taken. |
| ### Post-Contingency Overloads on Private Use Networks (PUNs) |  |
| 1 | IF: - Post-contingency overloads greater than 98% of the Emergency Rating exist; THEN: - Contact the PUNs QSE to determine if the post-contingency is real (review MW, MVAR flows and facility ratings), - If real, give the QSE the opportunity to correct or have a plan to mitigate if the contingency were to occur.. |
| 2 | IF: - It is determined that the PUN has no way to mitigate or correct THEN: - Direct the QSE to take action such as lower/raise generation or load (directs only, do not override HDL/LDL or activate constraint in SCED). |
| 3 | - Acknowledge the post-contingency overload in TCM - Make log entry of actions taken |
| ### Managing Constraints in SCED |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. The Operator must keep track of non-binding constraints that have flows approaching their limits and must be prepared to take action if the constraint is exceeded. |
| Output Displays | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary - Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows on the following displays. |
| In Series | It is common for series elements to have nearly identical shift factors for a given contingency. If post-contingency loading of 98% or greater occurs for multiple elements which have been identified as being in series with each other, only the most limiting constraints should be activated to mitigate all the series element congestion. Example: Contingency A overloads X, Contingency A overloads Y |
| Same Element | If post-contingency loading of 98% or greater occurs on the same element for multiple contingencies and they have nearly identical shift factors, only one of the most limiting constraints should be activated to mitigate the congestion. Example: Contingency A overloads X, Contingency B overloads X |
| 1 | Verify that the SCED executions are reducing the flows on each constraint that is binding. |
| 2 | If a constraint is violated in SCED, which is when it has reached its max shadow price, review the following bullets to determine the next action: - Confirm that pre-determined relevant RAPs are properly modeled in the EMS, - Ensure curtailed units are following base points (RLC Output Data display), - Verify that units with large shift factors (SF button on EMS/TCM display) do not have a status of ONTEST (RLC Output Data display), - Redistribute A/S to increase capacity available to SCED (see separate procedure below), - Determine if a unit carrying Off-line Non-Spin is needed to solve congestion, - Ask Resource Operator to deploy Non-Spin for the specific unit - The telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Determine if additional units need to be committed/decommitted, - Determine if there is a non-cascading conflicting constraint that is preventing the constraint to solve, - Override Resource that is in conflict to optimal output for both constraints - Release the constraint that prevents resolving the more severe post-contingency overload, - Create a “suggestion plan” for the constraint if can’t determine course of action from shift factors |
| 3 | At times, it may be necessary to manually override HDL/LDL, these reasons could include the following: - Manually dispatching slower moving Resources before an outage to better manage congestion caused by the outage - Conflicting constraints - Unsolved contingencies IF: - An override is necessary; THEN: - Notify QSE of override - Consider doing the override in steps as to not exceed ramp rate - Post message on MIS under Operational Information Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. NOTE: - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - DO NOT override a Resource ONRR |
| 4 | IF: - All applicable steps above have been completed, AND constraint is still exceeded in SCED (max shadow price); THEN: - Instruct Operations Support Engineer to develop a mitigation plan, AND - Contact Manager, System Operations and/or Control Room Operations Manager to investigate further |
| NOTE | EMP Applications>TCM-Transmission Constraint Manager>Related Displays>Message Log for CAM IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk to issue a ticket to EMMS Production to fix immediately. |
| Log | Log all action taken including the following: - Reason for doing a manual override - Any security violations that were ≥ 125% of the Emergency Rating |
| ### Redistribute A/S to Increase Capacity available to SCED |  |
| 1 | RLC Unit Input Data display IF: - A/S needs to be removed from a specific unit in order to increase capacity to SCED; THEN: - Determine which A/S to remove - Instruct the QSE to remove the A/S by updating their telemetry to free that capacity to SCED - Notify Resource Operator with undeliverable A/S type, amount and approximate hours. |
| LOG | Log all actions taken |
| ### Unsolved Contingencies |  |
| 1 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Operations Support Engineer to investigate |
| LOG | Log all action taken including the following: - Reason for unsolved contingency - Actions taken to resolve |
| ### Model Inconsistencies/Updates |  |
| 1 | IF: - Any inconsistencies in ratings, impedance changes, etc. are found; THEN: - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required, correct it through the NOMCR process. |
| 2 | IF: - There is a difference in line ratings between ERCOT and a TO; THEN: - The most limiting rating will be used until the correct rating can be determined - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required correct it through the NOMCR process. |
| LOG | Log all actions taken |
| ### QSE Requests to Decommit a Resource |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |

## 4.2	Transmission Issues in the Areas of the DC-Ties

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4 (8) | 4.4.4 | 6.5.1.1 | 6.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.5.2(1) | 6.5.7.1.10 | 6.5.7.1.11(1) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R1, R4.2 | IRO-002-2 R6 | IRO-003-2 R1 | IRO-004-2 R3 |
|  | IRO-005-3.1a R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 |  |  |

| Version: 1 | Revision: 89 | Effective Date: June July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Transmission Issues within ERCOT |  |
| NOTE | ERCOT is considered to be in an unreliable condition whenever ERCOT Transmission Grid status is such that the most severe single-contingency event presents the threat of uncontrolled separation or cascading Outages and/or large-scale service disruption to Load (other than Load being served from a radial transmission line) and/or overload of a critical Transmission Element, and no timely solution is obtainable through market processes. |
| NOTE | DC Tie Load shall neither be curtailed during the Adjustment Period, nor for more than one hour at a time, except for the purpose of maintaining reliability. |
| 1 | IF: - A Ppost-contingency overloads exists with shift factors for a DC-Tie export (load), voltage issues or unsolved contingencies cannot be corrected with congestion management techniques or committing additional Resources; THEN: - Activate the constraint if a 2% or more shift factor exists. IF: - Shift Factors exists for a DC-Tie export (load) only or if activating the constraint does not fully resolve the congestion; THEN: - Ensure appropriate Resources have been committed, - Ensure a Mitigation Plan exist for contingency and review with AEP TO, - If no Mitigation Plan exists, notify Operations Engineer to create one. Determine if there are export schedules over the CFE Ties that would help alleviate the situation if curtailed (which includes reductions). - Notify the ERCOT DC Tie Operator to curtail the schedule(s), specifying the time and MW amount. |
| 2 | IF: - The Transmission ERCOTSystem is in an unreliable condition without a generation solution which includes one of the following: - Unsolved contingency - A post-contingency overload of a 345kV to the Valley overloads a 345kV - A post-contingency overload above 125% - Voltage issues; THEN: - Have ERCOT DC-Tie Operator adjust DC-Tie export (load) as needed - Issue an Transmission WatchEmergency Notice - Make Hotline call to TOs - Posting message on MIS Public - Notify Real-Time Desk to make Hotline call to QSEs Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency NoticeTransmission Watch due to the post contingency loss of (name of contingency) overloads (name of overloaded element) resulting in curtailment(s) over the [name] DC-Tie.” [TO] please repeat this back to me. If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. Typical MIS Posting Script: Emergency Notice has been issued due to Export schedule(s) to CFE on DC-Tie [Tie name(s)] was curtailed due to the post contingency loss of (name of contingency) overloads (name of overloaded element) which resulted in an export schedule curtailment on the [Tie name] DC-Tie. Edit script as needed to fit situation. |
| 3 | WHEN: - Committing a Resource by electronic VDI; THEN: - Issue a VDI to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct VDI. |
| LOG | Log all actions taken. |
| ### Transmission/Capacity Issues within the CFE Area |  |
| 1 | IF: - Notified by AEP TO that CFE is unable to maintain reliability and needs to curtail an E-Tag; THEN: - Verify the MW amount, tie and time of the curtailment, - Notify ERCOT DC-Tie operator with information. |
| 2 | IF: - Notified by AEP TO that CFE is requesting emergency energy; THEN: - Determine which DC-Tie(s) and amount being requested, - Determine or have Operations Support Engineer determine that sending emergency energy to CFE would not put ERCOT in an emergency condition IF: - ERCOT is able to send CFE emergency energy; THEN: - Notify ERCOT DC Tie Operator with information and request they issue a VDI to AEP TENASKA QSE (QAEPS2). |
| 3 | WHEN: - Notified by AEP TO that CFE no longer is in need of emergency energy; THEN: - Notify the ERCOT DC Tie Operator with information. |
| LOG | Log all actions taken. |

## 4.3	Closely Monitored SOLs

Procedure Purpose: To identify SOLs that should be closely monitored.

| Protocol Reference | 6.5.7.1.10 (3) | 6.5.9(1) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | FAC-011-2 R1, R3 | IRO-002-2 R6, R8 | IRO-003-2 R1 | IRO-005-3a R1.2, R1.3, R1.7, R3, R5, R9, R16, R17 |
|  | IRO-009-1 R4 | TOP-002-2.1b R10 | TOP-004-2 R1, R6, R6.6 |  |

| Version: 1 | Revision: 8 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| NOTE | If the State Estimator (SE) results indicate and/or RTCA predicts any of the below conditions on the 138kV or 345kV system and no SPS (identified as RAS in EMS), RAP, PCAP, TOAP, or MP exists; notify Operations Support Engineer: - Post contingent rating exceedance in excess of 125% of the SOL of the monitored facility (2-hour or Emergency Rating) - Basecase exceedance exist in the SE greater than 100% of the SOL of the monitored facility (Continuous or Normal Rating) - An unsolved or divergent contingency is present - Under-voltage condition characterized by bus voltages of less than 90% across three or more related BES facilities - Over-voltage condition greater than 110% across three or more BES facilities |
| 1 | IF: - SCED is unable to resolve congestion and leading into an emergency condition; THEN: - Confirm all bullets in step 2 and 3 of Managing Constraints in SCED procedure have been reviewed/completed, - Contact Operations Support Engineer to develop a Mitigation Plan |
| 2 | IF: - Mitigation Plan is not available in 30 minutes; THEN: - Issue a Transmission Watch until Mitigation Plan is received, - Make a Hotline call to TOs - Post a Watch message on MIS Public. - Notify Real-Time operator to make hotline call - Notify Operations Support Engineer to develop a Mitigation Plan if not already done. Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission Watch due to the post-contingency overload of [constraint name] while a [mitigation plan/temporary outage action plan] is being developed. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting Script: “ERCOT issued a Transmission Watch for the contingency loss of [constraint name] overloads [overloaded element].” |
| 3 | If Operations Support Engineer determines this to be an IROL after conducting offline studies. They will provide an IROL Tv (minutes). |
| 4 | The IROL exceedance must be relieved without delay and within the IROL Tv (minutes) by taking action or directing other entities to take actions. |
| 5 | If Operations Support Engineer determines this to NOT an IROL after conducting offline studies, then continue taking actions to manage congestion until a Mitigation Plan can be completed or the SOL exceedance is returned to within the limit. |
| 6 | Make log entry: - Facility Rating violation being treated as a closely monitored SOL, - All actions implemented |

## 4.4	West-North Stability Limit

Procedure Purpose: Maintain Transmission stability between the West and North.

| Protocol Reference | 3.10.7.6(3) | 6.5.9.1(1)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Refernce |  |  |  |  |
| NERC Standard | IRO-002-2 R6, R8 | IRO-003-2 R1 | IRO-004-2 R3 | IRO-005-3a R1.2, R1.3, R1.7, R3, R5, R16, R17 |
|  | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-008-1 R2 | IRO-009-1 R4 | TOP-002-2.1b R10 |
|  | TOP-004-2 R1, R2, R6, R6.6 | TOP-006-2 R5 | TOP-007-0 R3, R4 | TOP-008-1 R1 |

| Version: 1 | Revision: 13 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The West – North dynamic stability limit is an IROL; the actual flow should not be allowed to exceed the limit, and MUST NOT exceed the limit for more than 30 minutes. |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| 1 | WHEN: - The West-North limit displayed on the W-N Stability spreadsheet changes value; THEN: - Update limit on RTMONI to give information to TOs. |
| AVR/PSS | WHEN: - AVR or PSS status changes are reported concerning West area generation; THEN: - Notify the Operations Support Engineer to make the changes in TSAT, AND - Follow process in Section 6.1 PSS and AVR of this manual. |
| 2 | IF: - The monitored flow on the Stability-WN monitor is approaching 85%; THEN: - Activate the West-North constraint, - Post message on MIS Public Typical MIS Posting Script: “ERCOT is constraining for the West-North stability limit.” |
| 3 | Once wind output is controlled, ease constraint up to allow maximum output. IF: - West – North approaches 100%; THEN: - Continue to tighten constraint, - Call QSEs beginning with those which have the largest WGR base point deviations and verbally dispatch as appropriate |
| 4 | IF: - West – North exceeds 100%; THEN: - Instruct QSEs, beginning with those which continue to have the largest WGR base point deviation, to zero immediately (violate ramp rate), as long as exceedance exists - Issue electronic VDI as time permits, - Notify the control room staff. Typical Script to appropriate QSE: “This is ERCOT operator [first and last name]. The West to North flow is exceeding the stability limit; At [xx:xx] ERCOT is directing you to take [unit name] to zero effective immediately, which means you may violate your ramp rate. I will be sending you an electronic VDI shortly. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 5 | IF: - West – North has been exceeded for 15 minutes; THEN: - Issue directive to TO(s) to open WGR breaker, beginning with those which have the largest WGR base point deviation (refer to Real-Time spreadsheet tab “West Wind”), - Issue electronic VDI as time permits, - Notify the control room staff. |
| GTL | If an unexpected change to system conditions occur that result in a significant limit change from the day-ahead GTL posting: - Declare a Watch by posting on MIS - Make Hotline call to TOs - Notify Real-Time operator to make hotline call - Notify Operations Support Engineer to post new GTL Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch because the posted West-North Generic Transmission Limit has been updated on the MIS due to an unexpected changed on the system. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting Script: “A Watch has been issued due to ERCOT updating the posted West-North GTL on the MIS due to an unexpected change on the system.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Log | Log all actions taken. |
| ### Managing W-N during System Failures |  |
| 1 | IF: - The W-N constraint was active during the system failure THEN: - The Real-Time Operator will instruct the QSEs whose WGRs were being curtailed, to stay curtailed at their current output. |
| 2 | IF: - The W-N constraint was not active OR - W-N needs to be constrained further during the system failure THEN: - Issue unit specific verbal directives to QSEs with WGRs. |
| 3 | WHEN: - System is functioning; THEN: - Activate or tighten W-N constraint - Issue electronic VDIs for directives given. |
| Log | Log all actions taken. |

## 4.5	North-Houston Voltage Stability Limit

Procedure Purpose:  Maintain Transmission Stability between the North and Houston.

| Protocol Reference | 3.10.7.6 (3) | 6.5.9.1(1)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-003-1 R1 | IRO-002-2 R6, R8 | IRO-003-2 R1 | IRO-004-2 R3 |
|  | IRO-005-3a R1.2, R1.3, R1.7, R3, R5, R16, R17 | IRO-006-5 R1, R4 IRO-006-TRE-1 | IRO-008-1 R1 | TOP-002-2.1b R10 |
|  | TOP-004-2 R1, R2, R6, R6.6 | TOP-006-2 R5 | TOP-007-0 R3, R4 | TOP-008-1 R1 |

| Version: 1 | Revision: 15 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| IROL | The North – Houston VSAT voltage stability limit is an IROL; the actual flow should not be allowed to exceed the limit, and MUST NOT exceed the limit for more than 30 minutes. If necessary, the System Operator has the authority to direct load shedding before this IROL has been exceeded. |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| VSAT | - Ensure VSAT has solved in the last 30 minutes, - Update RTMONI with new limit each time it changes to give transparency to Market Participants. |
| North-Houston 345kV Circuit Outage | IF: - Any of the 345kV lines going into the Houston area has a forced outage; THEN: - Manually run the entire sequence of RTNET, RTCA, and RTDCP (VSA) immediately and proceed to the Monitor Step in this procedure. |
| Monitor | Monitor each of the following Reliability Margins: - N-H G - N-H L If any of these Reliability Margins fall below the following pre-defined limits, take the appropriate corrective action for each limit and notify the Shift Supervisor. |
| ≤500MW | - Request TOs in the affected areas turn on capacitor banks and turn off reactors near the weak busses that are available. |
| ≤400MW | - Activate the appropriate constraint, - Post message on MIS Public. Typical MIS Posting Script: “ERCOT is constraining for the North-Houston voltage stability limit.” |
| ≤300MW | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL - Instruct Resource Operator to deploy Non-Spin in the Coast Weather Zone (WZ_COAST) - Issue a Transmission Watch by making a Hotline call and posting on MIS Public - Notify Real-Time Operator to make Hotline notification to QSEs Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the North-Houston interface. Non-Spin is being deployed in the Houston area to help mitigate the issue. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| NOTE | When the Non-Spin Resource is on-line, they must change their Non-Spin schedule to 0 in order for SCED to dispatch them. |
| ≤200MW | VDI QSGR in the Houston area that were not bid in as Non-Spin. Override LDLs as needed. - Determine QSGR in the Coast Weather Zone (WZ_COAST) - Choose “COMMIT” as the Instruction Type from Resource level |
| ≤100MW | - Instruct the Resource Desk Operator to deploy Load Resources providing RRS in Houston - Issue a Transmission Emergency Notice by making a Hotline call and posting on MIS Public - Notify Real-Time Operator to make Hotline notification to QSEs Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice for the North-Houston interface. Load Resources in the Houston area are being deployed to help mitigate the issue. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| 0MW | - Instruct Centerpoint to drop firm load in 100 MW blocks. - Continue Transmission Emergency Notice by making a Hotline call and posting on MIS Public - Notify Shift Supervisor to make NXT notification Typical Script for Centerpoint: This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is directing Centerpoint to drop [*** MW] of firm load for the North – Houston interface. Notify ERCOT when this task is complete. Please repeat this back to me. That is correct, thank you.” Typical Hotline Script: “At [xx:xx], ERCOT is continuing the Transmission Emergency Notice for the North-Houston interface. Firm Load is being shed in the Houston area to help mitigate the issue. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Cancel | Make appropriate cancellations when back to normal operations. |
| GTL | When an unexpected change to system conditions occur that result in a significant limit change from the day-ahead GTL posting: - Declare a Watch by posting on MIS - Make Hotline call to TOs - Notify Real-Time operator to make hotline call - Notify Operations Support Engineer to post the new GTL Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch because the posted North - Houston Generic Transmission Limit has been updated on the MIS due to an unexpected change on the system. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting Script: “A Watch has been issued due to ERCOT updating the posted North - Houston GTL limit on the MIS due to an unexpected change on the system.” |
| Log | Log all actions taken. |

## 4.6	SPS, RAP, PCAP, MP, and TOAP

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 5.5.2 | 6.5.1.1(a),(c),(e) |  | 6.5.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.5.2(1) | 6.5.7.1.10 | 6.5.7.1.11(1),(4) | 6.5.7.8 |
|  | 6.5.9 | 6.5.9.1(1)(d) |  | 7.1 |
| Guide Reference | 2.8.1 | 1.6 | 2.6.2 | 1.7.1 |
|  | 1.7.3 |  |  |  |
| NERC Standard | EOP-003-1 R6, R8 | IRO-003-2 R1 | IRO-005-3a R1.1,R1.2, R1.3, R1.7, R1.10, R3, R5, R9, R12, R13, R16, R17 | IRO-006-5 R1, R3, R4, R5, R6 IRO-006-TRE-1 |
|  | IRO-002-2 R6, R8 | IRO-004-2 R3 | PRC-001-1 R6 | TOP-001-1a R1, R2, R5 |
|  | TOP-002-2.1b R6, R8, R10 | TOP-004-2 R1, R6, R6.6 | TOP-006-2 R3, R5 | TOP-008-1 R1, R2, R4 |

| Version: 1 | Revision: 13 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The electronic copy for the SPSs, RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP |
| NOTE | Special Protection Schemes (SPS) (identified as RAS in EMS) OR Remedial Action Plans (RAP) - EXAMINE the results of RTCA, - If the background has a color indicating a SPS or RAP, - Refer to Desktop Guide Transmission Desk Section 2.7 for explanation of colors and for actions to be taken based on the color of the background. |
| Log | Log all actions taken. |
| ### Special Protection Systems (SPS) (Identified as RAS in EMS) |  |
| NOTE | Real Time Contingency Analysis (RTCA) indicates a Post Contingent overload(s) on a Contingency in which the SPS will not mitigate all the overloaded elements automatically. In this case, Congestion Management techniques will be utilized to return the system to the state in which the SPS was designed to automatically relieve the overload. |
| NOTE | Use caution when the tolerance setting is <100% in RTCA. If the post-contingency loading on an element monitored by an SPS is above the tolerance threshold, but below the activation point of the SPS (100%), the contingency associated with the SPS will show in the Transmission Constraint Manager (TCM) display. When this occurs, the result will be a light blue highlighted background identifying the device ID on the TCM display. In this scenario, congestion management is not needed until the criteria in Desktop Guide Transmission Desk Section 2.7, is met. |
| Monitor | Each SPS will be displayed on the “Real Time Values” spreadsheet, as the SPS activation threshold increases the display changes color as follows: - Greater than 80% but less than 90% turns Orange - Greater than 90% turns Red |
| 1 | Typically SPSs are to solve post-contingency overloads on the Transmission System. IF: - The Transmission system topology has temporarily changed due to outages (planned or forced) that affects an SPS; THEN: - Utilize congestion management techniques to prevent any known SPS from operating in a pre-contingent state. |
| 2 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the SPS will not mitigate all the overloaded elements automatically; Example: (Light blue or Salmon highlighted background and above 100% loading) THEN: - As system conditions warrant, activate congestion management techniques to relieve the overload. |
| 3 | IF: - No reliability issues will arise as a result of a SPS’s operation; THEN: - At the Operator’s discretion, allow the SPS to perform its function. |
| 4 | IF: - An SPS operates; THEN: - Notify affected TO to reset SPS as system conditions warrant |
| SPS Posting | All SPSs are considered in-service unless otherwise notified by the TO. IF: - An SPS is taken out of service; THEN: - Post the information on MIS Public WHEN: - The SPS is placed back in service, THEN: - Cancel the message. Typical MIS Posting: The [name] SPS has been taken out of service. |
| Status Change | If notified that an SPS has changed status (taken out or placed in service): - Send e-mail for notification and have RTCA updated, - “OPS Support Engineering” - “1 ERCOT System Operators” - “DAMTeam” |
| Basecase continuous SPS Triggering | Continual triggering of a SPS during basecase operations should be managed utilizing manual constraints created in TCM (only applies to manual reset of SPS controls causing a reliability issue). IF: - An SPS is continually triggered during Basecase operations; THEN: - Verify that an associated manual constraint exists for this SPS in TCM, and activate the manual constraint in SCED. IF: - A manual constraint does not exist for this SPS in TCM; THEN: - Coordinate with the Operations Support Engineer to build a manual constraint for the SPS action in TCM. |
| LOG | Log all actions taken. |
| ### Remedial Action Plan (RAP) |  |
| 1 | IF: - A RAP exists for the contingency; THEN: - Review the RAP with the associated TO, - Notify the Shift Supervisor of the anticipated actions. |
| 2 | IF: - A RAP is used to alleviate the identified problem regardless of the contingency listed on the RAP; THEN: - Make log entry. |
| 3 | IF: - A RAP exists for the contingency AND does not solve the contingency OR the pre-RAP overload exceeds the 15 MN rating; THEN: - RTCA does not pass the 15MN (15 minute) rating to TCM, only the EMGY (2-hour emergency) rating. To properly constrain for RAP-associated elements, the % Rating column in TCM may need to be increased so that the constraint limit matches the 15MN value. - Increase the value in the % Rating column in TCM to loosen the constraint (maximum 100% of 15MN value). |
| 4 | IF: - RTCA indicates a post-contingency overload(s) on a contingency in which the RAP will not mitigate all the overloaded elements automatically; Example: (Light blue or Yellow highlighted background and above 100% loading) THEN: - Activate constraint if a 2% shift factor exists. |
| 5 | IF: - The contingency anticipated by the RAP takes place; THEN: - Direct the implementation of the RAP, - Respond to requests made by the TO in accordance with the RAP, - If necessary, continue to use additional congestion management methods, - When the contingency clears, notify the TO as soon as possible. |
| LOG | Log all actions taken. |
| ### Pre-Contingency Action Plan (PCAP) |  |
| CAUTION | Pre-Contingency Action Plans (PCAPs) are designed to be enacted before the contingency occurs. |
| 1 | WHEN: - RTCA shows a post-contingency overload and a PCAP exists to resolve it; THEN: - Review the PCAP with the associated Transmission Operator, - Notify the Shift Supervisor of the anticipated actions, - Direct the execution of the PCAP with the associated Transmission Operator. Typical Script to appropriate TO: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is directing [TO] to implement the ****PCAP and [open/close] [breaker(s)]. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| NOTE | If necessary, use congestion management methods for post contingency loading after initiating the PCAP. |
| 2 | IF: - Any PCAPs are still in use (reviewed each day between 0000 and 0500), AND - It is determined, in concurrence with the Shift Supervisor that it is no longer needed; THEN: - Direct the associated Transmission Operator to return the system to: - Its normal status, OR - Its status prior to implementation of the PCAP. |
| 3 | IF: - A PCAP is used to alleviate the identified problem regardless of the contingency listed on the PCAP; THEN: - Make log entry. |
| LOG | Log all actions taken. |
| ### Mitigation Plan (MP) |  |
| NOTE | Mitigation Plans (MPs) are pre-determined actions to be taken associated with the occurrence of a specific contingency event if congestion management methods cannot resolve the post-contingency overload. MPs are designed to be enacted POST-Contingency. They are NOT pre-emptive congestion management actions. - A MP is developed when SCED cannot fully resolve the constraint, OR - A MP is developed when there are no generator shift factors greater than or equal to 2% as indicated in EMS, - If a MP is used to alleviate the identified problem regardless of the contingency listed on the MP, make a log entry. |
| SCED unable to fully resolve constraint | IF: - SCED is unable to resolve a constraint; THEN: - Keep constraint active in SCED, - Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the constraint; THEN: - Keep constraint active in SCED, - Coordinate with Operations Support Engineer to develop a MP - If constraint exists due to an outage, a TOAP should be developed (see TOAP procedure), - Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes and the constraint remains violated in SCED. |
| < 2% Absolute Shift Factors | IF: - A constraint exists for which there are no generator shift factors greater than or equal to 2% as indicated in EMS; THEN: - DO NOT activate the constraint in SCED - Verify a MP or TOAP exists for the contingency, and review the MP or TOAP with the associated TO IF: - No MP or TOAP exists for the constraint; THEN: - Coordinate with the Operations Support Engineer to develop MP - If contingency exists due to an outage, a TOAP should be developed (see TOAP procedure) - Issue a Transmission Watch if the MP or TOAP has not been developed within 30 minutes. |
| TO Issue | IF: - Notified by a TO that it will take more time to implement the MP than is identified on the MP; THEN: - Notify the Operations Support Engineer to restudy and modify MP, - Log actions taken |
| Issue Watch | When issuing a Transmission Watch for an unsolved post-contingency overload (and waiting on MP or TOAP to be developed: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Post message on MIS Public Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Transmission Watch due to the post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] is being developed. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. Typical MIS Posting Script: At [xx:xx] a Transmission Watch was issued due to the post-contingency overload of [constraint name], a [mitigation plan/temporary outage action plan] is being developed. |
| Cancel Watch | When the MP or TOAP has been developed, cancel the Watch: - Make Hotline call to TOs - Instruct Real-Time Operator to call QSEs - Cancel message on MIS Public Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Transmission Watch for post-contingency overload of [constraint name] a [mitigation plan/temporary outage action plan] has been developed. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Contingency Occurs | IF: - The anticipated contingency takes place; THEN: - Direct (if necessary) the implementation of the MP or TOAP to the associated TO, - Respond as quickly as possible to requests made by the TO in accordance with the MP, - If necessary, continue to use congestion management methods for post-contingency loading after initiating the MP. |
| LOG | Log all actions taken. |
| ### Temporary Outage Action Plan (TOAP) |  |
| NOTE | TOAPs are temporary since they are outage related - A TOAP is developed when there is no generation shift factors greater than or equal to 2% as indicated in EMS, OR - A TOAP is developed when SCED cannot fully resolve the constraint |
| Planned Outage | IF: - A post-contingency overload is due to a planned outage on a transmission line(s) or a transmission facility; THEN: - Locate the TOAP in the Outage Notes, - Follow the same process as a MP outlined above. |
| Forced Outage | IF: - A post-contingency overload is due to a forced outage or planned outage not recognized by Outage Coordination on a transmission line(s) or a transmission facility; THEN: - Follow the same process as a MP outlined above. |
| LOG | Log all actions taken. |

## 4.7	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security.

| Protocol Reference | 6.3.2(2) | 6.5.7.1.10(3) | 6.5.7.8 | 6.5.7.9(7) |
| --- | --- | --- | --- | --- |
|  | 6.5.9 (3) |  |  |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R5, R6 |  |  |  |

| Version: 1 | Revision: 9 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instruction under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |
| ### Manual Dispatch to take a Unit Off-Line |  |
| 1 | This step DOES NOT apply to Qualifying Facilities (QF). For QF’s, refer to Transmission Congestion Management/Post-Contingency Overloads/step 5. IF: - A manual dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue a VDI taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Ensure QSE updates telemetry. |
| ### Manual Dispatch to take a Unit of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one unit of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and request which unit the QSE would like to shutdown, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue VDI to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Log the above information. |
| ### Manual Dispatch to bring a Unit of a Combined Cycle On-line |  |
| 1 | IF: - System conditions require a unit of a Combined Cycle Plant to be manually dispatched on-line; THEN: - Contact the QSE and notify which unit will be committed, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue VDI to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Log the above information. |
| ### Manual Commit of a Resource |  |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition; THEN: - Issue a VDI to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name or capacity in “other information” - See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct VDI. |
| 2 | Log information. |
| ### Canceling RUC Commitments |  |
| 1 | IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information |
| 2 | Log information. |
| ### Posting Manual Actions |  |
| 1 | IF: - Any manual action is taken (manual override or VDI); THEN: - Post message on MIS Public. Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. |
| 2 | Log information. |

## 4.8	Responding to Diminishing Reserves

Procedure Purpose: Monitor the Physical Responsive Capability (PRC) for issuing advance notice of diminishing Responsive Reserve.  Steps within this procedure are intended to keep ERCOT from progressing into EEA.

| Protocol Reference | 6.5.9.4.1 | 6.5.9.4(5) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-1 R2.4 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R8 | IRO-005-3.1a R1.4, R1.5, R4 |  |

| Version: 1 | Revision: 5 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - ERCOT, at management’s discretion, may issue an appeal through the public news media for voluntary energy conservation at any time. - Resource Desk Operator will post message on MIS Public. |
| ### Advisory |  |
| Issue Advisory | IF: - PRC < 3000 MW; THEN: - Using the Hotline, issue an Advisory. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory due to Physical Responsive Capability falling below 3000 MW. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Cancel Advisory | WHEN: - PRC > 3000 MW; THEN: - Using the Hotline, cancel the Advisory. Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Advisory for Physical Responsive Capability. Physical Responsive Capability is now above 3000 MW. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Ensure that all actions taken have been logged. |
| ### Watch |  |
| Issue Watch | IF: - PRC < 2500 MW; THEN: - Using the Hotline, issue a Watch. Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to Physical Responsive Capability falling below 2500 MW. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Cancel Watch | WHEN: - Notified by the Real-Time operator; THEN: - Using the Hotline, cancel the Watch. Typical Hotline Script: “This is ERCOT Operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for Physical Responsive Capability. At this time, the Advisory is still in effect. Resource testing may resume. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Log actions |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.5.7.1.10(3)(c) | 6.5.9.2(1) | 6.5.9.3 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 | 6.5.9.3.4 |
|  | 3.1.4.6(2) | 6.3.3 | 3.1.4.7(1) |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R4.1 | IRO-005-3.1a R1.10 |  |

| Version: 1 | Revision: 13 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within first contingency criteria are not likely or possible due to Forced Outages or other conditions - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability. - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day. - When extreme hot weather is projected for next day or current day - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM or in SASM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that require operations with active transmission violations - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request - ERCOT varies from time-line for DAM/DRUC |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - SCED fails to reach a solution and/or Emergency Base Points are issued - Loss of Primary Control Center Functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards during the Operating Period using every Resource practically obtainable from the market - ERCOT forecasts an inability to meet applicable Reliability Standards and it has exercised all other reasonable options - A transmission condition has been identified causing unreliable operation or overloaded elements - A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules - A severe single contingency event presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load, and/or overload of critical transmission elements and no practicable resource solution exists - ERCOT has determined a fuel shortage exists that would affect reliability - ERCOT varies from timing requirements or omits Day-Ahead or Adjustment Period and Real-Time procedures (HRUC/SCED) - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact of the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Generic Script |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | All notices must be posted on the MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Log | Make log entry. |
| ### Specific Scripts |  |
| NOTE | At times, the Real-Time, Resource or RUC operator takes the lead on the issuance of Hotline calls for specific procedures they have. The following scripts are to help guide you when specific procedures don’t exist for the T/S operator. |
| 50% Probability Of Down Ramp | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN due to a 50% probability of a [4,000 MW down-ramp in the next 180 minutes] [2,000 MW down-ramp in the next 60 minutes]. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]. Any questions”? |
| 70% Probability Of Up Ramp | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issued an OCN due to a 70% probability of a 2,000 MW up-ramp in the next 60 minutes. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]. Any questions”? |
| SCED Or RLC Failure | Note: RLC can fail independently of AGC; this same script will also be used for a RLC failure. If RLC is failed, SCED will have invalid results. Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of SCED. ERCOT may issue Emergency Base Points until the issue is resolved. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At [xx:xx], SCED base points are now valid and ERCOT is canceling the Emergency Notice. Any questions”? |
| EMMS (LFC and RLC/SCED) Failure | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to an LFC and SCED failure. ERCOT has placed [Name] QSE on Constant Frequency. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], LFC is now functional and SCED solutions are valid. ERCOT is canceling the Emergency Notice. Any questions”? |
| Increasing Amount of Ancillary Services | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services (A/S) requirement above what was procured in the Day-Ahead Market due to [state the reason]. ERCOT will open a Supplemental Ancillary Service Market (SASM) to procure the additional A/S for hours [hours] for operating day [date]. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for increasing the system wide A/S requirement. Any questions”? |
| A/S Insufficiency Offers in DAM | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to an insufficiency in A/S offers in the Day Ahead Market. Currently, ERCOT is requesting additional A/S Offers from QSEs. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for insufficient A/S offers in the Day Ahead Market. Sufficient offers have been received. Any questions”? OR: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for insufficient A/S offers in the Day Ahead Market. A/S were covered through DRUC. Any questions”? |
| A/S Insufficiency from DAM | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to A/S insufficiency in DAM for operating day [day]. The A/S insufficiencies will be procured in DRUC. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch due to A/S insufficiency in DAM. Any questions”? |
| REG/ RRS - RUC Committed Shortages | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due insufficient A/S offers; HRUC will be used to commit the remaining A/S insufficiencies. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch due insufficient A/S offers. Any questions”? |
| DAM Timeline Deviation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the timeline deviation of the Day Ahead Market; the start of DRUC will be delayed. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for the delay of DAM. DAM is now complete. Any questions”? |
| DAM Failure | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to the failure of the Day Ahead Market for [effected date] due to [state issue]. ERCOT will open a SASM to procure Ancillary Services for tomorrow’s operating day. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Emergency Notice for the failure of the Day Ahead Market for [effected date]. All Ancillary Services have been procured for tomorrow’s operating day. Any questions”? |
| DRUC Delay or Timeline Deviation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the timeline deviation of DRUC for [effected date] due to [state issue]. ERCOT will continue to try to complete DRUC by 18:00. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for the timeline deviation of DRUC. DRUC completed at [time]. Any questions”? |
| DRUC Timeline not Met | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to DRUC not completing by 1800 due to [state reason]. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Emergency Notice due to DRUC not completing by 1800 due to [state reason]. ERCOT will procure in HRUC if needed. Any questions”? |
| HRUC Failure or Timeline Deviation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to HRUC not completing for [state HE] due to [failure or timeline deviation]. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Emergency Notice due to HRUC not completing for [state HE]. Any questions”? |
| DRUC Committed For Capacity Shortage | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]. ERCOT will commit Resources as needed.. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]. Any questions”? |
| Excess Generation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]. Any questions”? |
| Projected Reserve Capacity Shortage with no market solution | Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX], which causes a high risk for an EEA event. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX]. Any questions”? |
| RMR Projected Reserve Capacity Shortage | Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. Any questions”? Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for a RMR projected reserve capacity shortage with no market solution available. Any questions”? |

## 7.2	Implement EEA Levels

Procedure Purpose:  To provide for maximum possible continuity of service while maintaining the integrity of the ERCOT system to reduce the chance of cascading outages.

| Protocol Reference | 6.5.7.6.2.2 | 6.5.9.1(3) | 6.5.9.4 | 6.5.9.4.1 |
| --- | --- | --- | --- | --- |
|  | 6.5.9.4.2 |  |  |  |
| Guide Reference | 4.5.3 | 4.5.3.1 | 4.5.3.2 | 4.5.3.3 |
|  | 4.5.3.4 |  |  |  |
| NERC Standard | COM-002-2 R2 | EOP-001-0.1b R3.1, R3.3, R5 | EOP-002-3.1 R1, R2, R4, R6.1, R6.2, R6.4, R6.6, | IRO-005-3.1a R1.5 |

| Version: 1 | Revision: 14 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - IF frequency falls below 59.8 Hz, ERCOT CAN immediately implement EEA 3. - IF frequency falls below 59.5 Hz, ERCOT SHALL immediately implement EEA 3. |
| NOTE | - Public media appeals may be enacted prior to EEA as deemed necessary by the Shift Supervisor. When a media appeal for voluntary energy conservation is enacted, TOs should be notified via Hotline call (see EEA 2 for typical script). - Confidentiality requirements regarding transmission operations and system capacity information will be lifted, as needed to restore reliability. |
| ### Implement EEA Level 1 |  |
| 1 | IF: - PRC < 2300 MW; THEN: - Using the Hotline, notify all TOs to implement EEA 1. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; at [xx:xx], ERCOT is declaring EEA 1 due to Physical Responsive Capability is below 2300 MW. [TO] please repeat this back to me. That is correct, thank you” After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 2. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | The Load Management Program step below is only to be considered on weekdays (except holidays) during the summer months (June to September) between 1330 and 1900 hours due to restrictions in TO Load Management Program contracts. |
| Load Management Program | Monitor predicted load increase over the next hour and into the peak hours as indicated in the prevailing ERCOT Load Forecast. * Only applies during the summer months (June to September) IF: - The current time is AT LEAST 13:30 BUT NOT AFTER 16:00, and - It is predicted that this event will proceed to EEA level 2; THEN: - Using the Hotline, contact all TOs with Load Management Programs, requesting implementation of their Load Management Programs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]; This call applies to the following Transmission Operators: Oncor, Centerpoint, AEP, and TNMP. At [xx:xx], ERCOT is requesting that these TOs deploy all available capacity from their Load Management Programs due to continued increased load growth. [TO] please repeat this back to me. That is correct, thank you.” Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 2 |  |
| 1 | IF: - PRC < 1750 MW or unable to maintain system frequency at 60 Hz; THEN: - Using the Hotline, notify all TOs to implement EEA 2 and any measures associated with EEA 1, if not already implemented. - If the energy conservation call has not been made previously, it can be combined with this call (see step Media Appeal below). Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 2; - [Load Resources and/or ERS Resources] have been deployed, - Reduce customer loads by using distribution voltage reduction measures, if deemed beneficial - *Request deployment of Load Management Programs [TO] please repeat this back to me. That is correct, thank you” * Only applies during the summer months (June to September) and if not already deployed in EEA 1. After the repeat, give TOs an update of system conditions, including chances of proceeding into an EEA 3. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Media Appeal | - Unless already in effect, verify with the shift supervisor that the communications group has issued an appeal through the public news media for voluntary energy conservation, - Notify TOs, via Hotline, that a media appeal for conservation is in effect. Typical Hotline Script: “This is ERCOT Operator [first and last name]; ERCOT has issued an appeal through the public news media for voluntary energy conservation. Any questions? Thank you”. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| 3 | Verify and log that all measures have been implemented. |
| ### Implement EEA Level 3 |  |
| 1 | IF: - Unable to maintain system frequency at 59.80 Hz; THEN: - Using the Hotline, notify all TOs to implement EEA 3 and any measures associated with EEA 1 and 2, if not already implemented - *Request deployment of Load Management Programs * Only applies during the summer months (June to September) and if not already deployed. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx], ERCOT is declaring EEA 3. ERCOT is directing all Transmission Operators to shed their share of [amount] MW. Transmission Operators are to report to ERCOT when this is complete. [TO] please repeat this back to me. That is correct, thank you”. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| 2 | Verify and log that all measures have been implemented. |

## 7.4	Block Load Transfer

Procedure Purpose:  To transfer loads, located in ERCOT to a Non-ERCOT system or from a Non-ERCOT system to ERCOT during emergency conditions.

| Protocol Reference | 6.5.9.5 | 6.5.9.5.1 | 6.5.9.5.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.4 |  |  |  |
| NERC Standard | EOP-001-0.1b R3.2, R4.2, R7.2, & R7.4 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Restoration of service to outage customers using BLT’s will be accomplished as quickly as possible if the transfers will not jeopardize the reliability of the ERCOT Interconnection. - BLTs that are comprised of looped systems may be tied to the non-ERCOT Control Area’s electrical system(s) through multiple interconnection points at the same time. Transfers of looped configurations are permitted only if all interconnection points are registered and netted under a single Electric Service Identifier (ESI ID) and represented by a single TSP or DSP or netted behind Non-Opt-in Entity (NOIE) metering points. |
| ### ERCOT picks up Load for Non-ERCOT System |  |
| 1 | IF: - ERCOT is requested to pick up load for CFE, MISO or SPP; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists - If BLT is registered (refer to Desktop Guide Common to Multiple Desks Section 2.5): - Issue VDI to the QSE listed (if no QSE listed, no VDI needed) - If BLT is not registered, proceed to step 2 - Determine the amount of load being transferred into ERCOT - Issue VDI to QSE (if applicable) - Choose QSE level tab - Choose [Proper QSE from Desktop Guide] for Participant Name - Choose “OTHER For QSE” for Instruction Type - In text, state “BLT from SPP, MISO or CFE to ERCOT” - Send e-mail to “BLT” distribution list with the above information - Include in e-mail whether BLT is modeled or not |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists - If no issues, allow the BLT - Determine the amount of load being transferred into ERCOT - Send e-mail to “BLT” distribution list with information - Include in e-mail that BLT is not registered - Include in e-mail whether BLT is modeled or not |
| 3 | For BLTs that are deployed in an emergency and are not modeled in the Network Operations Model, the responsible TO will notify ERCOT as soon as practicable after deployment. |
| 4 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Terminate the BLT. |
| ### Non-ERCOT System picks up Load for ERCOT |  |
| 1 | IF: - CFE, MISO or SPP picks up load for ERCOT; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists, - If BLT is registered (refer to Desktop Guide Common to Multiple Desks Section 2.5): - Issue VDI to the QSE listed (if no QSE listed, no VDI needed) - If BLT is not registered, proceed to step 2 - Determine the amount of load being transferred out of ERCOT - Issue VDI to QSE if applicable (if applicable) - Choose QSE level tab - Choose [Proper QSE from Desktop Guide] for Participant Name - Choose “OTHER For QSE” for Instruction Type - In text, state “BLT from ERCOT to SPP, MISO or CFE” - Send e-mail to “BLT” distribution list with the above information - Include in e-mail whether BLT is modeled or not |
| 2 | IF: - BLT is not registered in ERCOT; THEN: - Consult with Operations Support Engineer to ensure no reliability issue exists, - If no issues, allow the BLT, - Determine the amount of load being transferred out of ERCOT, - Send e-mail to “BLT” distribution list with information - Include in e-mail that BLT is not registered - Include in e-mail whether BLT is modeled or not |
| 3 | For BLTs that are deployed in an emergency and are not modeled in the Network Operations Model, the responsible TO will notify ERCOT as soon as practicable after deployment. |
| 4 | IF: - Congestion management issues that arise from switching variations due to BLT; THEN: - Employ Congestion Management procedures, IF: - Congestion management cannot maintain the reliability of the ERCOT System, THEN: - Terminate the BLT. |
| NOTE | If the Alamito Creek (ALMC) to Presidio (PRES) 69 kV transmission line trips, CFE will automatically pick up approximately 2 MW of load on the Presidio/Gonzales BLT. When AEP TO has informed you that this happened, follow step 1 above. |

## 7.5	Restoration of Primary Control Center Functionality

Procedure Purpose:  To be performed once Transmission and Security Operator has arrived at ACC.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: July 15, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Before normal operation can be restored, be sure to communicate with the other desks to determine the current state of the grid and any communications that may have taken place with Market Participants. |
| Congestion Management | Continue with congestion management either manually or with systems. Check with other Operators to determine if any VDIs were issued. |
| Return to Normal TO Notification | When ready to resume normal operation, place the following Hotline call to the TOs: - Typical Hotline Script: - “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]; at [xx:xx], ERCOT is canceling the Emergency Notice and is resuming normal operations from the [alternate/primary] control center. [Select TO], please repeat that back for me. If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Make separate call to HHGT giving them the same information as above. They can be reached using the Turret phone button labeled (HHGT TO), page 25. |
| Nuclear Plants | Notify the appropriate Nuclear Plant’s QSE and inform them that they should notify the plants that ERCOT has canceled the Emergency Notice and RTCA and State Estimator are now functional. |
| Log | Make log entries as needed. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | September 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch, Hartmann & Weldon | Procedure writers and editors | July 8, 2013 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT)Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 2.1 2.3 3.4 4.1 4.2 7.4 10.1 | 1.0 / 1 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 13 1.0 / 5 1.0 / 3 1.0 / 2 | Updated Scope Changed TSP to TO Updated database load script Changed insecure state to emergency condition Updated 1st Note, steps 6 & 8 in Post Contingency Overloads, steps 2 & 3 in Managing Constraints in SCED, added Model Inconsistencies/Updates procedure Updated Notes 1 & 2, Steps 1 & 2 Changed insecure state to emergency condition Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 3.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.5 9.2 10.1 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 14 1.0 / 6 1.0 / 8 1.0 / 7 1.0 / 6 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 8 1.0 / 7 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated Operations Support Engineer Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, added 3rd Note, updated step 1 in Review Planned Outage Notes, steps 1, 2, 3, 4, 6, 7, 8, 9 & QSGR in Post Contingency Overloads, step 2, 4 & Log in Managing Constraints in SCED Updated Operations Support Engineer Updated Operations Support Engineer & step 1, 2 & 3 Updated Operations Support Engineer Updated Desktop Guide reference, 2nd Note, step 5 & SPS Posting & deleted step 4 in SPS, all steps in Mitigation Plan & Temporary Outage Action Plan Updated Desktop Guide reference Updated step 1 in Watch Updated TSP to TO, Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, changed TSP to TO, Desktop Guide reference & step 1 of Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Watch Updated step 1 in Implement EEA Level 1 & step 1 in Implement EEA Level 3 Updated script in step 1 in Restore Firm Load Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer & Desktop Guide reference Updated Desktop Guide reference Updated all steps in Telemetry Issues that could affect SCED and/or LMPs, step 1 in Backup/Alternate Control Center Transfer & Operations Support Engineer | March1, 2012 |
| 3.1 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.2 8.3 8.4 | 1.0 / 3 1.0 / 7 1.0 / 15 1.0 / 9 1.0 / 8 1.0 / 7 1.0 / 4 1.0 / 9 1.0 / 9 - / 8 1.0 / 8 1.0 / 5 1.0 / 4 1.0 / 0 1.0 / 4 1.0 / 2 1.0 / 4 | Updated step Gap Study Added TSAT Updated step 4 & deleted step 9 in Post-Contingency Overloads, clarified step 2 & 3 in Managing Constraints in SCED, Added Unsolved Contingencies Updated for TSAT tool, added Managing W-N during System Failures Updated step IROL and ‘instructing’ to ‘directing’ Updated step Status Change & ‘instructing’ to ‘directing’, updated step 3, 4 & log in RAP, added step 3 and log in PCAP, update Note, added TO Issue in MP Updated Opportunity Outage procedure Added Valley Import to VSAT procedure, deleted step 2 in PSS/AVR section Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather Added Load Management Programs in Implement EEA Added Load Management Programs in Restore EEA Updated for NPRR405 Changed ‘TDSP’ to ‘TO’ & T/S Operator to Real-Time Deleted Cold Weather Revised to 8.2 and changed Severe Cold Weather to Extreme Cold Weather Revised to 8.3, added OCN & Emergency Notice Revised to 8.4 and changed T/S Operator to Real-Time Operator | May 1, 2012 |
| 2.3 4.1 4.5 6.1 7.2 7.3 7.5 | 1.0 / 6 1.0 / 16 1.0 / 8 1.0 / 10 1.0 / 9 1.0 / 9 1.0 / 6 | Updated Database load with W-N active and Site Failover with W-N steps Added Constraint SF Cut Off step, updated step 2 & 3 in Managing Constraints in SCED Updated 2nd Note, added Basecase continuous SPS triggering step in SPS, updated step 1 in RAP, step Note, SCED unable to fully resolve constraint, & < 2% Absolute Shift Factors in MP, 1st Note in TOAP Updated step Valley Import Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT | June 1, 2012 |
| 1.3 3.3 4.1 4.4 5.1 6.1 7.1 7.2 7.3 8.3 9.2 | 1.0 / 1 1.0 / 8 1.0 / 17 1.0 / 9 1.0 / 5 1.0 / 11 1.0 / 10 1.0 / 10 1.0 / 10 1.0 / 3 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated step 2 Updated step Constraint SF Cut Off, Managing Congestion during SCED Failure Updated step ≤300MW Updated Maintenance Level 2 and 3 outages Updated STP Voltage Tables Updated all step 1’s Updated Load Management Program Updated step 1 Updated scripts Updated 4th note | July 16, 2012 |
| 2.3 4.4 | 1.0 / 7 1.0 / 10 | Added Note to step Database Load Updated step IROL | August 29, 2012 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.7 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 8 1.0 / 2 1.0 / 9 1.0 / 18 1.0 / 10 1.0 / 11 1.0 / 9 1.0 / 3 1.0 / 12 1.0 / 11 1.0 / 11 1.0 / 11 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 5 | Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated PUN section and added to make call to HHGT Added Hotline script and to make call to HHGT Added Hotline script and to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated step 1 and added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT | September 12, 2012 |
| 2.2 3.1 3.2 3.3 3.4 4.1 4.3 4.4 4.5 5.1 5.2 6.1 7.4 8.3 9.1 | 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 10 1.0 / 2 1.0 / 19 1.0 / 11 1.0 / 12 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 13 1.0 / 7 1.0 / 5 1.0 / 4 | Added Hotline Call Communication Moved protective relay section to 5.2 Updated step 3 Split VSAT/TSAT and SE/RTCA out into separate procedures Updated steps Immediate Action Updated step Unknown Operating State, all steps in Evaluate Real-Time Contingency Analysis Results, steps 1, 4 & 6 in Post-Contingency Overloads Added 1st Note Added 1st Note, Updated 2nd NOTE & step 0 MW Updated 2nd Note Updated Returning from Planned Outage Early Added new procedure Updated Exceed URL, Reduce MW, added NOTE & moved step 1 to section 3.3 and renumbered Added Note Word smith OCN, Advisory, & Watch Updated step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.5 4.1 4.4 4.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 0 1.0 / 20 1.0 / 13 1.0 / 11 1.0 / 14 1.0 / 12 1.0 / 7 | Updated step 3 Added procedure Updated Note, Constraint Shift Factor Cut Off, Post-Contingency Overloads steps 4-9 , QSGR & Managing Constraints in SCED step 2 & 4 Updated step VSAT Updated Special Protection Systems (SPS) (Identified as RAS in EMS) step 2, Remedial Action Plan (RAP) steps 1-5, & step 3 Pre-Contingency Action Plan (PCAP) Updated 2nd Note and steps 1-3 Voltage Issues Deleted step 2 per NPRR 480 Updated all step 1’s & added step 3 to clarify 6.5.9.5.2(1) | March1, 2013 |
| 2.3 2.4 3.1 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 9 1.0 / 3 1.0 / 5 1.0 / 11 1.0 / 1 1.0 / 21 1.0 / 7 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 7 1.0 / 15 1.0 / 12 1.0 / 13 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts and steps in Caution, Phase Shifters, Constraint Shift Factor Cut Off, Post Contingency Overloads, deleted Input Displays, added step In Series & Same Element in Managing Constraints in SCED & deleted Managing Congestion during SCED Failure Updated step 2 Deleted 2nd Note, added GTL and updated scripts Deleted 2nd Note, added GTL and updated scripts Deleted Directives, 1st Note in Mitigation Plan, 1st Note in Temporary Outage Action Plan and updated scripts Updated scripts Updated all steps and deleted Cancelation Updated script Updated script Added Generic script and Specific scripts Updated scripts Updated scripts Updated scripts Updated script Updated scripts Updated script Updated script Correct spelling and updated script | June 1, 2013 |
| 2.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 7.1 7.2 7.4 7.5 | 1.0 / 10 1.0 / 22 1.0 / 9 1.0 / 8 1.0 / 13 1.0 / 15 1.0 / 13 1.0 / 9 1.0 / 5 1.0 / 13 1.0 / 14 1.0 / 8 1.0 / 5 | Updated step EMS Changes and added MMS Changes Updated step Caution Updated and moved section 7.4 and renamed to 4.2 Changed section # Updated and changed section # Changed section #, IROL & updated step 0MW Changed section # & updated step 4 in RAPs Changed section # Changed section # Updated step 1 in Watch, Emergency Notice & DRUC Timeline not Met Updated 2nd Note Changed section # & step 2 Changed section # | July 15, 2013 |