- Power Operations Bulletin # 648

ERCOT has posted/revised the DC Tie Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 1.1	Purpose

The ERCOT DC Tie Operator is responsible for energy transactions into and out of the ERCOT Control Area across the asynchronous DC Ties.  These transactions will be implemented in accordance with the North American Electric Reliability Corporation (NERC) Standard and the ERCOT Protocols and operating policies.  The ERCOT Operator will perform schedule confirmation with the applicable interconnected non-ERCOT Control Areas and will coordinate the approval process for NERC E-tags as both the ERCOT Control Area and on behalf of ERCOT TOs.  The ERCOT Operator will also confirm interconnected non-ERCOT Control Area schedule profiles with the DC Tie Operators, who will control the DC Tie to the schedules agreed to by both the designated Reliability Coordinator for the interconnected non-ERCOT Control Area and ERCOT.

The ERCOT DC Tie Operator performs his/her job function from the alternate control center and is also responsible for performing the loss of primary control center functionality procedure.

## 3.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-3 R1.2 | INT-005-3 R1 | INT-006-3 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | IRO-005-3.1a R2 | TOP-002-2.1b R5, R9 |  |

| Version: 1 | Revision: 13 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | AEP TO in Corpus Christi is the DC Tie Operator (AEP TO) for the DC_R (Railroad DC tie), DC_S (Eagle Pass DC tie), and the DC_L (Laredo VFT). All communications will be with the DC-Tie Operator and they will communicate with CFE. |
| NOTE | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC-Tie schedules are seen by our EMMS as a generator (import) or load (export). |
| NOTE | - ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC-Ties - The Railroad DC-Tie has a 15 MW minimum flow requirement when E-Tags are scheduled - Approximately one hour before start of schedule, notify the ERCOT Transmission & Security Operator with scheduled MW, Tie and direction of flow and duration. |
| NOTE | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria ERCOT uses to validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCO specified in the Physical Path If either of the above validations fail, the E-Tag will be automatically denied. If you feel an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the ERCOT help desk and OATI help desk if needed. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Summary Data>QSE Contracts |
| 1 | When a New or Updated E-Tag is received in the WebTrans system: Manually validate the following: - “ERCO” must not be listed as a PSE in the Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard), CD (central daylight) or CP (central prevailing) during time change - “Transaction type” must be “Energy or Normal” - AEPT must be included as a TP (Transmission Provider) in the Physical Path and ERCO as a Scheduling Entity on the AEPT TP row in the Physical Path - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT as shown on the “Energy and Transmission Profiles” section - Tags are permitted to be submitted within the COP time frame (up to seven days in advance), but a separate tag for each day must be submitted and the Start Time and Stop Time MUST NOT cross the midnight hour. IF: - Any of this information is incorrect on the E-Tag; THEN: - Deny the E-Tag, otherwise proceed below. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| 2 | The ramp rate for DC_R will be 50 MW per minute due to reactive issues on the CFE side. DC_L and DC_S have no ramp limitations.. - Ramp Duration should be filled out on DC_R E-Tags only - Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered - DC_L and DC_S ramp duration can remain blank which is the default for a 10 minute ramp. |
| 3 | The Railroad DC-Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. WebTrans: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name |

## 3.4	Adjustment of SPP DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-Tags.

| Protocol Reference | 4.4.4 | 4.4.4.1 | 4.4.4.2 |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the net scheduled interchange. |
| 1 | IF requested by the DC Tie Operator, checkout the net scheduled interchange value for each SPP DC Tie (DC_E/DC_N) affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 3.5	Curtailment for the SPP DC Ties

Procedure Purpose: The process to curtail E-Tags for the SPP DC Ties

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | INT-005-3 R1.1 | IRO-006-TRE-1 R1 | IRO-006-5 R1 |  |

| Version: 1 | Revision: 3 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Curtailments are customarily scheduled for one hour at a time. Therefore a curtailment that occurs several hours in a row may require that this procedure be repeated hourly. |
| 1 | IF: - A curtailment alarm is received in WebTrans, AND complying with the request will NOT put ERCOT in an unreliable state (such as EEA or IROL exceedance); THEN: - Approve the E-Tag curtailment. IF: - A curtailment alarm is received in WebTrans, AND complying with the request WILL put ERCOT in an unreliable state (such as EEA or IROL exceedance); THEN: - Deny the E-Tag, stating the reason on the tag, AND - Call SPP RC and provide reliability reason for denying the request. Webtrans Reference Displays: Tag Validation Summary Tag Approval Monitor |
| NOTE | IRO-006-5 R1 requests to curtail from RCs, BAs, or TOPs from another Interconnection shall be complied with, unless it provides a reliability reason to the requestor why it cannot comply with the request. |
| 2 | If a QSE or SPP Tariff desk requests an E-Tag be curtailed or adjusted for any reason, curtail the E-Tag to 0 (zero). |
| NOTE | E-Tag curtailments must be in an “Approved” or “Implemented” status to be calculated into the net scheduled interchange. |
| 3 | IF requested by the DC Tie Operator, checkout the net scheduled interchange value for each SPP DC Tie affected by E-Tag curtailments. WebTrans Reference Display: Realtime Summary |

## 3.6	Adjustment of CFE DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-Tags.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 |  |  |  |
| NERC Standard | INT-004-2 R1 |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Imports |  |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the n scheduled interchange. |
| 1 | IF requested by the DC Tie Operator, AEP TO, checkout the net scheduled interchange value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |
| ### Exports |  |
| 1 | Notify the ERCOT Transmission & Security Operator when E-Tag Net Export adjustments are greater than 100 MW during the Adjustment Period. |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the net scheduled interchange. |
| 2 | IF requested by DC Tie Operator, AEP TO, checkout the net scheduled interchange value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 3.8	Managing Daily Inadvertent Energy for the SPP DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.2b R12.1 | INT-003-3 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 6 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored each hour during the day to ensure inadvertent flows do not accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ERCOT-E or ERCOT-N). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| NOTE | Due to the DC_N deadband issue, if the net schedule on the North DC-Tie is less than 25 MW, the DC-Tie Operator has the option of: - Automatically flow 25 MW in the default direction of the DC Tie, OR - Add MW flow in the direction of the schedule. IF: - The deadband is creating a transmission issue; THEN: - Contact AEP DC Tie Operator (AEP DC TIE) - Explain the problem - Request the deadband flow direction be changed to alleviate the problem. |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP DC TIE). If there is a discrepancy, go over each. E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag cannot be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>Interchange>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP DC TIE) for each DC Tie: - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10MWH or more and the reason is known (database load, loss of ICCP, AEP automatically overriding the schedule on the North DC Tie, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Group to investigate problems with the meter information. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Inadvertent>ATF |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator (AEP DC TIE): IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for both the DC_E and DC_N - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies If the discrepancy is with the scheduled values, email an Excel copy of the WebTrans Interchange Report display to check their information against ERCOT’s. - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator - Click the “Apply Checkout” button. - If asked to change a scheduled value, log the appropriate information and send email to shiftsupv@ercot.com. - If the discrepancy is with an actual value, change it to the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_N and DC_E and email it to the following: - SPP DC-Tie Inadvertent - AEPTOWEST@aep.com - aepcheckout-west@aep.com |

## 3.9	Managing Daily Inadvertent Energy for the CFE DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.2b R12.1 | INT-003-3 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 7 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored each hour during the day to ensure inadvertent flows do not accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ROAD_DC, EGPS_DC, or LAR_VFT). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP TO). If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP TO) for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Also call the ERCOT Help Desk to have a ticket opened for the EMMS Production Group to investigate problems with the meter information. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Interchange>ATF Checkout |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator (AEP TO): IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_L, DC_R and DC_S - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF Checkout |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and send email to shiftsupv@ercot.com. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Checkout Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_S, DC_R and DC_L DC-Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

## 3.11	Loss of E-Tagging

Procedure Purpose: Contingency plan for loss of E-tagging capability.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 6 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Loss of ERCOT E-Tagging |  |
| 1 | If the WebTrans system goes down for an unknown reason (i.e. maintenance), contact the ERCOT Operator at the primary control center to check on their connectivity. If their system is also down, contact the ERCOT help desk (ERCOT HELPDESK) to see if the issue is on our end. If issue is not on the ERCOT end, contact the OATI help desk (OATI HELPDESK) to see if the issue is on their end. |
| 2 | Determine the estimated down time, if longer than 30 minutes, notify the SPP Tariff Operator (SPP Tariff) and the DC-Tie Operators (AEP DC TIE, AEP TO). |
| 3 | Post message on MIS Public: Typical MIS Posting: “The ERCOT E-tagging system is down and no new schedules will be accepted across the DC-Ties at this time”. |
| 4 | No new E-tags will be accepted, only curtailments: - Coordinate with the SPP Tariff Operator (SPP Tariff) and the appropriate DC-Tie Operator - Notify Real-Time Operator to determine if SCED needs to be manually executed for curtailments |
| NOTE | Before-the-fact and after-the-fact check outs will not be available |
| 5 | Once the WebTrans system is available, confirm SPP Tariff (SPP Tariff) and the DC-Tie Operators availability. If available for all parties: - Update the MIS Public posting by sending a “Notice Cancellation” - If curtailments were made while the WebTrans system was down, ensure E-tags are updated |
| ### Loss of DC-Tie Operator E-Tagging |  |
| 1; If the E-Tagging system is down for one of the DC-Tie operators and not ERCOT, no new schedule can be accepted.. 2; Post message on MIS Public: Typical MIS Posting: “The E-tagging system is down for the [state DC-Tie Operator] and no new schedules will be accepted across the [state DC-Tie(s)] at this time”.. 3; Once E-tagging system is operational, cancel message.. |

## 4.1	ERCOT Declares EEA 1

Procedure Purpose: Steps to perform when ERCOT declares an Energy Emergency Alert (EEA) 1.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0.1b R1, R3.1, R4.2, R7.2 | EOP-002-3.1 R1, R2, R4, R6.4, R6.6 | INT-004-2 R1 |  |
|  | IRO-005-3.1a R4, R10 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE DC-Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP Tariff), page 2 - The DC Tie operator for the SPP DC-Ties can be reached using the Turret phone button labeled (AEP DC TIE), page 19 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to and from SPP. They can be reached using the Turret phone button labeled (AEP QSE), page 4 - AEP Tenaska is the generation dispatcher that a VDI for emergency energy is issued to and from CFE. They can be reached using the Turret phone button labeled (AEP TENASKA QSE), page 4 |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC-Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC-Ties. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. |
| Comisión Federal de Electricidad (CFE) |  |
| 1a | IF: - There are export schedules on any CFE DC-Tie; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | IF: - There is export inadvertent payback flowing to CFE; THEN: - Stop inadvertent payback by contacting the DC-Tie Operator (AEP TO) Typical Script to DC Tie Operator (AEP TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC-Tie] be ramped to zero. Please notify CFE.” |
| 3a | Contact DC-Tie Operator (AEP TO) and request them to contact CFE to inquire about the availability of emergency energy on all available CFE DC-Ties. IF: - Emergency energy is available; THEN: - Request the DC-Tie Operator to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP Tenaska (AEP TENASKA QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP Tenaska (AEP TENASKA QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| 4a | IF: - CFE can not supply ERCOT with emergency energy; THEN: - Make log entry with information. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1”. |
| 2b | IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) Typical script to DC Tie Operator (AEP DC TIE): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag (see Desktop Guide DC Tie Desk Section 2.5) - Notify the Shift Supervisor |
| 3b | IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DC TIE). Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1 and is requesting the inadvertent payback on [name DC-Tie] go to zero.” |
| 4b | IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC-Tie Operator (AEP DC TIE) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | IF: - The SPP DC-Ties are not at maximum import into ERCOT; THEN: - Notify the SPP Tariff desk (SPP Tariff) to determine the availability of transmission service for an EEA 1 schedule. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC-Tie to start a schedule into ERCOT?” IF: - No current hour transmission service is available; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor IF: - Status changes from EEA 1 to EEA 2 or 3; THEN: - Proceed to Section 4.2 |
| 6b | IF: - Transmission service is available; THEN: - Notify AEP QSE (AEP QSE): Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” IF: - No available capacity; THEN: - Make log entry and do not proceed - Notify Shift Supervisor. IF: - Capacity is available; THEN: - Request AEP QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you” NOTIFY: - DC Tie Operator (AEP DC TIE): Typical Script for DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. AEP QSE will be submitting the transmission request and the E-Tag (s) for an EEA 1 schedule. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency into ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 1 to EEA 2. Thank you”. If moved to EEA 2 or 3 proceed to section 4.2, ERCOT Declares EEA 2 or 3. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all actions taken. |

## 4.2	ERCOT Declares EEA 2 or 3

Procedure Purpose: Steps to secure emergency energy across the DC tie(s) in an Energy Emergency Alert (EEA) 2 or 3.

| Protocol Reference | 6.5.9.4 (6) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0.1b R1, R3.1, R4.2, R7.2 | EOP-002-3.1 R1, R2, R4, R6.4, R6.6 | INT-004-2 R1 | INT-010-1 R3 |
|  | IRO-005-3.1a R4, R10 |  |  |  |

| Version: 1 | Revision: 8 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE ties can be reached using the Turret phone button labeled (AEP TO), page 4 - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP Tariff), page 2 - The DC Tie operator for the SPP DC Ties can be reached using the Turret phone button labeled (AEP DC TIE), page 19 - AEP QSE is the generation dispatcher that a VDI for emergency energy is issued to and from SPP. They can be reached using the Turret phone button labeled (AEP QSE), page 4 - AEP Tenaska is the generation dispatcher that a VDI for emergency energy is issued to and from CFE. They can be reached using the Turret phone button labeled (AEP TENASKA QSE), page 4 |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC-Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC-Ties. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| EEA | When notified by Hotline that ERCOT has declared EEA 2 or 3, proceed with this procedure. |
| Comisión Federal de Electricidad (CFE) |  |
| 1a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There are export schedules on any CFE DC-Tie; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback flowing to CFE; THEN: - Stop inadvertent payback by contacting the DC-Tie Operator (AEP TO) Typical Script to DC Tie Operator (AEP TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC-Tie] be ramped to zero. Please notify CFE.” |
| 3a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. Contact DC-Tie Operator (AEP TO) and request them to contact CFE to inquire about the availability of emergency energy on all available CFE DC-Ties. IF: - Emergency energy is available; THEN: - Request the DC-Tie Operator to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP Tenaska (AEP TENASKA QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP Tenaska (AEP TENASKA QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| 4a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - CFE can not supply ERCOT with emergency energy; THEN: - Make log entry with information. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Thank you.” |
| 2b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide DC Tie Section 2.3 or 2.4). Typical script to DC Tie Operator (AEP DC TIE): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag, - Notify the Shift Supervisor. |
| 3b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DC TIE). Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3] and is requesting the inadvertent payback on [name DC-Tie] go to zero.” |
| 4b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC-Tie Operator (AEP DC TIE) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | Complete this step if in EEA 1 there was no non-firm transmission service available or EEA 1 was skipped. Notify the SPP Tariff desk (SPP Tariff) to determine the availability of emergency transmission service across the SPP DC-Ties. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC-Tie(s)?” IF: - No emergency transmission service is available, THEN: - Do NOT proceed and make log entry. - Notify Shift Supervisor |
| 6b | IF: - Emergency transmission service is available; THEN: - Request emergency energy from AEP QSE (AEP QSE) Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” IF: - No available capacity, THEN: - Make log entry and do not proceed. IF: - Capacity is available; THEN: - Request AEP QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP QSE (AEP QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you.” NOTIFY: - DC Tie Operator (AEP DC TIE): Typical Script for DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP QSE will be submitting the transmission request and the E-Tag (s) for emergency energy into ERCOT. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP QSE (AEP QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 2 to EEA 3. Thank you”. IF EEA 1 has ended continue with this procedure. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC); Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5), - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all action taken |

## 4.5	Transmission Issues in the Areas of the CFE DC-Ties

Procedure Purpose: The process to curtail E-Tags for the CFE Ties and request emergency energy, if needed.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0.1b R3.1, R4.2 | INT-004-2 R1 | INT-005-3 R1.1 | INT-010-1 R2 |

| Version: 1 | Revision: 12 | Effective Date: December 13, 2013 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie operator for the CFE DC-Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - AEP Tenaska is the generation dispatcher that a VDI for emergency energy is issued to and from CFE. They can be reached using the Turret phone button labeled (AEP TENASKA QSE), page 4 |
| NOTE | DC Tie Load shall neither be curtailed during the Adjustment Period, nor for more than one hour at a time, except for the purpose of maintaining reliability. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific MW amount, only CFE needs to approve the change. Curtailments will be automatically approved by them. |
| ### Transmission Issues within ERCOT |  |
| 1 | When ERCOT is in an Emergency, it may be necessary to curtail export E-Tags using the Last-in-First-Out (LIFO). IF: - Notified by the ERCOT Transmission & Security Operator of the need to curtail (which includes reductions) exports on a specific DC-Tie; THEN: - Verify the MW amount the E-tag needs to be curtailed, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE - Notify PSE with curtailment information and reason. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] to [state MW amount] starting at [xx:xx] due to transmission issues within ERCOT. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified by the ERCOT Transmission & Security Operator that the E-Tags can be re-loaded: - Notify PSE with reload information, - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Section 2.5), - Ensure DC Tie Operator (AEP TO) sees the re-loaded E-Tags, and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx], the transmission issues within ERCOT have been resolved and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CFE to approve re-loads. Please repeat this back to me. That is correct. Thank you.” |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Instruct DC Tie Operator (AEP TO) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission & Security Operator there is need for emergency energy; THEN: - Request the DC-Tie Operator (AEP TO) to inquire about the availability of emergency energy on [name DC-Tie(s)] Typical Script to DC Tie Operator (AEP TO) Corpus “This is ERCOT operator [first and last name] At [xx:xx] ERCOT declared an Emergency, we are requesting you to contact CFE to inquire about the availability of emergency energy into ERCOT on [name DC-Tie(s)] IF: - Emergency Energy is available; THEN: - Request the DC-Tie Operator (AEP TO) to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Issue AEP Tenaska (AEP TENASKA QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC-Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of rest) - Notify AEP Tenaska (AEP TENASKA QSE) that VDI has been issued. IF: - Emergency Energy is not available; THEN: - Notify ERCOT Transmission & Security Operator |
| LOG | Log all actions taken. |
| ### Transmission Issues within CFE |  |
| NOTE | On the CFE side of the Railroad DC-Tie, there is an automatic runback scheme that runs back the DC-Tie under CFE contingency conditions. When this occurs, and notification is made by the DC-Tie Operator; follow the procedure below. |
| 1 | Due to reliability issues within CFE it may be necessary to curtail import E-Tag(s) for them. IF: - Notified by the ERCOT Transmission & Security Operator or the DC Tie Operator (AEP TO) of the need to curtail imports on specific CFE DC-Ties; THEN: - Verify the MW amount and time of the curtailment, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact the DC Tie Operator (AEP TO) when curtailment is complete and instruct them to make notification to CFE, - Notify PSE with curtailment information and reason. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag [tag number] on the [DC tie name] to [state MW amount] due to reliability issues within CFE. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified that CFEs reliability issue has been resolved and E-Tags can be re-loaded: - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Ensure DC Tie Operator (AEP TO) sees the re-loaded E-Tags, and instruct them to make notification to CFE, - Notify PSE with reload information. |
| 3 | IF: - The re-loaded E-Tag goes passive deny because CFE did not approve the E-Tag in the allotted time; THEN: - Re-load the E-Tag again, - Call the DC Tie Operator (AEP TO) to make notification to CFE again. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission & Security Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.3, Emergency Energy to CFE. |
| LOG | Log all actions taken. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | June 27, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 9, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 1.0 / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |
| 2.3 3.1 3.2 3.3 3.6 3.7 3.8 3.9 3.11 4.1 4.2 4.3 4.5 4.6 4.8 | 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 7 1.0 / 4 1.0 / 6 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated step “Beginning of each Shift” Updated 1st note Updated steps 1, 2 & 3 Updated 1st, 4th note and step 1 Updated step 1 “Imports” and step 2 “Exports” Updated Steps 1, 2 and 4 in “CFE DC-Ties” Updated 2nd note and steps 1-3 Updated steps 1-3 Updated steps 1 and 2 Updated all steps Updated all steps Updated all steps Updated all steps Removed reference of Austin Control Room Added projected reserve capacity shortage and Extreme Hot Weather in Watch | September 1, 2011 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 6 1.0 / 7 | Updated step 2 Updated step 1 Updated Turret Phone, step 3a in Comision Federal de Electricidad (CFE) and step 5b to implement NPRR 379 Updated Turret Phone and step 3a in Comision Federal de Electricidad (CFE) Updated step 3 | October 1, 2011 |
| 4.6 | 1.0 / 7 | Updated step TO Hotline Call | November 1, 2011 |
| 3.1 3.3 4.6 4.8 | - / 9 1.0 / 9 1.0 / 8 1.0 / 7 | Updated step 2 Updated step 1 Added new section and updated all steps Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.3 4.6 | 1.0 / 1 1.0 / 10 1.0 / 10 1.0 / 9 | Updated Scope Updated step 2 Updated step 1 Updated Hotline call scripts | January 19, 2012 |
| 2.1 2.3 3.1 3.2 3.7 4.1 4.2 4.3 4.5 4.8 | 1.0 / 1 1.0 / 4 1.0 / 11 1.0 / 5 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 7 1.0 / 8 | Added dispatch instructions paragraph Updated Desktop Guide reference Added 3rd Note Changed Shift Engineer to Operations Support Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 2nd Note & all steps 1 – 3 Updated step 1 of Watch | March 1, 2012 |
| 3.1 3.3 3.7 3.8 3.9 4.54.6 4.8 | 1.0 / 12 1.0 / 11 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 10 1.0 / 9 | Updated step 2 Updated 3rd Note and step 1 Added posting and cancelling messages Updated overview Updated overview Updated procedure based on NPRR405 Updated W-N or N-H steps Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather | May 1, 2012 |
| 1.3 3.2 3.8 3.9 4.5 4.6 4.8 | 1.0 / 1 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 11 1.0 / 10 | Removed ERCOT Shift Supervisor paragraph Updated step 1 Updated step 4 Updated step 4 Added step Turret Phone & 1st Note, updated step 4 Updated several steps based on lessons learned from classroom training and simulation Updated all step 1’s | July 16, 2012 |
| 3.1 | 1.0 / 13 | Updated step 2 | August 29, 2012 |
| 2.2 3.2 4.5 4.6 | 1.0 / 1 1.0 / 7 1.0 / 10 1.0 / 12 | Added Hotline Call Communication Updated 1st Note Updated 1st and 2nd Note Updated steps West to North & North to Houston(IROL) All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.1 3.10 4.6 | 1.0 / 14 1.0 / 3 1.0 / 13 | Updated step 2 Updated 2nd note Updated Additional Notifications on Systems Functional and Systems are not Functional | March 1, 2013 |
| 3.1 3.2 3.7 3.11 4.6 | 1.0 / 15 1.0 / 8 1.0 / 9 1.0 / 4 1.0 / 14 | Updated step 2 Updated step 1, deleted steps 2 & 3 Updated scripts Updated script Updated scripts, West to North & step North to Houston | June 1, 2013 |
| 3.6 4.3 4.4 4.5 4.6 | 1.0 / 5 1.0 / 9 1.0 / 6 1.0 / 11 1.0 / 15 | Updated Exports, step 1 Updated step 1 & 3 Updated step 1 Deleted 2nd Note, updated step 1, 2 & 4 Added Monitor Frequency and updated Constant Frequency | July 1, 2013 |
| 3.1 3.3 3.11 4.8 | 1.0 / 16 1.0 / 12 1.0 / 5 1.0 / 11 | Updated step 1 Updated 4th note Updated step 1 Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.7 4.6 | 1.0 / 10 1.0 / 16 | Added CFE DC-Tie Derates and AEP DC-Tie Derates Removed HHGT TO reference | August 30, 2013 |
| 1.1 3.3 3.4 3.5 3.6 3.8 3.9 3.11 4.1 4.2 4.5 | 1.0 / 2 1.0 / 13 1.0 / 4 1.0 / 3 1.0 / 6 1.0 / 6 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 8 1.0 / 12 | Changed “Security” to “Reliability” Updated step 2 Updated both steps Updated last Note and step 3 Updated the Notes and step 1 and 2 Updated step 2 Updated step 2 New Loss of DC-Tie Operator E-tagging Updated step 6b Updated step 6b Added note to Transmission Issues within CFE All procedures in this manual have been reviewed. | December 13, 2013 |