- Power Operations Bulletin # 658

ERCOT has posted/revised the Shift Supervisor Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Resource Testing and In-Service Approvals

Procedure Purpose: This procedure provides direction and guidelines for conducting various required testing and approval processes for resources and transmission elements. This procedure does not include testing for the Net Dependable Capacity (NDC) on wind generation.

| Protocol Reference | 3.3.1 | 8.1.1.2.1.1(4) | 8.5.1.1 | 8.5.1.2(1) |
| --- | --- | --- | --- | --- |
|  | 8.5.1.2(3) |  |  |  |
| Guide Reference | 3.3.2.3 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 |  |  | Effective Date: January 29, 2014 |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Step |  | Action |  |  |  |  |  |
| ### Unit Testing |  |  |  |  |  |  |  |
| NOTE |  | QSEs will submit test requests to shiftsupv@ercot.com. If e-mail is down, a fax will be accepted at (512) 248-6858. Test request forms are located on the ERCOT website under ‘Operating Procedures’. |  |  |  |  |  |
| 1 |  | As requests for unit tests are received, make every reasonable effort to accommodate testing. Reasons for not accommodating testing: - Unit has best shift factor to manage congestion for an outage. Without unit, contingency may reach max shadow price and become unsolvable, - The request exceeds 7 days, - A pattern of repeated requests for the same unit(s) indicate that abuse of the testing privilege may be taking place. If any request is refused for this reason, notify the Manager, System Operations and/or Control Room Operations Manager. |  |  |  |  |  |
| CAUTION |  | If deployment of the testing unit is necessary to maintain system security, direct the test be canceled and deploy as needed. |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT recognizes the need of <Company Name> to test its unit on <date and time>. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | IF the request cannot be accommodated, RESPOND via e-mail or fax to the requesting party similar to the following: “ERCOT cannot accommodate the request of <Company Name>for a unit test on <date and time> for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| ### Approved Resources to be ONTEST |  |  |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to be ONTEST. |  |  |  |  |  |
| ### Turbine Governor |  |  |  |  |  |  |  |
| 1 |  | - At all times an All-Inclusive Generation Resource is on-line, its turbine governor must remain in service and be allowed to respond to all changes in system frequency. - When the governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT. - An All-Inclusive Generation Resource may not reduce governor response during abnormal conditions without ERCOT’s consent unless equipment damage is imminent. - Each Generation Entity shall conduct applicable generating governor speed regulation tests on each of its Generation Resources. |  |  |  |  |  |
| ### In Service Approval (or Approval to Energize) |  |  |  |  |  |  |  |
| 1 |  | IF: - A Market Participant makes a request to energize new or relocated equipment; THEN: - Review notification provided by Operations Support Engineering, - Approve the request if notification has been provided; IF: - The equipment has not been approved by Operations Support Engineering, THEN: - Delay the request and notify Operations Support Engineer. |  |  |  |  |  |
| ### Ancillary Service Testing Coordination |  |  |  |  |  |  |  |
| 1 |  | Ancillary Service Qualification Testing will be done in coordination with Operations Analysis and EMMS Production Support. IF: - A QSE requests an Ancillary Service Qualification Test; VERIFY: - A Wholesale Account Manager is in the notification or Direct the QSE representative to notify their Wholesale Account Manager to start the process. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Operations Analysis and EMMS Production Support. When contacted by Operations Analysis: - Wholesale Account Manager will notify QSE of scheduled test, - Ensure reliable conditions exist at all times. |  |  |  |  |  |
| Log |  | Log all actions. |  |  |  |  |  |
| ### Coordinated Reactive Tests |  |  |  |  |  |  |  |
| NOTE |  | The Resource Entity requesting to perform a Coordinated Test will provide ERCOT Operations and the TO with notice of the proposed test date before 1500 on the day prior to the day of the test. Requests shall be made between 0800 and 1700 on Business Days. Upon receipt of a request for test, ERCOT Operations and the TO will evaluate the expected conditions and determine whether ERCOT System conditions are conducive to a valid test can be created through coordinated network switching, modification of the generation reactive dispatch of nearby Generation Resources, or by some other means. Having established that suitable ERCOT System conditions exist or can be created, ERCOT Operations, and the TO shall confirm with the Resource Entity and the QSE the agreed upon test time and date or a rejection of the test time and date before 1700 on the day prior to the day of the test. |  |  |  |  |  |
| 1 |  | Coordinated Reactive Tests will be done in coordination with System Operations, Operations Analysis, the Transmission Operator (TO), and the Qualified Scheduling Entity (QSE). WHEN: - A QSE makes a request for a Coordinate Reactive Test; VERIFY: - Date/Time of Testing - MVAR Leading and/or Lagging expected during the test - CURL/D-Curve is attached - Estimated MW output If all information is included in the test request, proceed to step 2. If not, reply to e-mail from QSE and request the missing information. |  |  |  |  |  |
| 2 |  | The coordination of the testing times will be between System Operations, Operations Analysis and the Transmission Operator (TO). WHEN: - All information above is received; VERIFY: - TO has approved the test, - TO can approve verbally on a recorded line or by email Once the TO has approved and all information is accurate, approve the QSE test request. Include for following in the approval: - Operations Analysis - Shift Supervisors |  |  |  |  |  |
| OK to Test |  | If the testing can be accommodated, RESPOND via e-mail to the requesting party similar to the following: “ERCOT recognizes the need of <Company Name> to perform a Coordinated Reactive test with its unit <name> on <date and time>. ERCOT intends to make system adjustments to accommodate this testing to the extent possible consistent with system security. [TO] concurs with the test as long as real-time conditions allow for it. This will require the Generator Operator to contact the local transmission company prior to test initiation. This intent is NOT a guarantee of accommodation”. ___________________ (Shift Supervisor) |  |  |  |  |  |
| Not OK to Test |  | If the request cannot be accommodated, RESPOND via e-mail to the requesting party similar to the following: “ERCOT cannot accommodate the request of <Company Name>for a unit test on <date and time> for the following reason(s) : <List reasons>”. __________________ (Shift Supervisor) |  |  |  |  |  |
| Approval |  | - As Resource tests are approved, update “Approved Unit Tests” spreadsheet located on the System Operations SharePoint. - All operators will be able to view the list to determine which resources are approved to be ONTEST. |  |  |  |  |  |
| Log |  | Log all actions. |  |  |  |  |  |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Reliability Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R4.1, R5 | EOP-002-3.1 R3, R6.3, R7.2 | EOP-004-2 | IRO-014-1 R1.1.2 |
|  | IRO-015-1 R15 | TOP-002-2.1b R4 | DOE OE-417 |  |

| Version: 1 | Revision: 18 | Effective Date: January 29, 2014 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template between 0300 – 0400 and again between 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - When Off-Line Non-Spin is deployed for capacity (provide times) - A special update is not needed; provide information next time report is updated. - Conditions change that required new notices to be issued or cancelled - OCN , Advisory, Watch, or Emergency Notice - Clarify whether Transmission Watch/Emergency is due to a planned or forced outage (state the area of the state) - Do NOT update report for DAM delays or tool outages. - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas curtailments, not expected to cause reliability issues (be specific, how much is derated) - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Do Not use abbreviations, spell words out. Send updated report when conditions have returned to normal. |  |
| Weather Information | The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Physical Responsive Reserve ≤ 1750 MW and trending downward - Critical - Physical Responsive Reserve ≤ 1375 MW and trending downward Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - High - EEA Level 2 in effect - Physical Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.8 Hz - Critical - EEA Level 3 in effect |  |
| ### 7-Day Outlook |  |  |
| Report | Complete the 7-Day Outlook Report between 1500 – 1530 each day. |  |
| Open | The 7 Day Forecast file is located: P:\SYSTEM OPERATIONS drive in the “7-Day Outlook” Folder. |  |
| Verify | Data looks to be correct. |  |
| E-Mail Report | E-mail the report to the 7-Day Load and Capacity Outlook distribution list by selecting “Report” and confirming. |  |
| ### Event Analysis Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations and Control Room Operations Manager - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis program, brief reports must be completed with 5 days. Most events listed are either OE-417 or EOP-004 reportable, those timelines and forms will be used in place of the EA brief report. Category 1 Events: - An unexpected outage, contrary to design, of three or more elements caused by a common disturbance. For example: - The sustained outage of a combination of three or more facilities - The outage of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); each combined cycle unit is counted as one generator - Intended and controlled system separation by the proper operation of a SPS - Failure or misoperation of BPS SPS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BPS emergency - Unintended BPS system separation that results in an island of 100 MW to 999 MW. Excludes BPS radial connection, and non-BPS (distribution) level islanding - Unplanned evacuation from a control center facility with BPS SCADA functionality for 30 minutes or more - The loss of generation of 1,000 MW – 1,399 MW - Loss of monitoring or control, at a control center, such that it significantly affects the entity’s ability to make operating decisions for 30 continuous minutes or more. Examples include, but are not limited to the following: - Loss of operator ability to remotely monitor, control Bulk Electric System (BES) elements, or both. - Loss of communications from SCADA RTUs - Unavailability of ICCP links reducing BES visibility - Loss of the ability to remotely monitor and control generating units via AGC - Unacceptable State Estimator or Contingency Analysis solutions Category 2 Events: - Complete loss of all BPS control center voice communication system for 30 minutes or more - Complete loss of SCADA, control or monitoring functionally for 30 minutes or more - Voltage excursions equal to or greater than 10% lasting more than 15 continuous minutes due to a BPS emergency - Loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - Interconnection Reliability Operating Limit (IROL) Violation for time greater than Tv. Category 3 Events: - Unintended loss of load or generation of 1,400 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Unintended loss of load or generation from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Unintended loss of load of 10,000 MW or more - Loss of generation of 10,000 MW or more |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations and/or Control Room Operations Manager when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". - NERC 24-hour Emergency Hotline (404) 446-9780), |  |
| OE-417 Reporting Events | DOE OE-417 forms can be downloaded at: http://www.eia.gov/survey/form/oe_417/form.pdf. The items in bold/grey must be reported within 1 hour of the incident. The others must be reported within 6 hours. All final reports must be submitted within 48 hours. OE-417 reports are required for the following events: - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Complete operation failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system - Uncontrolled loss of 300 MW or more of firm system loads form more than 15 minutes from a single incident - Load shedding of 100 MW or more implemented under emergency operational policy - System-wide voltage reduction of 3 % or more - Public appeal to reduce the use of electricity for purposed of maintaining the continuity of the electric power system (ERCOT process each EEA) - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Loss of electric service to more than 50,000 customers for 1 hour or more - Fuel supply emergencies that could impact system adequacy or reliability |  |
| Event Reporting EOP-004-2 | NERC Preliminary Disturbance reports are to be completed within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time).. Events that are also DOE reportable, the OE-417 form should be used. For the other events, use the EOP-004 – Attachment 2 Event Reporting Form: - Damage or destruction of a Facility that results in actions to avoid a BES Emergency - Damage or destruction of a Facility that results from actual or suspected intentional human action - Physical threats to a Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility or suspicious device or activity at a Facility. Do not report theft unless it degrades normal operation of a Facility - Physical threats to a BES control center - Public appeal for load reduction event (ERCOT process each EEA) - System wide voltage reduction of 3% or more - Manual firm load shedding 100 MW or more - Automatic firm load shedding 100 MW or more (via automatic undervoltage or underfrequency load shedding schemes or SPS - Voltage deviation of 10% or more of nominal voltage sustained for 15 or more continuous minutes - IROL violation - Loss of firm load for 15 minutes or more: - 300 MW or more for entities with a previous year’s demand of 3,000 MW or more - 200 MW or more for all other entities - Each system separation resulting in an island 100 MW or more - Loss of generation of 1,000 MW or more - Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement - Unexpected loss within its area, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing - Unplanned evacuation from BES control center facility for 30 continuous minutes or more - Complete loss of voice communication capability affecting a BES control center for 30 continuous minutes or more - Complete loss of monitoring capability affecting a BES control center for 30 continuous minutes or more such that analysis capability (i.e., State Estimator or Contingency Analysis) is rendered inoperable |  |
| 1 | When required to file or forward a report, the Manager, of System Operations or the Control Room Operations Manager will be responsible. File or forward disturbance report to: - NERC System Awareness (systemawareness@nerc.net) - NERC (esisac@nerc.com), courtesy copy only - Fax (404) 446-9770, if internet down - Phone (404) 446-9780 - DOE when required above (doehqeoc@oem.doe.gov) - Fax (202) 586-8485, if internet down - Phone (202) 586-8100 - NERC and DOE Disturbance Reporting e-mail list |  |
| ### RCIS Reporting |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| NOTE |  | NXT notification should be coordinated with the Shift Engineer. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - Enter temperatures from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations and/or Control Room Operations Manager. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | A geomagnetic disturbance (GMD) occurs when the magnetic field embedded in the solar wind is opposite that of the earth. This disturbance, which results in distortions to the earth’s magnetic field, can be of varying intensity and has in the past impacted the operation of communications systems, and electric power systems. |  |
| 1 | Periodically, monitor the NERC Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net |  |
| 2 | WHEN: - Alerts for GMDs are issued for K-7 or higher; THEN: - Instruct the Transmission & Security and Real-Time Operators to make Hotline calls, AND - Post message on MIS Public |  |
| 3 | WHEN: - The GMD alert has expired; THEN: - Instruct the Transmission Operator to make Hotline call to TOs, AND - Post message on MIS Public |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |
| ### Special Protection Systems (SPSs) |  |  |
|  | IF: - A Monthly SPSs report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Shift Supervisors |  |

## 7.2	EEA Implementation Checklist

shift Supervisor – EEA IMPLEMENTATION Check List

| Time | Action | Comment |
| --- | --- | --- |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - MIS message posted |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posting |  |
|  | - Ensure 3-part communication is used |  |
|  | EEA Level 1 Implementation | PRC <2300 MW |
|  | - Non-Spin deployed |  |
|  | - 30 MIN ERS deployed, if deploying in Level 1. This includes Weather-Sensitive if June – September and business hours 2 & 3 |  |
|  | - Resource testing suspended |  |
|  | - Online RMRs loaded to full output |  |
|  | - Emergency Energy procedures implemented across CFE DC-Ties |  |
|  | - EEA 1 Schedule requested across SPP DC-Ties |  |
|  | - RUC VDIs issued, as appropriate |  |
|  | - TOs load management program deployed if deemed necessary if June - September |  |
|  | - OE-417 for public appeals |  |
|  | EEA Level 2 Implementation | PRC <1750MW |
|  | - Load Resources deployed and/or ERS Resources - Block 1 (<1750MW) - Block 2 (as needed) - Both (<1375MW) |  |
|  | - 30 MIN ERS deployed, if not deployed in Level 1. This includes Weather-Sensitive if June – September and business hours 2 & 3 |  |
|  | - 10 MIN ERS deployed, if deemed necessary |  |
|  | - TOs load management program deployed if June - September |  |
|  | - Emergency Energy Procedures implemented across SPP DC-Ties |  |
|  | - TOs notified of Load Resource deployment |  |
|  | - Distribution voltage reduction, as appropriate |  |
|  | - RUC VDIs issued, as appropriate |  |
|  | EEA Level 3 Implemention | Unable to maintain Freq at 59.8 Hz. |
|  | - Firm Load shed ordered (100 MW blocks) |  |
|  | - QSEs notified of Firm Load shed |  |
|  | - Load shed achieved |  |

## 7.3	EEA Restoration Checklist

Shift Supervisor – EEA Restoration Check List

| IMPORTANT: If the EEA event coincides with a severe weather event that resulted in the loss of residential load as well as the ERCOT directed shedding of firm load, COORDINATE load restoration with the appropriate Transmission Operator to insure lost residential load is given priority over the shed load. |  |  |
| --- | --- | --- |
| Time | Action | Comment |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - MIS message updated |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posted |  |
|  | RESTORE FIRM LOAD | Sufficient Regulation exist to control to 60 Hz & PRC – Reg Up Resp. is >1375 MW |
|  | - Firm load restoration directed |  |
|  | - QSEs notified of Firm load restoration |  |
|  | - Load shed recall achieved |  |
|  | EEA LEVEL 3 TO EEA LEVEL 2 | Sufficient Regulation exist to control to 60 Hz & PRC >1375 MW while Load Resources are being recalled |
|  | - Begin recalling Load Resources |  |
|  | - TOs notified of Load Resources |  |
|  | - May begin recalling 30/10 MIN ERS Resources |  |
|  | - TOs notified of Load Resource and ERS Resources recall |  |
|  | EEA Level 2 TO EEA LEVEL 1 | PRC > 1750 MW & all Load Resources and ERS have been instructed to be restored |
|  | - ERS Resources recalled if not already done |  |
|  | - Distribution voltage reductions measures recalled |  |
|  | - TOs notified of ERS Resources recall |  |
|  | - TOs load management program recalled |  |
|  | EEA Level 1 TO EEA 0 | PRC > 2300 MW & all Load Resources and ERS have been instructed to be restored |
|  | - End emergency energy across DC Ties |  |
|  | - Release any RUC committed Resources |  |
|  | - See administrative tasks |  |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |
| 3.4 4.1 6.1 7.3 | 1.0 / 6 1.0 / 5 1.0 / 16 1.0 / 5 | Updated QSE Notification, TO Notification & Send E-mail Updated Coordinated Reactive Tests Added 7-Day Outlook, updated Event List on Texas RE Event Reporting & step 2 on GEO-Magnetic Disturbance (GMD) Updated table | August 9, 2013 |
| 3.3 | 1.0 / 8 | Removed HHGT TO reference | August 30, 2013 |
| 3.3 3.4 4.1 4.2 5.3 5.4 5.6 5.7 6.1 7.6 8.1 8.2 8.3 9.1 9.2 10.2 | 1.0 / 9 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 17 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 7 | Updated step 1 and Log Updated step Log Updated step Log Updated step Log Updated step 4, Planned Outage, Forced Outage and added Log Updated step Log Updated step Log Updated step 1 and added Log Updated step Update Report, TRE Event Reporting changed to Event Analysis Report and event list updated, and NERC and DOE Reporting updated Added step Issues and updated Log Updated step 3 and added Log Updated step 3, 5 and added Log Updated step 3 Updated step Log Updated steps Log Added step 4 and updated Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 4.1 6.1 7.2 7.3 | 1.0 / 7 1.0 / 18 1.0 / 5 1.0 / 6 | Updated for NOGRR125 & OK to test on Coordinated Reactive Tests Updated NERC and DOE Reporting Updated EEA Implementation Checklist Updated EEA Restoration Checklist | January 29, 2014 |