- Power Operations Bulletin # 659

ERCOT has posted/revised the DC Tie Manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.3	Approve E-Tags for the CFE DC Ties

Procedure Purpose: An E-Tag received in the OATI WebTrans regarding DC Tie flows into or out of ERCOT will be validated for accuracy.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.1 (3)(e) |  |  |  |
| NERC Standard | INT-003-3 R1.2 | INT-005-3 R1 | INT-006-3 R1.1, R1.1.1, R1.1.2, R1.1.3, R1.2 | INT-007-1 R1.3.3 |
|  | INT-009-1 R1 | IRO-005-3.1a R2 | TOP-002-2.1b R5, R9 |  |

| Version: 1 | Revision: 14 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - AEP TO in Corpus Christi is the DC Tie Operator (AEP TO) for the DC_S (Eagle Pass DC Tie) and the DC_L (Laredo VFT) - Sharyland TO in Amarillo is the DC Tie Operator (SHARYLAND TO) for the DC_R (Railroad DC Tie) - All communications will be with the DC-Tie Operator and they will communicate with CFE |
| NOTE | ERCOT will not allow an E-Tag to flow from CFE to SPP or from SPP to CFE. This will require two separate E-Tags. E-Tags are not calculated in our ACE equation, DC Tie schedules are seen by our EMMS as a generator (import) or load (export). |
| NOTE | - ERCOT has analyzed the ramping capability of its Interconnection and is capable of ramping at a greater rate than the maximum ramp rate schedule on any of the DC Ties - The Railroad DC Tie has a 15 MW minimum flow requirement when E-Tags are scheduled - Approximately one hour before start of schedule, notify the ERCOT Transmission & Security Operator with scheduled MW, Tie and direction of flow and duration. |
| NOTE | Automatic validation in WebTrans for each new or updated E-Tag will display ‘pass’ or ‘fail’. The criteria ERCOT uses to validate E-Tags is: - ERCOT Market Information field must have QSE information - TP (Transmission Provider) must have ERCO specified in the Physical Path If either of the above validations fail, the E-Tag will be automatically denied. If you believe an E-Tag failed validation erroneously, the list of approved ERCOT Registered QSE’s can be found at the following website: http://www.ercot.com/mktparticipants/ Select the “List of Market Participants in ERCOT Region”, and then select the DC Tie Scheduling List tab to view the ERCOT Registered QSE’s. If the QSE name is on the list but was denied by WebTrans, approve the E-Tag and inform the ERCOT help desk and OATI help desk if needed. Another point of reference is to view the “QSE Contracts” in WebTrans. Each QSE is associated with each DC-Tie individually. WebTrans Reference Display: Tag Validation Summary Data>QSE Contracts |
| 1 | When a New or Updated E-Tag is received in the WebTrans system: Manually validate the following: - “ERCO” must not be listed as a PSE in the Tag Information - “ERCO” must not be listed as a PSE in the Physical Path - Time Zone should be CS (central standard), CD (central daylight) or CP (central prevailing) during time change - “Transaction type” must be “Energy or Normal” - AEPT must be included as the TP (Transmission Provider) in the Physical Path and ERCO as a Scheduling Entity on the AEPT TP row in the Physical Path for DC_S or DC_L - SULP must be included as the TP in the Physical Path and ERCO as a Scheduling Entity on the SULP TP row in the Physical Path for the DC_R - There are no losses (MW) in the ERCOT Control Area. This should be to or from AEPT or SULP as shown on the “Energy and Transmission Profiles” section - Tags are permitted to be submitted within the COP time frame (up to seven days in advance), but a separate tag for each day must be submitted and the Start Time and Stop Time MUST NOT cross the midnight hour. IF: - Any of the above information is incorrect on the E-Tag; THEN: - Deny the E-Tag, otherwise proceed below. WebTrans Reference Displays: Scheduling>Interchange>BTF Checkout |
| 2 | The ramp rate for DC_R will be 50 MW per minute due to reactive issues on the CFE side. DC_L and DC_S have no ramp limitations. - Ramp Duration should be filled out on DC_R E-Tags only - Deny any Railroad DC-Tie E-Tag that does not have a ramp duration entered - DC_L and DC_S ramp duration can remain blank which is the default for a 10 minute ramp. |
| 3 | The Railroad DC Tie has a 15 MW minimum flow requirement. Ensure the net of the E-Tags are not less than 15 MW. |
| NOTE | Webtrans and MMS (ABB) utilize a different sign convention (positive and negative numbers) between the two systems. WebTrans: - (-) Imports - (+) Exports MMS: - (+) Imports - (-) Exports |
| COP E-Tags | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> DSI Data Processes> DSI DC Tie Schedule Market Operation>Reliability Unit Commitment> HRUC Displays> DSI Displays> External Input Data> MI COP - Verify that E-tags are being imported into the MMS by going to the MI COP display and filter ‘ERCOT’ as the QSE name |

## 3.6	Adjustment of CFE DC Ties

Procedure Purpose: The process to approve or deny adjustments to E-Tags.

| Protocol Reference | 4.4.4 | 4.4.4.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 |  |  |  |
| NERC Standard | INT-004-2 R1 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Imports |  |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the n scheduled interchange. |
| 1 | IF requested by either DC Tie Operator, AEP TO or SHARYLAND TO, checkout the net scheduled interchange value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |
| ### Exports |  |
| 1 | Notify the ERCOT Transmission & Security Operator when E-Tag Net Export adjustments are greater than 100 MW during the Adjustment Period. |
| NOTE | E-Tag adjustments must be in an “Approved” or “Implemented” status to be calculated into the net scheduled interchange. |
| 2 | IF requested by either DC Tie Operator, AEP TO or SHARYLAND TO, checkout the net scheduled interchange value for each CFE DC Tie affected by E-Tag adjustments. WebTrans Reference Display: Realtime Summary |

## 3.7	DC Tie Trips or Derates

Procedure Purpose: The process when a DC Ties trip or is de-rated.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | INT-004-2 R1 | INT-005-3 R1.1 | INT-010-1 R2 |  |

| Version: 1 | Revision: 11 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### CFE DC Ties |  |
| 1 | IF: - Any of the CFE DC Ties trip, THEN: - ERCOT will have the responsibility to curtail the E-Tags. - Curtail the E-Tags for the Tie that tripped (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - . |
| 2 | Once the DC Tie that tripped is operational, re-load the curtailed E-Tag(s), if applicable: - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Notify the appropriate DC Tie Operator. |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because CFE or DC Tie Operator did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Notify the appropriate DC Tie Operator. If reload fails the second time stop trying and keep tag curtailed. |
| Post Message | WHEN: - The Eagle Pass, Railroad, or Laredo DC Tie trips; THEN: - Post message on MIS Public, - Use the canned message, - End time will be unknown, put through the end of the day |
| Cancel Message | WHEN: - The DC Tie returns to service; THEN: - Cancel message |
| ### CFE DC Tie Derates |  |
| Post Message | IF: - Notified that any of the CFE DC Ties are temporally derated; THEN: - Post message on MIS Public; - Select Create Freeform Notice, - Operational Information, - Low priority, - Public. Typical MIS Posting: “ERCOT has been notified that the [TIE] DC Tie has been derated to [AMOUNT] MW Import/Export due to [REASON] until further notice.” |
| Cancel Message | WHEN: - Tie returned to normal service; THEN: - Cancel message |
| ### SPP DC TIES |  |
| 1 | IF: - Any of the SPP DC Ties trip, THEN: - SPP has the responsibility to curtail the E-Tags. |
| Post Message | WHEN: - The East or North DC Tie trips; THEN: - Post message on MIS Public, - Use the canned message, - End time will be unknown, put through the end of the day |
| Cancel Message | WHEN: - Tie returned to service; THEN: - Cancel message |
| ### SPP DC Tie Derates |  |
| Post Message | IF: - Notified that any of the AEP DC Ties are temporally derated; THEN: - Post message on MIS Public; - Select Create Freeform Notice, - Operational Information, - Low priority, - Public. Typical MIS Posting: “ERCOT has been notified that the [TIE] DC Tie has been derated to [AMOUNT] MW Import/Export due to [REASON] until further notice.” |
| Cancel Message | WHEN: - Tie returned to normal service; THEN: - Cancel message |

## 3.9	Managing Daily Inadvertent Energy for the Laredo VFT and Eagle Pass DC Ties

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.2b R12.1 | INT-003-3 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 8 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored each hour during the day to ensure inadvertent flows do not accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (EGPS_DC or LAR_VFT). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator, inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| 1 | Before the start of the hour, confirm the net-scheduled value for each DC Tie with the DC Tie Operator (AEP TO). If there is a discrepancy, go over each E-Tag ID and MW amount for the affected DC Tie(s). - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator (AEP TO) for each DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 10 MWH, overwrite the actual value in the WebTrans system with a whole number. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Open an ERCOT Help Desk ticket for EMMS Production to investigate problems with the meter information and notify Shift Supervisor. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Interchange>ATF Checkout |
| 3 | After midnight, each day, check out the total scheduled and actual values for each DC Tie with the DC Tie Operator, AEP TO: IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_L and DC_S - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF Checkout |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies. If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and send email to shiftsupv@ercot.com. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Checkout Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for each the DC_S and DC_L DC Ties and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

## 3.10	Managing Daily Inadvertent Energy for the Railroad Tie

Procedure Purpose: To track any difference between the schedule net interchange and the actual net interchange.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8(1) |  |  |  |
| NERC Standard | BAL-005-0.2b R12.1 | INT-003-3 R1.2 | INT-009-1 R1 |  |

| Version: 1 | Revision: 0 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| OVERVIEW | Inadvertent Energy flows across the DC Ties need to be monitored each hour during the day to ensure inadvertent flows do not accumulate. |
| NOTE | If the proper information is not listed when an E-Tag is created and submitted, the E-Tag may not be displayed correctly in all WebTrans displays. Examples include, but are not limited to a PSE not using the proper POR/POD in the Physical Path (ROAD_DC). |
| CAUTION | If the E-Tag is created and submitted without any or all information in the above NOTE OR any other circumstance so that the E-Tag can not be seen by either ERCOT or the DC Tie Operator (SHARYLAND TO), inadvertent energy will be created. The E-Tag should be curtailed to zero (0). |
| 1 | Before the start of the hour, confirm the net-scheduled value for the DC Tie with the DC Tie Operator, SHARYLAND TO. If there is a discrepancy, go over each E-Tag ID and MW amount. - If an E-Tag can not be seen in WebTrans OR by the DC Tie Operator, work to resolve the problem OR ensure the E-Tag is curtailed to zero (0). WebTrans Reference Displays: Scheduling>QSE Summary Scheduling>BTF Display |
| 2 | Check out the Actual SCADA data values for the previous hour with the DC Tie Operator, SHARYLAND TO for the Railroad DC Tie. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by less than 10 MWH, overwrite the actual value in the WebTrans system with a whole number. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is known (database load, loss of ICCP, etc.), overwrite the actual value in the WebTrans system. Log the appropriate information. - If ERCOT’s actual values are different from the DC Tie Operator’s actual values by 10 MWH or more and the reason is unknown; ERCOT and the DC Tie Operator will initiate an investigation. Log the appropriate information (time, date, total MW difference, DC Tie, name of the DC Tie Operator and any other relevant information). Open an ERCOT Help Desk ticket for EMMS Production to investigate problems with the meter information and notify Shift Supervisor. WebTrans Reference Displays: Scheduling>Inadvertent>Tie Data Scheduling>Interchange>ATF Checkout |
| 3 | After midnight, each day, check out the total scheduled and actual values for the Railroad DC Tie with the DC Tie Operator, SHARYLAND TO: IF: - Both parties agree on the Scheduled In and Out values and on the Actual In and Out values; THEN: - Prepare report for the DC_R - Select “[Tie name]” on the CA/Interface - Select “Schedule” on the “Checkout” dropdown - Check the bottom box on the totals row in Column C - Click the “Apply Checkout” button - Proceed to Step 5. WebTrans Reference Display: Scheduling>Interchange>ATF Checkout |
| 4 | If there is a disagreement on the total scheduled and/or actual values with the DC Tie Operator, verify the values for each hour as necessary to find the discrepancy. An effort should be made to work out all discrepancies. If the discrepancy is with the scheduled values: - Check the box in Column C for each hour that ERCOT is in agreement with the DC Tie Operator for the scheduled value. - Leave the box unchecked in Column C for each hour where there is a discrepancy with a scheduled value and it can not be worked out with the DC Tie Operator. - Click the “Apply Checkout” button. - Log the appropriate information and send email to shiftsupv@ercot.com. If the discrepancy is with an actual value, change the ERCOT value to match the DC Tie Operator’s value. WebTrans Reference Displays: Scheduling>Interchange>ATF Checkout Scheduling>Inadvertent>Tie Data |
| 5 | Create an Excel file for the DC-R Tie and email to the following: - CFE DC-Tie Inadvertent - cenal.transaccionesinter@cfe.gob.mx |

## 3.11	Managing Inadvertent Energy Payback

Procedure Purpose: To provide communication contacts and information prior to starting and ending inadvertent payback.

| Protocol Reference | 6.5.4 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.8 (3) |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Payback will only be planned when there is room on the DC Tie(s). Energy schedules of market participants will supersede any inadvertent payback bias. Payback plans are implemented by each of the DC Tie Operators. They will bias the DC Tie(s) and create inadvertent in the opposite direction. This will reduce the inadvertent values. |
| NOTE | When inadvertent needs to be paid back in either direction, the ERCOT Operator will receive the payback plan information from the Manager of System Operations and/or Control Room Operations Manager. |
| 1 | - Prior to the start of the Payback plan, call the appropriate DC Tie Operator and confirm the start time, hourly MW amount, and direction of the payback plan. - If payback is planned across the DC_L, verify the transmission path (230kV or 138kV). |
| 2 | Prior to the Payback plan stopping, call the appropriate DC Tie Operator and confirm the agreed upon stop time. |

## 3.12	Loss of E-Tagging

Procedure Purpose: Contingency plan for loss of E-tagging capability.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Loss of ERCOT E-Tagging |  |
| 1 | If the WebTrans system goes down for an unknown reason (i.e. maintenance), contact the ERCOT Operator at the primary control center to check on their connectivity. If their system is also down, contact the ERCOT help desk (ERCOT HELPDESK) to see if the issue is on our end. If issue is not on the ERCOT end, contact the OATI help desk (OATI HELPDESK) to see if the issue is on their end. |
| 2 | Determine the estimated down time, if longer than 30 minutes, notify the SPP Tariff Operator (SPP Tariff) and the DC Tie Operators (AEP DC TIE, AEP TO, and SHARYLAND TO). |
| 3 | Post message on MIS Public: Typical MIS Posting: “The ERCOT E-tagging system is down and no new schedules will be accepted across the DC Ties at this time”. |
| 4 | No new E-tags will be accepted, only curtailments: - Coordinate with the SPP Tariff Operator (SPP Tariff) and the appropriate DC Tie Operator - Notify Real-Time Operator to determine if SCED needs to be manually executed for curtailments |
| NOTE | Before-the-fact and after-the-fact check outs will not be available |
| 5 | Once the WebTrans system is available, confirm SPP Tariff (SPP Tariff) and the DC Tie Operators availability. If available for all parties: - Update the MIS Public posting by sending a “Notice Cancellation” - If curtailments were made while the WebTrans system was down, ensure E-tags are updated |
| ### Loss of DC Tie Operator E-Tagging |  |
| 1; If the E-Tagging system is down for one of the DC Tie operators and not ERCOT, no new schedule can be accepted.. 2; Post message on MIS Public: Typical MIS Posting: “The E-tagging system is down for the [state DC Tie Operator] and no new schedules will be accepted across the [state DC Tie(s)] at this time”.. 3; Once E-tagging system is operational, cancel message.. |

## 4.1	ERCOT Declares EEA 1

Procedure Purpose: Steps to perform when ERCOT declares an Energy Emergency Alert (EEA) 1.

| Protocol Reference | 6.5.9.4 | 6.5.9.4.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3 | 4.5.3.3 |  |  |
| NERC Standard | EOP-001-0.1b R1, R3.1, R4.2, R7.2 | EOP-002-3.1 R1, R2, R4, R6.4, R6.6 | INT-004-2 R1 |  |
|  | IRO-005-3.1a R4, R10 |  |  |  |

| Version: 1 | Revision: 12 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie Operator for the Laredo and Eagle Pass DC Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - The DC Tie Operator for the Railroad DC Tie can be reached using the Turrent phone button labeled (SHARYLAND TO), page 14 - AEP un-regulated QSE is responsible for assets associated with unregulated retail operations (SQ2, SQ3, and SQ4 sub-QSEs). The VDI for emergency energy to and from CFE will be given to this QSE. They can be reached using the Turret phone button labeled (AEP UNREG QSE), page 4 |
| NOTE | The DC Tie Operator for Laredo and Eagle Pass (AEP TO) has agreed to help in the coordination between ERCOT/Sharyland and CFE concerning the Railroad DC Tie during emergency operations. |
| EEA | When notified by Hotline that ERCOT has implemented EEA 1, proceed with this procedure. |
| Comisión Federal de Electricidad (CFE) |  |
| 1a | IF: - There are export schedules on the Laredo or Eagle Pass DC Tie; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC Tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 1b | IF: - There are export schedules on the Railroad DC Tie; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (SHARYLAND TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (SHARYLAND TO): This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the Railroad DC-Tie due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | IF: - There is export inadvertent payback flowing to CFE from Laredo or Eagle Pass DC Ties; THEN: - Stop inadvertent payback by contacting the DC Tie Operator (AEP TO) and instruct them to make notification to CFE. Typical Script to DC Tie Operator (AEP TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC Tie] be ramped out. Please notify CFE.” |
| 2b | IF: - There is export inadvertent payback flowing to CFE from Railroad DC Tie; THEN: - Stop inadvertent payback by contacting the DC Tie Operator (SHARYLAND TO) and instruct them to notify CFE. Typical Script to DC Tie Operator (SHARYLAND TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on Railroad DC Tie be ramped out. Please notify CFE.” |
| 3a | Contact DC Tie Operator (AEP TO) and request them to contact CFE to inquire about the availability of emergency energy on the Laredo and Eagle Pass DC Ties. IF: - Emergency energy is available; THEN: - Request the DC Tie Operator to ramp the appropriate DC Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP un-regulated QSE (AEP UNREG QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP un-regulated QSE (AEP UNREG QSE) that VDI has been issued. |
| 3b | Contact DC Tie Operator (SHARYLAND TO) and request them to contact CFE to inquire about the availability of emergency energy on the Railroad DC Tie. IF: - Emergency energy is available; THEN: - Request the DC Tie Operator to ramp the DC Tie with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP un-regulated QSE (AEP UNREG QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP un-regulated QSE (AEP UNREG QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| Turret Phone | - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - SPP Tariff operator can be reached using the Turret phone button labeled (SPP Tariff), page 2 - The DC Tie Operator for the SPP DC-Ties can be reached using the Turret phone button labeled (AEP DC TIE), page 19 - AEP regulated QSE is responsible for assets associated with regulated retail operations (Main and SQ1sub-QSE). The VDI for emergency energy to and from SPP will be given to this QSE. They can be reached using the Turret phone button labeled (AEP REG QSE), page 4 |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC Ties. This is the reason for the two different procedures. - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour. |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA 1 status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1”. |
| 2b | IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) Typical script to DC Tie Operator (AEP DC TIE): This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC Tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag (see Desktop Guide DC Tie Desk Section 2.5) - Notify the Shift Supervisor |
| 3b | IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC-Tie Operator (AEP DC TIE). Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1 and is requesting the inadvertent payback on [name DC Tie] go to zero.” |
| 4b | IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC Tie Operator (AEP DC TIE) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | IF: - The SPP DC Ties are not at maximum import into ERCOT; THEN: - Notify the SPP Tariff desk (SPP Tariff) to determine the availability of transmission service for an EEA 1 schedule. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. Is there transmission service available on either DC Tie to start a schedule into ERCOT?” IF: - No current hour transmission service is available; THEN: - Do NOT proceed and make log entry - Notify Shift Supervisor IF: - Status changes from EEA 1 to EEA 2 or 3; THEN: - Proceed to Section 4.2 |
| 6b | IF: - Transmission service is available; THEN: - Notify AEP regulated QSE (AEP REG QSE): Typical Script to AEP regulated QSE (AEP REG QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. SPP Tariff desk reports there is [amount] of available transmission service on the East tie and [amount] of available transmission service on the North tie. Do you have any available capacity up to that amount for an EEA 1 schedule?” IF: - No available capacity; THEN: - Make log entry and do not proceed - Notify Shift Supervisor. IF: - Capacity is available; THEN: - Request AEP REG QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP regulated QSE (AEP REG QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you” NOTIFY: - DC Tie Operator (AEP DC TIE): Typical Script for DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1. AEP REG QSE will be submitting the transmission request and the E-Tag (s) for an EEA 1 schedule. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP REG QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP REG QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency into ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP regulated QSE (AEP REG QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 1 to EEA 2. Thank you”. If moved to EEA 2 or 3 proceed to section 4.2, ERCOT Declares EEA 2 or 3. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5) - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all actions taken. |

## 4.2	ERCOT Declares EEA 2 or 3

Procedure Purpose: Steps to secure emergency energy across the DC Tie(s) in an Energy Emergency Alert (EEA) 2 or 3.

| Protocol Reference | 6.5.9.4 | 6.5.9.4.3 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0.1b R1, R3.1, R4.2, R7.2 | EOP-002-3.1 R1, R2, R4, R6.4, R6.6 | INT-004-2 R1 | INT-010-1 R3 |
|  | IRO-005-3.1a R4, R10 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie Operator for the Laredo and Eagle Pass ties can be reached using the Turret phone button labeled (AEP TO), page 4 - The DC Tie Operator for the Railroad DC Tie can be reached using the Turrent phone button labeled (SHARLAND TO), page 14 - AEP un-regulated QSE is responsible for assets associated with unregulated retail operations (SQ2, SQ3, and SQ4 sub-QSEs). The VDI for emergency energy to and from CFE will be given to this QSE. They can be reached using the Turret phone button labeled (AEP UNREG QSE), page 4 |
| EEA | When notified by Hotline that ERCOT has declared EEA 2 or 3, proceed with this procedure. |
| Comisión Federal de Electricidad (CFE) |  |
| 1a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There are export schedules on the Laredo or Eagle Pass DC-Ties; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (AEP TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (AEP TO): This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 1b | IF: - There are export schedules on the Railroad DC Tie; THEN: - Curtail (see Desktop Guide DC Tie Desk Section 2.3 or 2.4) - Contact DC Tie Operator (SHARYLAND TO) with curtailment information and instruct them to make notification to CFE. Typical script to DC Tie Operator (SHARYLAND TO): This is ERCOT operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the Railroad DC Tie due to ERCOTs EEA status. Please ramp the Tie(s) accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback flowing to CFE from the Laredo and/or Eagle Pass DC Ties; THEN: - Stop inadvertent payback by contacting the DC Tie Operator (AEP TO) and instruct them to make notification to CFE. Typical Script to DC Tie Operator (AEP TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on [name DC-Tie] be ramped out. Please notify CFE.” |
| 2b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback flowing to CFE from the Railroad DC Tie; THEN: - Stop inadvertent payback by contacting the DC Tie Operator (SHARYLAND TO) and instruct them to make notification to CFE. Typical Script to DC Tie Operator (SHARYLAND TO): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA 1, we are requesting the inadvertent payback on the Railroad DC-Tie be ramped out. Please notify CFE.” |
| 3a | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. Contact DC Tie Operator (AEP TO) and request them to contact CFE to inquire about the availability of emergency energy on the Laredo and Eagle Pass DC Ties. IF: - Emergency energy is available; THEN: - Request the DC Tie Operator to ramp the appropriate DC-Tie(s) with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP un-regulated QSE (AEP UNREG QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP un-regulated QSE (AEP UNREG QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| 3b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4.1 ERCOT Declares EEA 1. Contact DC Tie Operator (SHARYLAND TO) and request them to contact CFE to inquire about the availability of emergency energy on the Railroad DC Tie. IF: - Emergency energy is available; THEN: - Request the DC Tie Operator to ramp the DC-Tie with the amount of emergency energy that CFE is able to send, - Notify Shift Supervisor - Issue AEP un-regulated QSE (AEP UNREG QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP un-regulated QSE (AEP UNREG QSE) that VDI has been issued. - Continue on with the Southwest Power Pool (SPP) section of this procedure. |
| Southwest Power Pool (SPP) |  |
| Turret Phone | - SPP Reliability Coordinator can be reached using the Turret phone button labeled (SPP RC), page 2 - SPP Tariff Operator can be reached using the Turret phone button labeled (SPP Tariff), page 2 - The DC Tie Operator for the SPP DC Ties can be reached using the Turret phone button labeled (AEP DC TIE), page 19 - AEP regulated QSE is responsible for assets associated with regulated retail operations (Main and SQ1 sub-QSE). The VDI for emergency energy to and from SPP will be given to this QSE. They can be reached using the Turret phone button labeled (AEP REG QSE), page 4 |
| NOTE | - During an EEA 1, only non-firm transmission service is available for the North and East DC Ties. For EEA 2 or 3, emergency transmission service is available for the North and East DC Ties. This is the reason for the two different procedures - Transmission Service is usually only good for an hour at a time. Keep AEP informed so they can make the proper submittals hour to hour |
| 1b | Notify the SPP Reliability Coordinator (SPP RC) of ERCOT’s EEA status: Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Thank you.” |
| 2b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There are export E-tags across the DC Ties (does not apply to DC_N schedules which are identified by “OKLA” in the Physical Path on the tag); THEN: - Curtail (usually done one hour at a time) (see Desktop Guide DC Tie Section 2.3 or 2.4). Typical script to DC Tie Operator (AEP DC TIE): This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC Tie name] due to ERCOTs EEA status. Please ramp the Tie(s) accordingly. Please repeat this back to me. That is correct. Thank you.” IF: - SPP provides a reliability reason for NOT approving the curtailing of the E-Tag(s); THEN: - Re-instate the E-Tag, - Notify the Shift Supervisor. |
| 3b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - There is export inadvertent payback across the DC Ties; THEN: - Stop export inadvertent payback by notifying the DC Tie Operator (AEP DC TIE). Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3] and is requesting the inadvertent payback on [name DC-Tie] go to zero.” |
| 4b | Complete this step only if EEA 1 was skipped, otherwise this was performed in 4. 1 ERCOT Declares EEA 1. IF: - The DC_N deadband is active and exporting; THEN: - Notify the DC Tie Operator (AEP DC TIE) to request they temporarily turn the deadband into ERCOT. Typical Script to DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting that the deadband be turned into ERCOT while we are in EEA”. |
| 5b | Complete this step if in EEA 1 there was no non-firm transmission service available or EEA 1 was skipped. Notify the SPP Tariff desk (SPP Tariff) to determine the availability of emergency transmission service across the SPP DC Ties. Typical Script to SPP Tariff (SPP Tariff): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. Is there emergency transmission service available across the DC Tie(s)?” IF: - No emergency transmission service is available, THEN: - Do NOT proceed and make log entry. - Notify Shift Supervisor |
| 6b | IF: - Emergency transmission service is available; THEN: - Request emergency energy from AEP regulated QSE (AEP REG QSE) Typical Script to AEP regulated QSE (AEP REG QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. SPP Tariff desk reports there is [amount] of available emergency transmission service on the East tie and [amount] of available emergency transmission service on the North tie. Do you have any available capacity up to that amount for emergency assistance?” IF: - No available capacity, THEN: - Make log entry and do not proceed. IF: - Capacity is available; THEN: - Request AEP REG QSE to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Typical Script to AEP regulated QSE (AEP REG QSE): “This is ERCOT Operator [first and last name]. At [time], ERCOT requests you to arrange for the submission of the transmission request and the E-tag(s) for the available capacity. Please repeat this back to me. That is correct. Thank you.” NOTIFY: - DC Tie Operator (AEP DC TIE): Typical Script for DC Tie Operator (AEP DC TIE): “This is ERCOT Operator [first and last name]. At [time], ERCOT declared EEA [2 or 3]. AEP REG QSE will be submitting the transmission request and the E-Tag (s) for emergency energy into ERCOT. Thank you”. NOTIFY: - Shift Supervisor |
| NOTE | The AEP REG QSE does not submit the transmission service request or the E-tag; however they are responsible for notifying their hourly desk to get them submitted. |
| 7b | Issue VDI to AEP REG QSE: - Choose QSE level tab - Choose QAEPSC for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT” and which DC Tie(s) in Other Information - End time will be the same as initiation time (back office will take care of the rest) - Notify AEP regulated QSE (AEP REG QSE) to acknowledge the VDI |
| 8b | WHEN: - EEA status changes; THEN: - Notify SPP Reliability Coordinator (SPP RC) Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT moved from EEA 2 to EEA 3. Thank you”. IF EEA 1 has ended continue with this procedure. |
| 9b | WHEN: - EEA has ended; THEN: - Notify SPP Reliability Coordinator (SPP RC); Typical Script to SPP Reliability Coordinator (SPP RC): “This is ERCOT Operator [first and last name]. At [time], ERCOT has ended EEA 1. Thank you.” Take appropriate actions for the following: - End Emergency Energy - Reload any E-Tag (see Desktop Guide DC Tie Section 2.5), - Re-start inadvertent payback - Have deadband turn back into SPP |
| LOG | Log all action taken |

## 4.3	Emergency Energy to CFE

Procedure Purpose: Provide Emergency Energy to CFE across the DC Ties.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-0.1b R1 | INT-010-1 R3 |  |  |

| Version: 1 | Revision: 11 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | If CFE requests emergency energy, no emergency notification needs to be declared by ERCOT. |
| 1 | IF: - Notified by the ERCOT Transmission & Security Operator or a DC Tie Operator, AEP TO or SHARYLAND of CFEs emergency situation; THEN: - Identify if CFE has export schedule(s) that can be curtailed, if CFE has no exports, proceed to step 2, - Curtail the appropriate E-Tag(s) (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact the appropriate DC Tie Operator when curtailment is complete and instruct them to make notification to CFE. Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC tie name] due to CFEs emergency situation. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | IF: - CFE has export inadvertent payback flowing into ERCOT; THEN: - Notify appropriate DC Tie Operator to stop inadvertent payback Typical Script to appropriate DC Tie Operator: “This is ERCOT Operator [first and last name]. At [time], ERCOT is requesting the inadvertent payback being imported to ERCOT on [name DC Tie] be ramped out due to CFEs emergency situation. Please repeat this back to me. That is correct. Thank you.” |
| 3 | IF: - Notified by the ERCOT Transmission & Security Operator or a DC Tie Operator that CFE is requesting emergency energy; THEN: - Verify with the ERCOT Transmission & Security Operator that sending emergency energy to CFE will not cause a reliability issue for ERCOT, IF: - ERCOT is able to send CFE emergency energy; THEN: - Request the appropriate DC Tie Operator to ramp the appropriate DC Tie with the amount of emergency energy that ERCOT is able to send Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT will send [amount] of emergency energy on [DC Tie(s)] Please ramp Ties accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” - Notify Shift Supervisor - Issue AEP un-regulated QSE (AEP UNREG QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to CFE” and which DC Ties in “Other Information” - End time will be the same as initiation time. - Notify AEP un-regulated QSE (AEP UNREG QSE) to acknowledge the VDI. |
| 4 | WHEN: - Notified that CFEs emergency has ended; THEN: - Perform/verify the following: - End Emergency Energy, if appropriate - Re-load E-Tag(s), if appropriate (see Desktop Guide DC Tie Section 2.5) - Restart import inadvertent payback, if appropriate |
| Log | Log all actions taken. |

## 4.5	Emergency Condition in the Areas of the CFE DC Ties

Procedure Purpose: The process to curtail E-Tags for the CFE Ties and request emergency energy, if needed.

| Protocol Reference | 4.4.4 | 6.5.9.4(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.3 |  |  |  |
| NERC Standard | EOP-001-0.1b R3.1, R4.2 | INT-004-2 R1 | INT-005-3 R1.1 | INT-010-1 R2 |

| Version: 1 | Revision: 14 | Effective Date: February 25, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Turret Phone | - The DC Tie Operator for the Laredo or Eagle Pass DC Ties can be reached using the Turret phone button labeled (AEP TO), page 4 - The DC Tie Operator for the Railroad DC Tie can be reached using the Turret Phone button labeled (SHARYLAND TO), page 14 - AEP un-regulated is the QSE receiving the VDI for emergency energy is issued to and from CFE. They can be reached using the Turret phone button labeled (AEP UNREG QSE), page 4 |
| NOTE | DC Tie Load shall neither be curtailed during the Adjustment Period, nor for more than one hour at a time, except for the purpose of maintaining reliability. |
| NOTE | When ERCOT curtails an E-Tag whether to zero (0) or a specific MW amount, only CFE needs to approve the change. Curtailments will be automatically approved by them. |
| ### Emergency Condition within ERCOT |  |
| 1 | When ERCOT is in an Emergency, it may be necessary to curtail export E-Tags using the Last-in-First-Out (LIFO). IF: - Notified by the ERCOT Transmission & Security Operator of the need to curtail (which includes reductions) exports on a specific DC Tie; THEN: - Verify the MW amount the E-tag needs to be curtailed, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4) - Notify the appropriate DC Tie Operator with curtailment information and instruct them to ramp the DC Tie and to notify CFE - Notify PSE with curtailment information and reason. Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. ERCOT has curtailed E-Tag(s) [tag number(s)] on the [DC Tie name] to [state MW amount] starting at [xx:xx] due to an Emergency condition within ERCOT. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified by the ERCOT Transmission & Security Operator that the E-Tags can be re-loaded: - Notify PSE with reload information - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Section 2.5) - Notify the appropriate DC Tie Operator to approve the re-loaded E-Tag and instruct them to notify CFE. Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. At [xx:xx], the Emergency conditions within ERCOT has ended and the E-Tag(s) [tag number(s)] have been re-loaded for [xx:xx]. Please notify CFE to approve re-load. Please repeat this back to me. That is correct. Thank you.” |
| 3 | IF: - The re-loaded E-Tag(s) go passive deny because DC Tie Operator or CFE did not approve the E-Tag(s) in the allotted time; THEN: - Re-load the E-Tag(s) again, AND - Notify appropriate DC Tie Operator. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission & Security Operator there is need for emergency energy across a specific DC Tie; THEN: - Request the appropriate DC-Tie Operator to inquire about the availability of emergency energy on [name DC Tie(s)] Typical Script to appropriate DC Tie Operator: “This is ERCOT Operator [first and last name] At [xx:xx] ERCOT declared an Emergency, we are requesting you to contact CFE to inquire about the availability of emergency energy into ERCOT on [name DC Tie(s)] IF: - Emergency Energy is available; THEN: - Request the appropriate DC Tie Operator to ramp the appropriate DC Tie(s) with the amount of emergency energy that CFE is able to send, - Issue AEP un-regulated QSE (AEP UNREG QSE) a VDI for the emergency energy: - Choose QSE level tab - Choose QAEPS2 for Participant Name - Choose PROVIDE EMERGENCY POWER FROM DC TIE for Instruction Type - State “Emergency Energy to ERCOT on [DC Tie(s)] in Other Information - End time will be the same as initiation time (back office will take care of rest) - Notify AEP un-regulated QSE (AEP UNREG QSE) that VDI has been issued. IF: - Emergency Energy is not available; THEN: - Notify ERCOT Transmission & Security Operator |
| LOG | Log all actions taken. |
| ### Emergency Condition within CFE |  |
| NOTE | On the CFE side of the Railroad DC Tie, there is an automatic runback scheme that runs back the DC Tie under CFE contingency conditions. When this occurs, and notification is made by the DC Tie Operator; follow the procedure below. |
| 1 | Due to reliability issues within CFE it may be necessary to curtail import E-Tag(s) for them. IF: - Notified by the ERCOT Transmission & Security Operator or one of the DC Tie Operators of the need to curtail imports on specific CFE DC Ties; THEN: - Verify the MW amount and time of the curtailment, - Curtail the appropriate E-Tag to the MW amount needed (see Desktop Guide DC Tie Section 2.3 or 2.4), - Contact the appropriate DC Tie Operator when curtailment is complete and instruct them to ramp the DC Tie and make notification to CFE - Notify PSE with curtailment information and reason. Typical script to appropriate DC Tie Operator: This is ERCOT Operator [first and last name]. At [xx:xx] ERCOT has curtailed E-Tag [tag number] on the [DC Tie name] to [state MW amount] due to reliability issues within CFE. Please ramp the Tie accordingly and notify CFE. Please repeat this back to me. That is correct. Thank you.” |
| 2 | Once notified that CFEs reliability issue has been resolved and E-Tags can be re-loaded: - Notify PSE with reload information - Re-load curtailed E-Tag(s) (see Desktop Guide DC Tie Desk Section 2.5), - Notify the appropriate DC Tie Operator to approve the re-loaded E-Tag and to notify CFE. |
| 3 | IF: - The re-loaded E-Tag goes passive deny because a DC Tie Operator or CFE did not approve the E-Tag in the allotted time; THEN: - Re-load the E-Tag again, AND - Notify the appropriate DC Tie Operator. If reload fails the second time stop trying and keep tag curtailed. |
| 4 | IF: - Notified by the ERCOT Transmission & Security Operator of the need for emergency energy; THEN: - Proceed and follow step 3 in section 4.3, Emergency Energy to CFE. |
| LOG | Log all actions taken. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 27, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 16, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | June 27, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 9, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 30, 2010 |
| 3.1 3.3 3.12 3.13 3.14 3.16 3.17 4.1 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 1 Updated step 1 Updated step 1 and added Log Updated step 4 Updated step 3 Updated step 1 and added Log Updated step 3 Updated Constant Frequency, Respond to QSE’s, Stability Limits Reached and Thermal Limits Reached | December 1, 2010 |
| 2.3 3.4 4.1 4.2 4.3 | 1.0 / 0 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 1 | Added new procedure Updated step 1 Updated steps “Constant Frequency”, “QSE Hotline Call”, “TO Hotline Call”, “Respond to QSEs” “Respond to TOs”, “Stability Limits” and added “Nuclear Plants” Updated Note and “Additional Operators” Updated Hotline in “Notifications” | January 31, 2011 |
| 2.3 3.1 3.2 3.3 3.7 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 4.9 | 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 - / 2 1.0 / 2 - / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 3 - / 2 1.0 / 2 | Updated NXT Test Updated 4th Note and step 1 Updated step 2 Updated 5th note, step 1, deleted step 4 and 6th Note Updated all sections Section number changed from 3.12 and updated all steps Section number changed from 3.13 and updated all steps Section number changed from 3.14 and updated all steps Section number changed from 3.15 and updated all steps Section number changed from 3.16 and updated step 1 Section number changed from 3.17 and updated step 1 Section number changed from 4.1 & updated multiple steps Section number changed from 4.2 & Note Section number changed from 4.3 | March 25, 2011 |
| 1.1 2.3 3.1 3.2 3.3 3.4 3.5 3.6 3.7 3.8 3.9 3.10 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 1 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 1 1.0 / 1 - / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 3 | Updated text Updated step “Beginning of each Shift” Updated 1st & 3rd note and step 1, deleted 2nd note and added 5th note Updated 1st note and step 2 Updated 1st & 4th note, step 1 & 2, deleted 2nd and added 5th note Updated 1st & step 1 Updated steps 1, 2 and 3 Updated “Import” step 1 and “Export” steps 1 & 2 Updated all sections Updated all sections Updated all sections Updated 1st & 2nd note and step 1 and 2 Updated 1st note and step 1 Updated 1st note Updated 1st note Updated step 3 Updated step 1 Updated step 2 Updated step QSE Hotline Call Updated step 1 in Watch and Emergency Notice | April 22, 2011 |
| 3.1 3.2 3.3 3.4 3.5 3.6 3.73.8 3.9 3.10 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.9 | 1.0 / 4 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 31.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 4 - / 5 1.0 / 4 | Updated all steps Updated all steps Updated all steps Updated step 1 Updated step 1, 2, 3 & added 2nd note Updated step 1 and 2 Updated all steps Updated all steps Updated all steps Updated 3rd note and step 1 Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated step 1 Updated steps 2 & 3 Updated steps Call in Additional Operators and Respond to QSEs Updated all steps | June 8, 2011 |
| 3.1 3.3 3.7 3.9 4.2 | 1.0 / 5 1.0 / 5 1.0 / 4 1.0 / 2 1.0 / 5 | Changed 3rd Note to step 1, updated step 1 & 2 Updated step 1 Updated all steps in DC Tie Trips, step 1 in Transmission Issues within ERCOT & step 1 & 2 in Transmission Issues within CFE Updated webtrans references Updated step 1 | June 17, 2011 |
| 3.1 3.3 3.6 3.7 3.9 3.11 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 | 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 2 1.0 / 6 1.0 / 4 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 5 1.0 / 2 1.0 / 5 | Updated 1st Note and step 1 & 2 Updated step 1 Updated all steps Split procedure out, changed title and moved Transmission Issue within ERCOT to 4.5 Updated step 2 Updated steps 2, 4 and 5 Updated step 1, added steps 2 - 4 Updated all steps, added new step 3 Updated Turret phone label for SPP Tariff and all steps Changed section number from 4.4 to 4.3 and updated all steps Changed section number from 4.5 to 4.4 and updated all steps Changed section number from 4.6 to 4.5, updated all steps and moved Transmission Issues from 3.7 to 4.5 Changed section number from 4.7 to 4.6 Changed section number from 4.8 to 4.7 Changed section number from 4.9 to 4.8 and updated step 1 in Watch | July 20, 2011 |
| 2.3 3.1 3.2 3.3 3.6 3.7 3.8 3.9 3.11 4.1 4.2 4.3 4.5 4.6 4.8 | 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 7 1.0 / 4 1.0 / 6 1.0 / 3 1.0 / 4 1.0 / 3 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated step “Beginning of each Shift” Updated 1st note Updated steps 1, 2 & 3 Updated 1st, 4th note and step 1 Updated step 1 “Imports” and step 2 “Exports” Updated Steps 1, 2 and 4 in “CFE DC-Ties” Updated 2nd note and steps 1-3 Updated steps 1-3 Updated steps 1 and 2 Updated all steps Updated all steps Updated all steps Updated all steps Removed reference of Austin Control Room Added projected reserve capacity shortage and Extreme Hot Weather in Watch | September 1, 2011 |
| 3.1 3.3 4.1 4.2 4.3 | 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 6 1.0 / 7 | Updated step 2 Updated step 1 Updated Turret Phone, step 3a in Comision Federal de Electricidad (CFE) and step 5b to implement NPRR 379 Updated Turret Phone and step 3a in Comision Federal de Electricidad (CFE) Updated step 3 | October 1, 2011 |
| 4.6 | 1.0 / 7 | Updated step TO Hotline Call | November 1, 2011 |
| 3.1 3.3 4.6 4.8 | - / 9 1.0 / 9 1.0 / 8 1.0 / 7 | Updated step 2 Updated step 1 Added new section and updated all steps Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.3 4.6 | 1.0 / 1 1.0 / 10 1.0 / 10 1.0 / 9 | Updated Scope Updated step 2 Updated step 1 Updated Hotline call scripts | January 19, 2012 |
| 2.1 2.3 3.1 3.2 3.7 4.1 4.2 4.3 4.5 4.8 | 1.0 / 1 1.0 / 4 1.0 / 11 1.0 / 5 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 7 1.0 / 8 | Added dispatch instructions paragraph Updated Desktop Guide reference Added 3rd Note Changed Shift Engineer to Operations Support Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 2nd Note & all steps 1 – 3 Updated step 1 of Watch | March 1, 2012 |
| 3.1 3.3 3.7 3.8 3.9 4.54.6 4.8 | 1.0 / 12 1.0 / 11 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 10 1.0 / 9 | Updated step 2 Updated 3rd Note and step 1 Added posting and cancelling messages Updated overview Updated overview Updated procedure based on NPRR405 Updated W-N or N-H steps Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather | May 1, 2012 |
| 1.3 3.2 3.8 3.9 4.5 4.6 4.8 | 1.0 / 1 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 11 1.0 / 10 | Removed ERCOT Shift Supervisor paragraph Updated step 1 Updated step 4 Updated step 4 Added step Turret Phone & 1st Note, updated step 4 Updated several steps based on lessons learned from classroom training and simulation Updated all step 1’s | July 16, 2012 |
| 3.1 | 1.0 / 13 | Updated step 2 | August 29, 2012 |
| 2.2 3.2 4.5 4.6 | 1.0 / 1 1.0 / 7 1.0 / 10 1.0 / 12 | Added Hotline Call Communication Updated 1st Note Updated 1st and 2nd Note Updated steps West to North & North to Houston(IROL) All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.1 3.10 4.6 | 1.0 / 14 1.0 / 3 1.0 / 13 | Updated step 2 Updated 2nd note Updated Additional Notifications on Systems Functional and Systems are not Functional | March 1, 2013 |
| 3.1 3.2 3.7 3.11 4.6 | 1.0 / 15 1.0 / 8 1.0 / 9 1.0 / 4 1.0 / 14 | Updated step 2 Updated step 1, deleted steps 2 & 3 Updated scripts Updated script Updated scripts, West to North & step North to Houston | June 1, 2013 |
| 3.6 4.3 4.4 4.5 4.6 | 1.0 / 5 1.0 / 9 1.0 / 6 1.0 / 11 1.0 / 15 | Updated Exports, step 1 Updated step 1 & 3 Updated step 1 Deleted 2nd Note, updated step 1, 2 & 4 Added Monitor Frequency and updated Constant Frequency | July 1, 2013 |
| 3.1 3.3 3.11 4.8 | 1.0 / 16 1.0 / 12 1.0 / 5 1.0 / 11 | Updated step 1 Updated 4th note Updated step 1 Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.7 4.6 | 1.0 / 10 1.0 / 16 | Added CFE DC-Tie Derates and AEP DC-Tie Derates Removed HHGT TO reference | August 30, 2013 |
| 1.1 3.3 3.4 3.5 3.6 3.8 3.9 3.11 4.1 4.2 4.5 | 1.0 / 2 1.0 / 13 1.0 / 4 1.0 / 3 1.0 / 6 1.0 / 6 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 8 1.0 / 12 | Changed “Security” to “Reliability” Updated step 2 Updated both steps Updated last Note and step 3 Updated the Notes and step 1 and 2 Updated step 2 Updated step 2 New Loss of DC-Tie Operator E-tagging Updated step 6b Updated step 6b Added note to Transmission Issues within CFE All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.8 4.1 4.2 4.3 4.4 4.5 4.8 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 1.0 / 7 1.0 / 13 1.0 / 13 | Updated step 2 Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step Turret Phone, 3a, 6b, Note, & 7b Updated step 3 Updated step 2 Updated step Turret Phone & 4 Updated all step 1’s | January 29, 2014 |
| 3.3 3.6 3.7 3.9 3.10 3.11 3.12 4.1 4.2 4.3 4.5 | 1.0 / 14 1.0 / 7 1.0 / 11 1.0 / 8 1.0 / 0 1.0 / 4 1.0 / 7 1.0 / 12 1.0 / 10 1.0 / 11 1.0 / 14 | Updated 1st & 4th Note & step 1 to include Sharyland as Tie Operator Updated steps 1 & 2 Updated steps 1, 2, 3 & Cancel Message Updated 1st Note, step 2, 3 & 5 New procedure Updated section number Updated section number & step 2 Updated Turret Phone, 1st Note, CFE & SPP sections Updated Turret Phone, 1st Note, CFE & SPP sections Updated 1st None, steps 1, 2 & 3 Updated to include Sharyland change | February 25, 2014 |