- Power Operations Bulletin # 688

ERCOT has posted/revised the Transmission and Security manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 4.1	Transmission Congestion Management

Procedure Purpose:  To verify and take corrective action for post-contingency overloads for various conditions.

| Protocol Reference | 3.10.4(2) | 6.5.1.1 | 6.5.5.2(1) |  |
| --- | --- | --- | --- | --- |
|  | 6.5.7.1.10 | 6.5.7.1.11 | 6.5.7.8 | 6.5.9 (2) |
|  | 6.5.9.2(3)(c)&(e) | 6.5.9.3.3(2)(c) | 6.5.9.3.4(2) | 6.5.9.3.4(5) |
| Guide Reference | 2.2.2 |  |  |  |
| NERC Standard | IRO-002-2 R4, R5, R6 | IRO-003-2 R1, R2 | IRO-005-3.1a R1, R6, R10 | IRO-006-TRE-1 R1, R2 |
|  | TOP-002-2.1b R5, R6, R10 | TOP-004-2 All | TOP-006-2 R1, R2 | TOP-008-1 R1, R2, R4 |

| Version: 1 | Revision: 31 | Effective Date: October 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, exclude steps, or take any additional actions required to ensure system security based on the information and situational awareness available during both normal and emergency conditions. |
| Authority | ERCOT System Operators have the authority to take or direct timely and appropriate real-time action, up to and including shedding firm load to alleviate System Operating Limit (SOL) violations. Following a separation from the Interconnection, and following automatic under-frequency load shedding, System Operators will also direct TOs to shed additional load manually when there is insufficient capacity to restore system frequency. To include directing physical operation of the ERCOT Transmission Grid, including circuit breakers, switches, voltage control equipment, and Load-shedding equipment. |
| Unknown State | When in an unknown operating state (any state for which valid operating limits have not been determined), it will be considered to be an emergency and ERCOT shall restore operations to respect proven reliable power system limits within 30 minutes. |
| CAUTION | IF: - At any time, the prescribed measures within this procedure fail to resolve the congestion, AND - The transmission system is in an unreliable state (see Section 4.2 if a DC-Tie has a shift factor) THEN: - Issue an Emergency Notice - See Generic Script in Section 7.1 - Notify Real-Time operator to make hotline call to QSEs. |
| Critical Facilities | Critical facilities are the ERCOT defined contingencies that show up after running Real Time Contingency Analysis (RTCA) as a post-contingency overload. This list is located in the EMS and an electronic copy is located on the MIS Secure site: Select: Grid>Generation>Reliability Unit Commitment>Standard Contingency List’ Select “Standard Contingency List” Open the zip file>Open the CIM file>Select the Standard_Contingency_List tab and view the contingencies. A potential critical facility becomes a critical facility when the contingency appears in RTCA as a post-contingency overload. |
| NOTE | Congestion Management Techniques consist of: - SCED - Phase Shifters - Remedial Action Plan (RAP) - Pre-Contingency Action Plan (PCAP) - Mitigation Plan (MP) – enacted Post-Contingency - Temporary Outage Action Plans (TOAP) - Unit specific dispatch instructions (Override HDL/LDL or VDI) - Non-Spin may be used as necessary. If there is a difference in line ratings between ERCOT and the TO, the most limiting rating will be used until the correct rating can be determined. The electronic and hard copy for the RAPs, PCAPs, and MPs are to be considered current. Should a conflict exist between the electronic and hard copy, the electronic version is to be used. - This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Special Protection Systems (SPS) and/or MP/PCAP/RAP , - A hardcopy of the SPSs are maintained in the control room by the Operations Support Administrative Assistant, - TOAPs are usually located in the daily Outage Notes. |
| Phase Shifters | Phase shifters can be used to help with congestion management: - Putnam – NW/WN transfers to increase transfer capability - Yellow Jacket – Mitigate local congestion and increase W/N transfers - Big Lake – Mitigate local congestion and increase W/N transfers - Firerock ETT – Mitigate local congestion and increase W/N transfers - Nelson Sharp – Valley import during outages and flow in/out of Corpus Christi - Hamilton Road – Control wind export issues from McCamey area and occasionally Laredo import issues during outages - North Laredo – Control Laredo import issues during outages - Thomaston – Control flow into Cuero, Yoakum and Victoria Areas Refer to OpsMon Display 08 HRUC Phase Shifter Position and they are also with the shift factors in the EMS. |
| Constraint Shift Factor Cut Off | Basecase and post-contingency constraints which do not have generator shift factors for units greater than or equal to 2% as indicated in EMS are not activated in SCED. See Section 4.7 Mitigation Plan for additional details. |
| ### Review Planned Outage Notes |  |
| 1 | Review daily outage notes: IF: - Outage notes recommend slower moving Resources to be lowered to maintain system security; THEN: - Take a real-time snap shot to determine where Resource(s) are needed before outage is taken - Use the manual override to step down Resource(s) - Once Resource(s) are down to where snap shot showed, - Give approval for switching, - Release manual overrides, and - Activate constraint (when necessary). - Post message on MIS Public Typical MIS Posting Script: ERCOT is taking manual actions to pre-posture for XXXX outage. |
| 2 | IF: - An outage requires a Resource to be On-line to solve a voltage issue and having the Resource On-line causes a post-contingency overload; THEN: - Manually override the Resources to its LSL - Notify QSE of action - Post message on MIS Public Typical MIS Posting Script: ERCOT is taking manual actions due to XXXX planned outage. |
| Log | Log all actions. |
| ### Evaluate Real Time Contingency Analysis (RTCA) Results |  |
| 1 | IF: - A major topology change has occurred; THEN: - Re-run RTCA and VSAT/TSAT. |
| Log | Log all actions. |
| ### Post-Contingency Overloads |  |
| 1 | WHEN: - Post-contingency overloads are approaching 98% of the Emergency Rating; THEN: - Determine if the SCADA is of similar magnitude to the pre-contingency value. - Example: Review the MW and MVAR flows |
| 2 | IF: - Inaccurate; THEN: - DO NOT employ congestion management techniques, - Notify the Shift Supervisor and Operations Support Engineer to investigate. - Make log entry. |
| 3 | IF: - Accurate; THEN: - Verify NO SPS (identified as RAS in EMS), or RAP exist - Verify that a PST cannot be used to resolve congestion IF: - A PST can help solve the congestion; THEN: - Activate the constraint until the PST is studied and moved. |
| 4 | IF: - Post-contingency loading is 98% or greater, and generator shift factors for units with at least a 2% shift factor as indicated in EMS exist; THEN: - Activate constraint - Lower the value in the % Rating column in TCM to tighten the constraint if needed (minimum of 95%, excluding W-N), - If experiencing oscillation issues, notify the Operations Support Engineer to investigate - If constraint needs to be controlled before the next SCED run: - Manually run RTCA after activating the constraint, - Manually execute the SCED process - Refer to “Managing Binding and Exceeded Constraints”. |
| 5 | IF: - Constraints with pre-contingency or post-contingency flows which exceed the rating of the overloaded Transmission Element are not activated in SCED; THEN: - Acknowledge the constraint and list a reason using the drop down box, - The comment field should be used for additional information |
| 6 | A list of Qualifying Facilities can be found in Desktop Guide Common to Multiple Desk section 2.20 IF: - A Qualifying Facility (QF) is needed to operate below its LSL, or be ordered off-line to solve congestion; THEN: - Issue VDI to the appropriate QSE(s), - Choose “DECOMMIT or ERCOT REQUESTED QF OPERATE BELOW LSL” as the Instruction Type from Resource level - Enter contingency name in “other information” - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Issue an Emergency Notification via Hotline call to TOs, - Instruct the Real-Time Operator to make Hotline call to QSEs, - Post message to MIS Public. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to directing a Qualifying Facility [offline or operate below its LSL]. [TO] please repeat this back to me. If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 7 | IF: - Post-contingency overloads of 98% or greater of the “15-Minute Rating” exist with a RAP in place to relieve; THEN: - Activate constraints as necessary to reduce the predicted post-contingency loading to no more than 98% of the “15-Minute Rating”; IF: - Constraint needs to be controlled within the next 5 minutes; THEN: - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”. |
| 8 | IF: - Congestion can not be fully resolved and does not have a MP or TOAP; THEN: - REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.7 Mitigation Plan). |
| 9 | Periodically check the Base Case violations for Thermal overloads: IF: - A valid Thermal overload exists in Real-Time; THEN: - Activate constraints as necessary, - Manually run RTCA after activating the constraint, - Manually execute the SCED process, - Refer to “Managing Constraints in SCED”, - Take additional manual actions as necessary up to and including shedding firm load to alleviate System Operating Limit violations. IF: - A transmission condition has been identified causing unreliable operation or overloaded elements, AND firm load is shed, THEN: - Issue an Emergency Notice - See Generic Scripts in Section 7.1 - Notify Real-Time operator to make hotline call to QSEs. |
| ONTEST | Resources with a Resource Status of ONTEST, may not be issued dispatch instructions except: - For Dispatch Instructions that are a part of the testing; or - During conditions when the Resource is the only alternative for solving a transmission constraint (would need QSE to change Resource Status); or - During Force Majeure Events that threaten the reliability of the ERCOT System. |
| QSGR | Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Overide HDL And LDL IF: - A QSGR is needed for voltage support or an unsolved contingency; THEN: - Override LDL to a level greater than or equal to the COP LSL - DO NOT override while SCED is running, - Notify QSE as time permits - Post message on MIS Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. - These Resources can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Approved Quick Start (QSGR) Resources |
| Not Dispatchable to SCED | REVIEW REFERENCE DISPLAY: EMS Applications>Generation Control>Resource Limit Calculation>RLC Unit Input Data and RLC Unit Output Data WHEN: - A QSE has telemetered more A/S on a specific Resource that is greater than their HSL, OR - A Resource is generating more than their telemetered HSL; THEN: - SCED will set the HDL=LDL=MW making the Resource undispatchable, - Request the QSE to make corrections to telemetry (Resource status, Resource limits, A/S responsibilities, etc) - Disregard IRRs unless transmission constraint is active. |
| Log | Log all actions. If known, log the outage that is causing the congestion. |
| ### Post-Contingency Overloads on Private Use Networks (PUNs) or Customer Owned Equipment behind the Meter |  |
| 1 | IF: - A post-contingency overload is 100% of the Rating on a PUN or customer owned equipment; THEN: - Contact the appropriate QSE/PUN to alert them of the post-contingency overload, VERIFY: - There is a plan to mitigate the overload if the contingency were to occur. |
| 2 | IF: - It is determined that the QSE/PUN has no way to mitigate or correct; THEN: - Direct the QSE/PUN to take action such as lower/raise generation or load (verbal directive only, do not override HDL/LDL or activate constraint in SCED) and - Acknowledge the post-contingency overload in TCM. |
| 3 | IF: - The contingency occurs; THEN: - Notify the QSE/PUN to ensure action is being taken on the plan. |
| 4 | IF: - A post-contingency overload of 98% or greater of the Rating on transmission equipment (non-PUN or customer owned equipment), and the only shift factor of 2% or more is a PUN unit; THEN: - Activate the constraint. |
| Log | Log all actions. |
| ### Managing Constraints in SCED |  |
| NOTE | One of the key tasks is to properly monitor and manage transmission constraints. Keep track of non-binding constraints that have flows approaching their limits and be prepared to take action as the constraint approaches its rating. |
| Output Displays | REVIEW REFERENCE DISPLAY: Market Operation>Real-Time Market>SCED Displays>DSP Displays>DSP Constraint Summary Once SCED has completed its run, check the validity of the binding/exceeded constraints, limits, shadow price, and current real-time flows. |
| In Series | It is common for series elements to have nearly identical shift factors for a given contingency. If post-contingency loading of 98% or greater occurs for multiple elements which have been identified as being in series with each other, only the most limiting constraints should be activated to mitigate all the series element congestion. Example: Contingency A overloads X, Contingency A overloads Y |
| Same Element | If post-contingency loading of 98% or greater occurs on the same element for multiple contingencies and they have nearly identical shift factors, only one of the most limiting constraints should be activated to mitigate the congestion. Example: Contingency A overloads X, Contingency B overloads X |
| 1 | Verify that the SCED executions are reducing the flows on each constraint that is binding. |
| 2 | When a constraint becomes violated in SCED, which is when it has reached its max shadow price, review the following bullets to determine the next action: - Confirm that pre-determined relevant RAPs are properly modeled in the EMS, - Ensure curtailed units are following base points (RLC Output Data display), - Verify that units with large shift factors (SF button on EMS/TCM display) do not have a status of ONTEST (RLC Output Data display), - Redistribute A/S to increase capacity available to SCED (see separate procedure below), - Determine if a unit carrying Off-line Non-Spin is needed to solve congestion, - Ask Resource Operator to deploy Non-Spin for the specific unit - The telemetered Non-Spin schedule must be changed to 0 for SCED to dispatch the Resource - Determine if additional units need to be committed/decommitted, - Confirm SCED is balancing conflicting constraints, - Create a “suggestion plan” for the constraint if can’t determine course of action from shift factors |
| 3 | At times, it may be necessary to manually override HDL/LDL, these reasons could include the following: - Manually dispatching slower moving Resources before an outage to better manage congestion caused by the outage - Conflicting constraints - Unsolved contingencies IF: - An override is necessary; THEN: - Notify QSE of override - Consider doing the override in steps as to not exceed ramp rate - Post message on MIS under Operational Information Typical MIS Posting Script: ERCOT is taking manual actions for XXXX constraint. NOTE: - DO NOT override while SCED is running - DO NOT override a Resource ONTEST - DO NOT override a Resource ONRR |
| 4 | IF: - All applicable steps above have been completed, AND constraint is still exceeded in SCED (max shadow price); THEN: - Instruct Operations Support Engineer to develop a mitigation plan, AND - Contact Manager, System Operations and/or Control Room Operations Manager to investigate further |
| NOTE | EMP Applications>TCM-Transmission Constraint Manager>Related Displays>Message Log for CAM IF: - No shift factors are passed for the constraint; THEN: - Contact Help Desk to issue a ticket to EMMS Production to fix immediately. |
| Log | Log all action taken including the following: - Reason for doing a manual override - Any security violations that were ≥ 125% of the Emergency Rating |
| ### Redistribute A/S to Increase Capacity available to SCED |  |
| 1 | RLC Unit Input Data display IF: - A/S needs to be removed from a specific unit in order to increase capacity to SCED; THEN: - Determine which A/S to remove - Instruct the QSE to remove the A/S by updating their telemetry to free that capacity to SCED - Notify Resource Operator with undeliverable A/S type, amount and approximate hours. |
| LOG | Log all actions. |
| ### Unsolved Contingencies |  |
| 1 | Periodically check the “Contingency Solution Results” display: IF: - Unsolved contingencies exist; THEN: - Run the State Estimator again, - If unsolved contingencies remain, notify the Operations Support Engineer to investigate |
| LOG | Log all action taken including the following: - Reason for unsolved contingency - Actions taken to resolve |
| ### Model Inconsistencies/Updates |  |
| 1 | IF: - Any inconsistencies in ratings, impedance changes, etc. are found; THEN: - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required, correct it through the NOMCR process. |
| 2 | IF: - There is a difference in line ratings between ERCOT and a TO; THEN: - The most limiting rating will be used until the correct rating can be determined - Notify Operations Support Engineer so that they can work with the TO to confirm the correct information and if required correct it through the NOMCR process. |
| LOG | Log all actions. |
| ### QSE Requests to Decommit a Resource |  |
| 1 | IF: - Notified by the Resource/RUC Operator of a request to decommit a self-scheduled Resource; THEN: - Perform a real-time study (if necessary) to determine if ERCOT will remain N-1 secure with the Resource off-line and no additional active constraints for SCED will occur, - Notify the RUC Operator with determination. |

## 5.1	Outages

Procedure Purpose:  Monitor and respond to various types of equipment outages, both Transmission and Generation, in order to maintain reliability of the ERCOT Grid.

| Protocol Reference | 3.1.1(2)(j) | 3.1.4.2 | 3.1.4.4 | 3.1.4.5 |
| --- | --- | --- | --- | --- |
|  | 3.1.4.6 | 3.1.5.1 | 3.1.5.4 | 3.1.5.5 |
|  | 3.1.5.7 | 3.1.5.11 | 3.1.6.11(2) | 6.5.7.1.6 |
|  | 6.5.7.1.10(2)(c) | 6.5.7.1.6 |  |  |
| Guide Reference | 2.4 |  |  |  |
| NERC Standard | TOP-002-2 R6 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: October 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT Operators can only make the following changes in the Outage Scheduler: - Remove actual start/end time if it is within 2 hours of the time the MP entered the outage, - Change status, - Add notes If a MP needs assistance or is unable to enter their outages, direct them to Outage Coordination. Outage Coordination has an “Impersonation” certification that will allow them to make the needed changes. |
| NOTE | Forced Outages should be verbally communicated to ERCOT and must be entered into the Outage Scheduler if it is to remain an Outage for longer than two hours. |
| 1 | IF: - An Emergency Condition is declared; THEN: - Determine if Outages can be returned to service if causing negative impacts to reliability, - Make a Hotline call and post Emergency Notice message on MIS Public. |
| ### Monitor Mode |  |
| 1 | IF: - Any outages, either planned or forced, that may require additional monitoring; THEN: - Mark the outages in the Outage Scheduler OS Monitored Outage display as deemed necessary, - Verify that the marked outages are in monitor mode, - Continue to monitor the marked outages. |
| ### Forced and Unavoidable Extensions |  |
| 1 | IF: - A Forced or Unavoidable Extension is received, review the outage details; THEN: - Monitor congestion and make appropriate changes as necessary, - Determine if it will have an effect on previously approved outages which may be to withdrawn. |
| ### Remedial Switching Action |  |
| Definition | “Remedial Switching Action” is a Forced Outage sub-type in the Outage Scheduler. ERCOT must approve all Remedial Switching Actions prior to implementation by TOs. |
| < 3 Days in length | Remedial Switching Actions are limited to a maximum of 3 days. |
| > 3 Days in length | If the Remedial Switching Action is required to remain active for longer than 3 days, a Planned Outage must be submitted to change the position of effected breakers and switches. |
| Approve | IF: - No issues identified; THEN: - Approve the Outage as received. |
| Reject | IF: - Reliability issues; THEN: - Notify Operations Support Engineer; - Reject the outage to ensure system reliability. |
| Restoration | Breakers and switches in a Remedial Switching Action must be able to be returned to their normal position within 4 hours or less (this allows for drive time for remote switches w/o SCADA). |
| Log | Log all actions. |
| ### Maintenance Outages |  |
| Definition | - Level 1- Equipment that must be removed from service within 24 hours to prevent a potential Forced Outage; - Level 2 - Equipment that must be removed from service within 7 days to prevent a potential Forced Outage; and - Level 3 - Equipment that must be removed from service within 30 days to prevent a potential Forced Outage. |
| Maintenance Outage with start time ≤ 24 Hours | IF: - A Maintenance Outage is received, review the outage if the scheduled start time is within the next 24 hours; THEN: - Run a study to determine if the outage will cause any reliability issues. |
| Approve Maintenance Outage with start time ≤ 24 Hours | IF: - No reliability issues identified; THEN: - Approve the Maintenance Outage. |
| Coordinate Maintenance Outage with start time ≤ 24 Hours | IF: - Reliability issues exist; THEN: - Coordinate the start of the outage with the TO to ensure system reliability as long as the outage is allowed to start within 24 hours, AND - Approve the Maintenance Outage. |
| Coordinate Maintenance Level 2 and 3 Outage ≤ 24 Hours | IF: - Maintenance Level 2 and 3 outages are received with a start time of less than the next 24 hours, AND - Reliability issues exist; THEN: - Coordinate the start of the outage with the TO to ensure system reliability as long as the outage is within the allowed Maintenance Level 2 (7 Days) and 3 (30 Days) outage criteria, - ERCOT Outage Coordination group may help coordinate a new start time, IF: - Reliability issues continue, THEN: - REQUEST the Operations Support Engineer investigate the development of a MP or TOAP (see section 4.7 Mitigation Plan), - Approve the Maintenance Outage after coordination. |
| Maintenance Level 2 and 3 Outages | IF: - Maintenance Level 2 and 3 outages are received with a start time of greater than the next 24 hours; THEN: - The ERCOT Outage Coordination group has a process to review all Maintenance Level 2 and 3 outages without further action. |
| Log | Log all actions. |
| ### Consequential Outages |  |
| 1 | WHEN: - A TO enters the breaker and switch statuses associated with an Electrical Bus; THEN: - A downstream topology processor will evaluate the breakers and switches associated with the applicable Electrical Bus to determine if the Electrical Bus is consequentially outaged, and to thereby designate the status of the Electrical Bus. |
| Evaluate | IF: - The TO has submitted the outage in the Outage Scheduler; THEN: - As time permits, perform a study to determine the effects the outage has on the ERCOT system and evaluate the request and verify the Outage meets the applicable requirements. |
| No Violations | IF: - NO, violations of applicable reliability standards exist; THEN: - Approve the request in the Outage Scheduler. |
| Yes Violations | IF: - YES, violations of applicable reliability standards exist; THEN: - Reject the request in the Outage Scheduler. |
| Log | Log all actions. |
| ### Returning from Planned Outage Early |  |
| 1 | Before an early return from an Outage, a Resource Entity or QSE may inquire of ERCOT whether the Resource is expected to be decommitted by ERCOT upon its early return. IF: - A QSE is notified by ERCOT that the Resource will be decommitted if it returns early and the Resource Entity or QSE starts the Resource within the previously accepted or approved Outage period,; THEN: - The QSE representing the Resource will not be paid any decommitment compensation. |
| ### Guidelines for Withdrawal of an Outage |  |
| 1 | IF: - Security analysis and/or Operator experience indicates that an “Approved” or “Active” outage may have an adverse impact on system reliability; THEN: - Review the restoration time of the outage and if necessary, - ERCOT may withdraw the outage. |
| 2 | WHEN: - ERCOT withdraws an outage via the Outage Scheduler; THEN: - Enter an explanation in the “Reviewers Notes” listing the reliability concerns that caused the withdrawal, - Notify the following, by e-mail, as soon as possible: - OPS Outage Coordination - OPS Support Engineering - 1 ERCOT Shift Supervisors - Include the following information: - From Station – To Station (if applicable) - The planned Start and End date of the outage. |
| 3 | IF: - A TO or QSE reports that the outage in question has progressed to a point that withdrawal is not practicable within the outages designated restoration time; THEN: - Record this information in the “Outage Scheduler Reviewer’s Notes”, - Log the outage in the Transmission Security Log, - Inform the Shift Supervisor, - Continue monitoring system security, - Request Operations Support Engineer to develop Mitigation plan if necessary. |
| ### Approval of an Outage on Transmission Devices of More than one hour duration |  |
| 1 | IF: - A verbal request for permission to remove a transmission device from service for more than one hour is received; THEN: - Verify with the TO that the work being done will not prevent the device from being placed back in service immediately if needed, - As time permits, determine that such operation will not affect the reliability of the Transmission System, - If outage will cause reliability issues, go to Step 2 - If no impact to the system, go to 3. |
| 2 | IF: - System reliability is impacted; THEN: - Discuss with the TO the possibility of postponing the outage to a later time OR deny the request. |
| 3 | IF: - There is no reliability issue; THEN: - Verbally approve for the TO to remove a transmission device from service. - Instruct TO to make notification when device is place back in service. |
| Log | Log all actions. |
| ### Simple Transmission Outage |  |
| NOTE | A Simple Transmission Outage is a classification of outage that can be removed from service without effecting LMP prices or causing congestion. The Outages are limited to the following 3 basic descriptions: - Expanded Bus Outage - Generator Breaker Maintenance - Open-ended Lines Refer to Desktop Guide Transmission Desk Section 2.2. |
| 1 | IF: - The outage meets the requirements of a Simple Transmission Outage, which are: - Has been submitted between 1 and 2 days in advance, - Cannot exceed 12 hours in duration, AND - Has a restoration time of 1 hour or less; THEN: - ERCOT will approve or reject within 8 business hours after receipt. |
| ### Opportunity Outages |  |
| Definition | An Outage that may be accepted by ERCOT when a specific Resource is Off-Line due to an Outage. |
| 1 | Opportunity Outages for Resources are a special category of Planned Outages that may be approved by ERCOT when a specific Resource has been forced Off-Line due to a Forced Outage and the Resource has been previously accepted for a Planned Outage during the next eight days. |
| 2 | When a Forced Outage occurs on a Resource that has an accepted or approved Outage scheduled within the following eight days, the Resource may remain Off-Line and start the accepted or approved Outage earlier than scheduled. The QSE must give as much notice as practicable to ERCOT. |
| 3 | Opportunity Outages of Transmission Facilities may be approved by ERCOT when a specific Resource is Off-Line due to a Forced, Planned or Maintenance Outage. A TO may request an Opportunity Outage at any time. |
| 4 | When an Outage occurs on a Resource that has an approved Transmission Facilities Opportunity Outage request on file, the TO may start the approved Outage as soon as practical after receiving authorization to proceed by ERCOT. ERCOT must give as much notice as practicable to the TO. |

## 6.1	Voltage Control

Procedure Purpose:  Ensure adequate voltage levels are maintained throughout the ERCOT grid to prevent a potential voltage collapse.

| Protocol Reference | 3.15.1(3) | 6.5.1.1 | 6.5.7.1.10(3)(h) | 6.5.7.7(2) |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.5(1) | 2.2.6(2) | 2.7.2 | 2.7.3 |
|  | 2.7.4 |  |  |  |
| NERC Standand | IRO-005-3.1a R1.1-R1.4 | NUC-001-2 R4.2 | TOP-002-2.1b R8, R10 | TOP-004-2 R1, R6 |
|  | TOP-006-2 R2 | VAR-001-4 R2, R3 |  |  |

| Version: 1 | Revision: 21 | Effective Date: October 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The intent of this procedure is to verify and take corrective action for voltage issues. Although the steps within the procedure are numbered, the numbering is for indexing purposes and are not sequential in nature. The system operator will determine the sequence of steps, or any additional actions required to prevent voltage collapse. |
| NOTE | ERCOT posts the "Seasonal Voltage Profiles" desired voltage for each generation interconnection. The current profiles for generators may be found in the ERCOT Market Information System (MIS) Secure site. Select: Grid> Transmission>Voltage and Dynamic Ratings>Voltage Profiles Select “Voltage Profiles” Open the current file>Open the xls file. |
| NOTE | All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| ### Assist TOs with Voltage Issues at Nuclear Power Plants |  |
| NOTE | ERCOT and TOs shall maintain the switchyard voltage at each operating nuclear power plant at a nominal value that does not violate its licensing basis with the Nuclear Regulatory Commission. |
| Comanche Peak Voltage Table | For Comanche Peak: - System; - 345 kV; - 138kV. - Nominal Voltage; - 352 kV; - 141 kV. - Tolerance; - +2.56% or -3.40%; - +2.13% or -4.26%. - Maximum Voltage; - 361 kV; - 144 kV. - Minimum Voltage; - 340 kV; - 135 kV. Decordova and Wolf Hollow are points at which generation voltage adjustments can be expected to impact control of Comanche Peak voltage. |
| STP Voltage Table | For South Texas Project: - Plant Configuration; - Maximum kV; - Minimum kV. - Normal line up, through 12/31/2015; - 362.25; - 340. - Alternate line up, through 12/31/2015; - 362.25; - 347. - Alternate without Unit Auxiliary Transformer, through 12/31/2015; - 362.25; - 355. - All line ups, after 12/31/2015; - 362.25; - 331. The STP Switchyard Facilities’ steady state voltage, with both STP units off-line, should be maintained within the ranges above. Calaveras (Spruce), Braunig (Von Rosenberg), DOW, and WAP are points at which generation voltage adjustments can be expected to impact control of STP voltage. If voltage goes outside the above ranges, notify the STP QSE and inform them that voltage is outside the range and is expected to be within range in [# minutes]. Note: It is the STP QSEs responsibility to notify ERCOT when STP is in an alternate line up. |
| 1 | IF: - Voltage levels exceed the maximum or minimum levels as stated in the voltage tables; THEN: - Coordinate the appropriate voltage control action with the corresponding TO and QSE. |
| 2 | WHEN: - Voltage is back to normal range; THEN: - Notify the appropriate QSE. |
| ### Real-Time Voltage Issues |  |
| NOTE | - Post-Contingency low voltage alarms beyond the emergency operating low voltage limit could trigger Automatic Under-Voltage Load Shedding if the contingency were to occur. Detailed information on the amount of load on Automatic Under-Voltage Load Shedding Schemes (UVLS) can be found in Desktop Guide Transmission Section 2.9. - Generation Resources required to provide VSS may not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT unless equipment damage is imminent. - Major transmission lines shall be kept in service during Light Load as much as possible. Lines should only be removed after all applicable reactive controls are implemented and studies are performed showing that reliability will not be degraded. |
| NOTE | ERCOT Nominal Voltage Levels are 345kV, 138kV, and 69kV. The general voltage guidelines are as follows (listed in kV): Nominal Voltage; Normal Operating Limits; Emergency Operating Limits; Ideal Voltage Range. 345; 327.75 – 362.25; 310.5 – 379.5; 345 – 359. 138; 131.1 – 144.9; 124.2 – 151.8; 138 – 144. 69; 65.55 – 72.45; 62.1 – 75.9; 69 – 71.5. Some TOs utilize different Normal (Basecase) and Emergency (Post-Contingency) voltage operating limits than the general voltage guidelines. These limits can be seen under the Network Limits display. |
| 1 | Monitor the voltage contingency violations and Basecase voltage violation displays in RTCA WHEN: - Indicated by SCADA alarms, RTCA or by a TO of voltage concerns; THEN: - Determine if the SCADA is of similar magnitude to the pre-contingency value. - Example: Review nearby kV measurements - Review “Voltage Tracking Issues Spreadsheet” on SharePoint to ensure the basecase/contingency is not listed - If listed, no further action needed. IF: - Inaccurate; THEN: - Notify the Shift Supervisor and Operations Support Engineer to investigate. - Log in “Voltage Tracking Issues” on SharePoint - Make log entry. |
| 2 | IF: - Accurate; THEN: - Discuss the voltage concern with the appropriate TO - Ensure the TO has utilized all static reactive power resources (capacitors, reactors, change transformer taps) INSTRUCT: - The TO to take pre-contingency actions such as closing a cap bank for low voltage, close a reactor for high voltage or adjust a transformer tap to resolve voltage contingency violations and Basecase voltage violation. Typical Script to appropriate TO: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [TO] to [Raise/Lower] voltage at [specify bus] by [Closing/Opening/Adjusting] [Cap/Reactor/Transformer Tap] to resolve a [Basecase Voltage Violation/RTCA Voltage Contingency Violation]. [TO] please repeat this instruction back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. IF: - These actions show to inadvertently cause a high voltage limit or low voltage limit exceedance; OR - All static reactive power resources have been utilized and there is still an issue; THEN: - Determine if adjusting voltage at a nearby Generation Resource will help rectify the voltage concern, coordinate this action with the appropriate TO, IF: - The TO needs assistance from ERCOT to get voltage adjusted; THEN: - Instruct the appropriate QSE to raise or lower bus voltage, - The QSE should complete the requested in no more than five minutes. Typical Script to appropriate QSE: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is instructing [QSE] to [raise or lower] voltage at [specify bus] by [+1 or 2kV or -1 or 2kV] for a target of [target kV]. [QSE] please repeat this instruction back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. IF: - No Generation Resources are on-line; THEN: - Determine if a Generation Resource can be brought On-Line within an appropriate timeframe. If the answer is Yes: - Request a manual constraint be built if quickstart or request RUC operator to commit. |
| 3 | IF: - Voltage violations are still indicated; THEN: - Determine if the cause is due to a planned outage - Return the outage if it can be done within the needed timeframe. IF: - No solution is available; THEN: - Notify the Shift Engineer to develop a Mitigation Plan. |
| LOG | Log all actions. |
| ### Future Voltage Issues |  |
|  | WHEN: - Notified by the RUC Operator of a future voltage contingency; THEN: - Discuss the voltage concern with the appropriate TO - Discuss the identified future voltage contingency and come to an agreement as to the proper action. This could be reactive resource switching, transmission switching, development of a CMP, or commitment of additional generation IF: - A Resource is identified in order to maintain reliability of the ERCOT Grid Reliability THEN: - Instruct RUC Operator to commit the Resource |
| LOG | Log all actions. |
| ### Operating beyond CURL or URL |  |
| Exceed URL | ERCOT shall not instruct any single Generation Resource to operate beyond its CURL or URL as displayed on the EMS RTNET UNIT MVAR display Min and Max columns for the resources current output level. IF: - Instructing a QSE’s Generation Resource to exceed its Unit Reactive Limit (URL); THEN: - Issue a VDI to the QSE for exceeding the URL (Exceed URL VDI). The VDI must include the following: - Resource name - Specific voltage set point. - Start time - End time - Choose “HOLD X VOLTAGE LEVEL” as the Instruction Type from Resource level - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Notify Operations Support Engineer of instruction, they will be providing analysis to Settlements. |
| Reduce MW | IF: - MW output must be reduced to follow a voltage support instruction to avoid violating the CURL or URL; THEN: - Issue a VDI to the QSE providing Voltage Support Service (VSS VDI). The VDI must include the following: - Resource name - MW level at time of instruction - MW level Resource needs to move to for Voltage Support - Start time - End time - Choose “STAY AT/ABOVE X MW/MVAR LEVEL” or “STAY AT/BELOW X MW/MVAR LEVEL” as the Instruction Type from Resource level - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Notify Operations Support Engineer of instruction, they will be providing analysis to Settlements. |
| NOTE | The Change columns on the UNIT_MVAR display indicate how many MVAR the CURL or URL is being exceeded by at this time. If the Change columns are both zero (0), the CURL or URL is not being exceeded. |
| QSE Performance | Maintain a log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests. QSEs responding in less than two minutes from the time of issuance shall be deemed satisfactory. |
| ### Voltage Security Assessment Tool (VSAT) |  |
| NOTE | VSAT and RUC perform full AC analysis of all contingencies. |
| 1 | IF: - Any of the monitored VSAT scenario results approaches the Reliability margins listed in the table below; THEN: - Manually rerun the entire sequence of RTNET, RTCA, and RTDCP (VSA) - Confirm VSAT indicates either “Normal” or “Pending” Reliability Margin Table. Scenario Name; Margin. O-DFW_L; 200MW. O-CORP_L; 75MW. O-VAL_L; 75MW. O-H_L; 200MW. N-H_G; 200MW. N-H_L; 200MW. For N-H_G and N_H_L: Refer to section 4.5 North-Houston Voltage Stability Limit of this procedure. |
| 2 | IF: - VSAT indicates that a Reliability Margin may be exceeded; THEN: - Determine if the current Reliability Margin pre-contingency value is less than the Margin on the table in the previous step. - If no, no further action is required. - If yes, go to Step 3. |
| 3 | Determine the contingency status in RTCA (solved/unsolved). IF: - Solved, - Have Operations Support Engineer verify if the problem is real, - If real, request information on weak bus, - Request the TO in the affected area turn on capacitor banks and turn off reactors near the weak busses. - If not real, no further action is required. - Unsolved, - Notify Shift Supervisor and Operations Support Engineer - Manually dispatch fast ramp generators to increase generation in weak bus area. - If all online units are at maximum capacity - Instruct RUC Operator to commit additional resources in the weak bus area that are available. |
| 4 | WHEN: - Capacitor banks are placed in service; THEN: - Rerun VSAT with new topology. |
| 5 | Determine if the current Reliability Margin pre-contingency value is greater than the Margin Value from the table above. IF: - The current Reliability Margin pre-contingency value is greater than the Margin; THEN: - No further action is required. OR IF: - The current Reliability Margin pre-contingency value is less than the Margin; THEN: - Determine if there are more units available in the affected area, AND - Repeat the process starting with Step 3. If no additional generation is available, continue. |
| 6 | IF: - No additional generation is available; THEN: - Notify Operations Support Engineer to create a Mitigation Plan. |
| ### Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) |  |
| NOTE | Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT. |
| NOTE | Operations Support will keep a spreadsheet with the current status of each PSS and AVR. This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > AVR AND PSS Status |
| 1 | WHEN: - Notified by a QSE of a PSS or AVR in manual or in Power Factor Mode; THEN: - Instruct the QSE to manually adjust VAR output as required to maintain voltage set-point until the AVR is back in service, NOTIFY: - The appropriate TO of the status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “OPS Advanced Network Applications” - “1 ERCOT System Operators” |
| 2 | WHEN: - Notified by a QSE that the PSS or AVR is in Auto and back in service; NOTIFY: - The appropriate TO of the status, if not already done so by QSE, - Enter the status change information into the ERCOT Logs, - Log type of either “PSS” or “AVR”. - Include the company name, the name of the person spoken with, and reason (if device is being placed in or taken out of service). - Include that the TO has been notified of change in status - Copy and paste the log entry into an e-mail and send to - “Operations Analysis” - “OPS Support Engineering” - “OPS Advanced Network Applications” - “1 ERCOT System Operators” |

## 7.1	Market Notices

Procedure Purpose: Guidelines for issuing Emergency Conditions and the four possible levels: Operating Condition Notices (OCN), Advisories, Watches, and Emergency Notices.

| Protocol Reference | 6.3.2(3)(a)(i)(ii) | 6.3.3 | 6.5.1.1(1) | 6.5.9.2(1) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3 | 6.5.9.3.1 | 6.5.9.3.2 | 6.5.9.3.3 |
|  | 6.5.9.3.4 |  |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 | EOP-001-2.1b R3.1 |  |  |

| Version: 1 | Revision: 19 | Effective Date: October 1, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### OCN |  |
| NOTE | Consider the severity of the potential Emergency Condition. The severity of the Emergency Condition could be limited to an isolated local area, or the condition might cover large areas affecting several entities, or the condition might be an ERCOT-wide condition potentially affecting the entire ERCOT System. |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Operating Condition Notice (OCN). The OCN can be issued for any of the following reasons or to obtain additional information from Market Participants. - There is a projected reserve capacity shortage that could affect reliability and may require more Resources - When extreme cold weather is forecasted approximately 5 days away - When extreme hot weather is forecasted approximately 5 days away - When an approaching Hurricane / Tropical Storm is approximately 5 days away - Unplanned transmission Outages that may impact reliability - When adverse weather conditions are expected, ERCOT may confer with TOs and QSEs regarding the potential for adverse reliability impacts and contingency preparedness |
| ### Advisory |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Advisory. The Advisory can be issued for any of the following reasons or to obtain additional information from Market Participants. - When an approaching Hurricane / Tropical Storm is approximately 3 days away - When extreme cold weather is forecasted approximately 3 days away - When extreme hot weather is forecasted approximately 1 to 3 days away - When conditions are developing or have changed and more Ancillary Services will be needed to maintain current or near-term reliability - ERCOT may exercise its authority to increase Ancillary Service requirements above the quantities originally specified in the Day-Ahead Market in accordance with ERCOT procedures - When extreme weather or conditions require more lead-time than the normal Day-Ahead Market allows - Transmission system conditions are such that operations within security criteria are not likely or possible due to Forced Outages or other conditions unless a CMP exists - Loss of communications or control condition is anticipated or significantly limited - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Watch |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue a Watch. The Watch can be issued for any of the following reasons or to obtain additional information from Market Participants. - A projected reserve capacity shortage is projected with no market solution available that could affect reliability. - When an approaching Hurricane / Tropical Storm is approximately 1 day away - When extreme cold weather is projected for next day or current day. - When extreme hot weather is projected for next day or current day - Conditions have developed such that additional Ancillary Services are needed in the Operating Period - Insufficient Ancillary Services or Energy Offers in the DAM - Market-based congestion management techniques embedded in SCED will not be adequate to resolve transmission security violations - Forced Outages or other abnormal operating conditions have occurred, or may occur that would require ERCOT to operate with active violations of security criteria as defined in the Operating Guides unless a CMP exists - ERCOT varies from timing requirements or omits one or more Day-Ahead or Adjustment Period and Real-Time procedures. - ERCOT varies from timing requirements or omits one or more scheduling procedures in the Real-Time process. - The SCED process fails to reach a solution, whether or not ERCOT is using one of the measures in Failure of the SCED Process. - The need to immediately procure Ancillary Services from existing offers - ERCOT may instruct TOs to reconfigure transmission elements as necessary to improve the reliability of the system - ERCOT may require information from QSEs representing Resources regarding the Resources’ fuel capabilities. Requests for this type of information shall be for a time period of no more than seven days from the date of the request |
| ### Emergency Notice |  |
| 1 | As directed by the Shift Supervisor or when appropriate, issue an Emergency Notice. The Emergency Notice can be issued for any of the following reasons or to obtain additional information from Market Participants. - Loss of Primary Control Center Functionality - Load Resource deployment for North-Houston voltage stability - ERCOT cannot maintain minimum reliability standards (for reasons including fuel shortages) during the Operating Period using every Resource practically obtainable from the market - Immediate action cannot be taken to avoid or relieve a Transmission Element operating above its Emergency Rating - ERCOT forecasts an inability to meet applicable Reliability Standards and it has exercised all other reasonable options - A transmission condition has been identified that requires emergency energy from any of the DC-Ties or curtailment of schedules - The Transmission Grid is such that a violation of security criteria as defined in the Operating Guides presents the threat of uncontrolled separation or cascading outages, large-scale service disruption to load (other than Load being served from a radial transmission line) and/or overload of Transmission Elements, and no timely solution is obtainable through SCED or CMPs - When extreme cold weather is beginning to have an adverse impact on the System - When extreme hot weather is beginning to have an adverse impact of the System - When Hurricane / Tropical Storm is in the ERCOT Region and is beginning to have an adverse impact on the System |
| ### Generic Script |  |
| Hotline | Communications must specify the severity of the situation, the area affected, the areas potentially affected, and the anticipated duration of the Emergency Condition. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a [state Notice type] for [state reason]. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. All directives shall be in a clear, concise, and definitive manner. Ensure the recipient of the directive repeats the information back correctly. Acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| Post | All notices must be posted on the MIS Public using Notice Builder. - For “free form” messages, the “Notice priority” will be specified as follows: - Operational Information/OCN type messages – low priority - Advisory/Watch type messages – medium priority - Emergency type messages – high priority |
| Hotline Cancellation | Typical Hotline Script cancellation: “This call requires everyone to remain on the line until it is complete. [TO] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the [state Notice type] for [state reason]. [TO] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Log | Log all actions. |
| ### Specific Scripts |  |
| NOTE | At times, the Real-Time, Resource or RUC operator takes the lead on the issuance of Hotline calls for specific procedures they have. The following scripts are to help guide you when specific procedures don’t exist for the T/S operator. |
| 50% Probability Of Down Ramp | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN due to a 50% probability of a [4,000 MW down-ramp in the next 180 minutes] [2,000 MW down-ramp in the next 60 minutes]. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]”. |
| 70% Probability Of Up Ramp | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issued an OCN due to a 70% probability of a 2,000 MW up-ramp in the next 60 minutes. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]”. |
| SCED Or RLC Failure | Note: RLC can fail independently of AGC; this same script will also be used for a RLC failure. If RLC is failed, SCED will have invalid results. Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to the failure of SCED. ERCOT may issue Emergency Base Points until the issue is resolved”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At [xx:xx], SCED base points are now valid and ERCOT is canceling the Watch”. |
| EMMS (LFC and RLC/SCED) Failure | Typical Hotline Script: “This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice due to an LFC and SCED failure. ERCOT has placed [Name] QSE on Constant Frequency. Please monitor your own service area and notify ERCOT if you exceed the emergency ratings of your transmission elements. Report West - North and North – Houston stability limits if power flows reach 70% of their respective limits and notify ERCOT of any forced line operations”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], LFC is now functional and SCED solutions are valid. ERCOT is canceling the Emergency Notice”. |
| Increasing Amount of Ancillary Services | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to the need to increase the system wide Ancillary Services (A/S) requirement above what was procured in the Day-Ahead Market due to [state the reason]. ERCOT will open a Supplemental Ancillary Service Market (SASM) to procure the additional A/S for hours [hours] for operating day [date]”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for increasing the system wide A/S requirement”. |
| A/S Insufficiency Offers in DAM | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to an insufficiency in A/S offers in the Day Ahead Market. Currently, ERCOT is requesting additional A/S Offers from QSEs”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for insufficient A/S offers in the Day Ahead Market. Sufficient offers have been received”. OR: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for insufficient A/S offers in the Day Ahead Market. A/S were covered through DRUC”. |
| A/S Insufficiency from DAM | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to A/S insufficiency in DAM for operating day [day]. The A/S insufficiencies will be procured in DRUC”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch due to A/S insufficiency in DAM”. |
| REG/ RRS - RUC Committed Shortages | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due insufficient A/S offers; HRUC will be used to commit the remaining A/S insufficiencies”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch due insufficient A/S offers”. |
| DAM Timeline Deviation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the timeline deviation of the Day Ahead Market; the start of DRUC will be delayed”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Advisory for the delay of DAM. DAM is now complete”. |
| DAM Failure | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to the failure of the Day Ahead Market for [effected date] due to [state issue]. ERCOT will open a SASM to procure Ancillary Services for tomorrow’s operating day”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Emergency Notice for the failure of the Day Ahead Market for [effected date]. All Ancillary Services have been procured for tomorrow’s operating day”. |
| DRUC Delay or Timeline Deviation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the timeline deviation of DRUC for [effected date] due to [state issue]. ERCOT will continue to try to complete DRUC by 18:00”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Advisory for the timeline deviation of DRUC. DRUC completed at [time]”. |
| DRUC Timeline not Met | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to DRUC not completing by 1800 due to [state reason]”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch due to DRUC not completing by 1800 due to [state reason]. ERCOT will procure in HRUC if needed”. |
| HRUC Failure or Timeline Deviation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory due to HRUC not completing for [state HE] due to [failure or timeline deviation]”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Advisory due to HRUC not completing for [state HE]”. |
| DRUC Committed For Capacity Shortage | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]. ERCOT will commit Resources as needed”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]”. |
| Excess Generation | Typical Hotline Script: This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]”. |
| Projected Reserve Capacity Shortage with no market solution | Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX], which causes a high risk for an EEA event”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for a projected reserve capacity shortage with no market solution available for [HE XX – XX]”. |
| RMR Projected Reserve Capacity Shortage | Typical Hotline Script: “This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed”. Typical Hotline Script Cancellation: “This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for a RMR projected reserve capacity shortage with no market solution available”. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 4, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | September 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch, Hartmann & Weldon | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Solis and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch and Hartmann | Procedure writers and editors | February 18, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |

Manual Change History

| Procedure | Ver/ Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.2 4.1 4.2 4.3 4.4 4.5 4.6 6.1 7.4 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities In section “Post-Contingency Overloads”, updated step 5 and QSGR, “Managing Binding and Violated Constraints” step 1, “Reaching Shadow Price Cap” step 1, and ” Managing Congestion during SCED Failure” step 1 Updated steps 1 and 2 Updated steps 2 and 3 Updated step ≤200MW In section “Special Protection Systems (SPS) (Identified as RAS in EMS)” changed 3rd Note to “Monitor”, changed “Operation” to step 4, changed “Runback” to step 5 and updated In section “Manual Dispatch Instruction to take a Unit Off-Line” and “Taking One CT of a Combined Cycle Off-line”, Updated step 1 and deleted Manual Dispatch Instruction In section “Voltage Issues”, Updated 1st Note and Exceed URL, deleted 3rd Note and added QSE Performance In section “ERCOT picks up Load for Non-ERCOT System” and “Non-ERCOT System picks up Load for ERCOT”, updated step 1 | December 1, 2010 |
| 4.1 4.2 4.3 5.1 | 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 | Deleted 1st Note, updated step Critical Facilities & 2nd Note, step 1 in Evaluate Real-Time Contingency Analysis Results, steps 3-6, 8 & QSGR in Post-contingency Overload, step 2 in Transmission Issues in the Areas of the CFE Ties, changed title & updated all steps in Managing Binding and Violated Constraints, step 1 in Reaching Shadow Price Cap, all steps in QSE Requests to Decommit a Resource, deleted Deploy/Termination of Non-Spin for Congestion, updated step 1 in Managing Congestion during SCED failure Updated step 1 & 2 Updated step 3 Added Remedial Switching Action section | December 15, 2010 |
| 4.1 4.2 4.3 7.1 | 1.0 / 3 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Reaching Shadow Price Cap Updated step 1 & 2 Updated step 2 & 3 and added step 4 & 5 Updated step 1 in Watch and step Hotline in Scripts | January 5, 2011 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.6 4.7 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 9.3 | 1.0 / 0 1.0 / 0 1.0 / 1 1.0 / 4 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added “Site failovers and Database Loads” as new procedure Added “Switching Control Center” as new procedure Updated step 5 Updated scripts, step 1 in “Managing Binding and Exceeding Constraints”, “Reaching Shadow Price Cap” and “Managing Congestion during SCED Failure” Updated step 2, 3 & 4 Updated scripts Updated scripts Added “Manual Commit of a Resource” as new procedure Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Deleted procedure | January 31, 2011 |
| 2.3 4.1 4.6 7.1 7.2 | 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 | Updated Site Failovers & added W-N Active step Added Review Planned Outage Notes, Updated all steps in Transmission Issues in the Areas of the CFE DC-Ties and step 1 of SCED not able to Solve Congestion (Reached Max Shadow Price) Added Posting Manual Actions Updated Watch and Emergency Notice Updated step 2 in Implementation of EEA Level 2A | March 25, 2011 |
| 2.3 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.3 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 2 | Added steps and updated whole procedure Updated step 8 Updated Review Planned Outage Notes Added 1st Note Updated 1st Note and step VSAT Updated step Status Change in SPS Updated Definition in Remedial Switching Action Updated “PSS & AVR” 2nd note Updated step 1 in Watch and Emergency Notice and step Post Updated “Restore Firm Load” and “Move From EEA Level 3 to EEA Level 2B” step 1 | April 22, 2011 |
| 2.3 3.3 4.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.3 8.4 9.1 | 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 1.0 / 1 | Added step Site Failover Complete Updated step 2 Updated Critical Facilities and step 5 in Post-Contingency Overloads, changed Managing Binding and Exceeded Constraints procedure to Managing Constraints in SCED & updated procedure, deleted SCED not able to Solve Congestion procedure Updated 2nd Note and step 2 in Voltage Issues Updated all step 1’s Updated all step 1’s and deleted Note in Implement EEA Level 2A Updated all step 1’s Updated all steps Updated all steps Added new procedure Changed section number and updated all steps Changed section name and updated all steps Updated 1st Note and steps 2 & 3 | June 14, 2011 |
| 4.1 4.5 6.1 7.2 7.3 7.4 7.5 7.6 10.1 | 1.0 / 8 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 1 | Updated 2nd note & step Phase Shifters in Transmission Congestion Management, steps 3, 5 & 7 in Post-Contingency Overloads, Moved Transmission Issues in the Areas of the CFE DC Ties to 7.4 Updated 1st note, steps SPS Posting and Status Change in Special Protection Systems (SPS) (Identified as RAS in EMS) and Updated all steps in Mitigation Plan (MP) Updated 2nd note in Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Implement EEA Level 1 and 2A Updated step 1 in Move from EEA Level 1 to EEA 0 Moved procedure from section 4.1 Changed section number from 7.4 to 7.5 Changed section number from 7.5 to 7.6 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 4.1 4.4 4.6 6.1 8.4 8.5 | 1.0 / 9 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 0 1.0 / 3 | Updated step 5 in Post-Contingency Overloads and step Log in Managing Constraints in SCED Updated monitor section Updated step 1’s Updated step 2 and deleted For HHGT_G-O in Voltage Security Assessment Tool Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.4 4.1 4.3 4.4 7.1 7.2 7.3 8.4 9.2 | 1.0 / 1 1.0 / 10 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 5 1.0 / 5 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated step 2 in Managing Constraints in SCED Updated step 2, 4 & 5, added step 3 Added 2nd note Updated step 1 in Watch Updated step 2 in Implement EEA Level 1, steps 1 & 2 in Implement EEA Level 2A Updated the step 1’s Updated temperature from 102 to 103 Updated 4th Note | September 1, 2011 |
| 3.3 4.2 7.2 7.3 7.4 7.5 9.1 | 1.0 / 4 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 2 1.0 / 4 1.0 / 2 | Updated Note to ensure compliance with IRO-008-1R2 Added 1st Note, added step 5, updated steps 4 & 6 Combined EEA 2 A and B per NPRR 379 Combined EEA 2 A and B per NPRR 379 Updated step 2 in Transmission Issues within CFE Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT Updated step 2 | October 1, 2011 |
| 3.3 4.1 4.3 4.6 9.1 | 1.0 / 5 1.0 / 11 1.0 / 7 1.0 / 5 1.0 / 3 | Updated scripts Updated step 4 in Post Contingency Overloads & step 3 in Managing Constraints in SCED Updated step 3 Added Canceling RUC Commitments Added 3rd Note | November 1, 2011 |
| 2.3 3.1 4.1 4.4 4.5 4.6 6.1 7.1 8.1 8.3 | 1.0 / 4 1.0 / 1 1.0 / 12 1.0 / 6 1.0 / 5 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 3 1.0 / 3 | Updated step “Site Failover” Updated step “Review” Updated step 4 in Post-Contingency Overloads & added new procedure Post-Contingency Overloads on PUNs Updated 1st Note Updated step Status Change in SPS, step 1 in Remedial Action Plan (RAP) & Mitigation Plan (MP) Deleted 1st Note, changed titles to Manual Dispatch to take a Unit Off-line, Manual Dispatch to take a Unit of a CC Off-line, & updated procedure, changed title to Manual Dispatch to bring a Unit of a CC On-Line, & updated procedure Updated 2nd note and step 1 in Voltage Security Assessment Tool (VSAT)Updated Post in “Scripts” Added 2nd NOTE Updated OCN All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 2.1 2.3 3.4 4.1 4.2 7.4 10.1 | 1.0 / 1 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 13 1.0 / 5 1.0 / 3 1.0 / 2 | Updated Scope Changed TSP to TO Updated database load script Changed insecure state to emergency condition Updated 1st Note, steps 6 & 8 in Post Contingency Overloads, steps 2 & 3 in Managing Constraints in SCED, added Model Inconsistencies/Updates procedure Updated Notes 1 & 2, Steps 1 & 2 Changed insecure state to emergency condition Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 3.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.5 9.2 10.1 | 1.0 / 2 1.0 / 2 1.0 / 6 1.0 / 14 1.0 / 6 1.0 / 8 1.0 / 7 1.0 / 6 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 8 1.0 / 8 1.0 / 7 1.0 / 7 1.0 / 4 1.0 / 5 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated Operations Support Engineer Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, added 3rd Note, updated step 1 in Review Planned Outage Notes, steps 1, 2, 3, 4, 6, 7, 8, 9 & QSGR in Post Contingency Overloads, step 2, 4 & Log in Managing Constraints in SCED Updated Operations Support Engineer Updated Operations Support Engineer & step 1, 2 & 3 Updated Operations Support Engineer Updated Desktop Guide reference, 2nd Note, step 5 & SPS Posting & deleted step 4 in SPS, all steps in Mitigation Plan & Temporary Outage Action Plan Updated Desktop Guide reference Updated step 1 in Watch Updated TSP to TO, Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer, changed TSP to TO, Desktop Guide reference & step 1 of Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) Updated step 1 in Watch Updated step 1 in Implement EEA Level 1 & step 1 in Implement EEA Level 3 Updated script in step 1 in Restore Firm Load Updated Operations Support Engineer & Desktop Guide reference Updated Operations Support Engineer & Desktop Guide reference Updated Desktop Guide reference Updated all steps in Telemetry Issues that could affect SCED and/or LMPs, step 1 in Backup/Alternate Control Center Transfer & Operations Support Engineer | March1, 2012 |
| 3.1 3.3 4.1 4.3 4.4 4.5 5.1 6.1 7.1 7.2 7.3 7.4 8.1 8.2 8.2 8.3 8.4 | 1.0 / 3 1.0 / 7 1.0 / 15 1.0 / 9 1.0 / 8 1.0 / 7 1.0 / 4 1.0 / 9 1.0 / 9 - / 8 1.0 / 8 1.0 / 5 1.0 / 4 1.0 / 0 1.0 / 4 1.0 / 2 1.0 / 4 | Updated step Gap Study Added TSAT Updated step 4 & deleted step 9 in Post-Contingency Overloads, clarified step 2 & 3 in Managing Constraints in SCED, Added Unsolved Contingencies Updated for TSAT tool, added Managing W-N during System Failures Updated step IROL and ‘instructing’ to ‘directing’ Updated step Status Change & ‘instructing’ to ‘directing’, updated step 3, 4 & log in RAP, added step 3 and log in PCAP, update Note, added TO Issue in MP Updated Opportunity Outage procedure Added Valley Import to VSAT procedure, deleted step 2 in PSS/AVR section Updated OCN, Advisory, Watch and Emergency Notice for Cold Weather and Extreme Cold Weather Added Load Management Programs in Implement EEA Added Load Management Programs in Restore EEA Updated for NPRR405 Changed ‘TDSP’ to ‘TO’ & T/S Operator to Real-Time Deleted Cold Weather Revised to 8.2 and changed Severe Cold Weather to Extreme Cold Weather Revised to 8.3, added OCN & Emergency Notice Revised to 8.4 and changed T/S Operator to Real-Time Operator | May 1, 2012 |
| 2.3 4.1 4.5 6.1 7.2 7.3 7.5 | 1.0 / 6 1.0 / 16 1.0 / 8 1.0 / 10 1.0 / 9 1.0 / 9 1.0 / 6 | Updated Database load with W-N active and Site Failover with W-N steps Added Constraint SF Cut Off step, updated step 2 & 3 in Managing Constraints in SCED Updated 2nd Note, added Basecase continuous SPS triggering step in SPS, updated step 1 in RAP, step Note, SCED unable to fully resolve constraint, & < 2% Absolute Shift Factors in MP, 1st Note in TOAP Updated step Valley Import Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated step 1 in ERCOT picks up Load for Non-ERCOT System and step 1 in Non-ERCOT System picks up Load for ERCOT | June 1, 2012 |
| 1.3 3.3 4.1 4.4 5.1 6.1 7.1 7.2 7.3 8.3 9.2 | 1.0 / 1 1.0 / 8 1.0 / 17 1.0 / 9 1.0 / 5 1.0 / 11 1.0 / 10 1.0 / 10 1.0 / 10 1.0 / 3 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated step 2 Updated step Constraint SF Cut Off, Managing Congestion during SCED Failure Updated step ≤300MW Updated Maintenance Level 2 and 3 outages Updated STP Voltage Tables Updated all step 1’s Updated Load Management Program Updated step 1 Updated scripts Updated 4th note | July 16, 2012 |
| 2.3 4.4 | 1.0 / 7 1.0 / 10 | Added Note to step Database Load Updated step IROL | August 29, 2012 |
| 2.3 2.4 3.3 4.1 4.3 4.4 4.5 4.7 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 8 1.0 / 2 1.0 / 9 1.0 / 18 1.0 / 10 1.0 / 11 1.0 / 9 1.0 / 3 1.0 / 12 1.0 / 11 1.0 / 11 1.0 / 11 1.0 / 6 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 5 | Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated PUN section and added to make call to HHGT Added Hotline script and to make call to HHGT Added Hotline script and to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Updated step 1 and added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT Added to make call to HHGT | September 12, 2012 |
| 2.2 3.1 3.2 3.3 3.4 4.1 4.3 4.4 4.5 5.1 5.2 6.1 7.4 8.3 9.1 | 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 10 1.0 / 2 1.0 / 19 1.0 / 11 1.0 / 12 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 13 1.0 / 7 1.0 / 5 1.0 / 4 | Added Hotline Call Communication Moved protective relay section to 5.2 Updated step 3 Split VSAT/TSAT and SE/RTCA out into separate procedures Updated steps Immediate Action Updated step Unknown Operating State, all steps in Evaluate Real-Time Contingency Analysis Results, steps 1, 4 & 6 in Post-Contingency Overloads Added 1st Note Added 1st Note, Updated 2nd NOTE & step 0 MW Updated 2nd Note Updated Returning from Planned Outage Early Added new procedure Updated Exceed URL, Reduce MW, added NOTE & moved step 1 to section 3.3 and renumbered Added Note Word smith OCN, Advisory, & Watch Updated step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.5 4.1 4.4 4.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 0 1.0 / 20 1.0 / 13 1.0 / 11 1.0 / 14 1.0 / 12 1.0 / 7 | Updated step 3 Added procedure Updated Note, Constraint Shift Factor Cut Off, Post-Contingency Overloads steps 4-9 , QSGR & Managing Constraints in SCED step 2 & 4 Updated step VSAT Updated Special Protection Systems (SPS) (Identified as RAS in EMS) step 2, Remedial Action Plan (RAP) steps 1-5, & step 3 Pre-Contingency Action Plan (PCAP) Updated 2nd Note and steps 1-3 Voltage Issues Deleted step 2 per NPRR 480 Updated all step 1’s & added step 3 to clarify 6.5.9.5.2(1) | March1, 2013 |
| 2.3 2.4 3.1 3.3 3.5 4.1 4.2 4.3 4.4 4.5 4.6 4.7 5.1 6.1 7.1 7.2 7.3 7.4 7.6 8.1 8.2 8.3 8.4 | 1.0 / 9 1.0 / 3 1.0 / 5 1.0 / 11 1.0 / 1 1.0 / 21 1.0 / 7 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 7 1.0 / 15 1.0 / 12 1.0 / 13 1.0 / 12 1.0 / 8 1.0 / 4 1.0 / 6 1.0 / 6 1.0 / 6 1.0 / 6 | Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts and steps in Caution, Phase Shifters, Constraint Shift Factor Cut Off, Post Contingency Overloads, deleted Input Displays, added step In Series & Same Element in Managing Constraints in SCED & deleted Managing Congestion during SCED Failure Updated step 2 Deleted 2nd Note, added GTL and updated scripts Deleted 2nd Note, added GTL and updated scripts Deleted Directives, 1st Note in Mitigation Plan, 1st Note in Temporary Outage Action Plan and updated scripts Updated scripts Updated all steps and deleted Cancelation Updated script Updated script Added Generic script and Specific scripts Updated scripts Updated scripts Updated scripts Updated script Updated scripts Updated script Updated script Correct spelling and updated script | June 1, 2013 |
| 2.3 4.1 4.2 4.3 4.4 4.5 4.6 4.7 4.8 7.1 7.2 7.4 7.5 | 1.0 / 10 1.0 / 22 1.0 / 9 1.0 / 8 1.0 / 13 1.0 / 15 1.0 / 13 1.0 / 9 1.0 / 5 1.0 / 13 1.0 / 14 1.0 / 8 1.0 / 5 | Updated step EMS Changes and added MMS Changes Updated step Caution Updated and moved section 7.4 and renamed to 4.2 Changed section # Updated and changed section # Changed section #, IROL & updated step 0MW Changed section # & updated step 4 in RAPs Changed section # Changed section # Updated step 1 in Watch, Emergency Notice & DRUC Timeline not Met Updated 2nd Note Changed section # & step 2 Changed section # | July 15, 2013 |
| 2.3 4.1 4.2 4.5 6.1 7.1 | 1.0 / 11 1.0 / 23 1.0 / 10 1.0 / 16 1.0 / 16 - / 14 | Spelling correction to step MMS Changes Updated Caution, Constraint Shift Factor Cut Off, step 8 of Post-Contingency Overloads & PUN procedure Removed the word “load” Updated step VSAT Updated 2nd note & step 1 on Voltage Security Assessment Tool (VSAT) Updated Specific Scripts EMMS (LFC and RLC/SCED) Failure | August 9, 2013 |
| 2.3 2.4 3.3 3.5 4.1 4.2 4.4 4.5 4.6 4.8 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 | - / 12 - / 4 - / 12 - / 2 - / 24 1.0 / 11 1.0 / 14 1.0 / 17 1.0 / 14 1.0 / 6 1.0 / 15 1.0 / 15 1.0 / 13 1.0 / 6 1.0 / 7 1.0 / 7 1.0 / 7 1.0 / 7 | Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference Removed HHGT TO reference | August 30, 2013 |
| 4.1 5.1 6.1 | 1.0 / 25 1.0 / 8 1.0 / 17 | Updated step 5 in Post-Contingency Overloads Updated to reflect SCR770 changes Updated script and added new script for Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | September 27, 2013 |
| 3.3 3.4 3.5 4.1 4.2 4.4 4.5 4.6 4.7 4.8 4.9 5.1 5.2 6.1 7.1 7.2 7.3 7.5 8.1 8.2 8.3 8.4 9.2 10.1 | 1.0 / 13 1.0 / 3 1.0/ 3 1.0 / 26 1.0 / 12 1.0 / 15 1.0 / 18 1.0 / 15 1.0 / 10 1.0 / 7 1.0 / 0 1.0 / 9 1.0 / 1 1.0 / 18 1.0 / 16 1.0 / 16 1.0 / 14 1.0 / 7 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 8 1.0 / 4 1.0 / 4 | Updated Log steps Updated Log steps Updated Log step Updated step 1 on Review Planned Outage Notes, step 1 for PUNs, Managing Constraints in SCED and Logs Updated Title, added step 2 and Log steps Deleted step GTL, updated step 1 and Log Updated step VSAT, Log and deleted GTL Updated Log steps Updated Log steps Updated Log steps Added new procedure Updated steps Definition, Approve Maintenance Outage, Coordinate Maintenance, Coordinate Maintenance Level 2 and 3, Log and step 1 in Simple Transmission Outage Updated Log steps Updated VSAT section Updated Log steps Updated Log steps Added step Reserves and Log steps Updated Log steps Updated note, OCN, Advisory and Log step Added note, updated OCN, Advisory, Watch and Log step Added note, updated OCN, Advisory, Watch and Log step Updated note and Log step Updated Log steps Updated Log steps All procedures in this manual have been reviewed | December 13, 2013 |
| 4.2 4.4 4.5 4.6 4.7 4.8 4.9 4.10 7.1 | 1.0 / 13 1.0 / 16 1.0 / 19 1.0 / 0 1.0 / 16 1.0 / 11 1.0 / 8 1.0 / 1 1.0 / 17 | Updated 1st Note, step 3, added step 4 & deleted step 5 in Transmission Issues within ERCOT. Added Note to Transmission/Capacity Issues within the CFE Area Removed posting requirement Removed posting requirement New procedure for new GTL Updated section number Updated section number Updated section number Updated section number & changed Watch to OCN Updated to incorporate NPRR542 and update scripts | January 1, 2014 |
| 4.1 4.2 4.6 7.3 8.4 | 1.0 / 27 1.0 / 14 1.0 / 1 1.0 / 15 1.0 / 9 | Updated step 3 in Post-Contingency Overloads Updated step 3, 4 in Transmission Issues within ERCOT and step 1, 2 & 3 in Transmission/Capacity Issues within the CFE Area Updated step 1 & 2 Updated steps Reserves and 1 in Restore Firm Load Updated 1st Note | February 25, 2014 |
| 4.1 4.2 4.4 4.5 4.8 6.1 7.2 7.4 9.1 | 1.0 / 28 1.0 / 15 1.0 / 17 1.0 / 20 1.0 / 12 1.0 / 19 1.0 / 17 1.0 / 9 1.0 / 5 | Updated VDI information Updated steps in Transmission Issues within ERCOT Updated VDI information Updated VDI information Updated Manual commitment process Updated VDI information Updated media appeal language & LM Program Updated VDI information Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 4.1 4.2 4.4 4.6 4.7 4.9 6.1 7.1 8.1 | 1.0 / 2 1.0 / 29 1.0 / 16 1.0 / 18 1.0 / 2 1.0 / 17 1.0 / 9 1.0 / 20 1.0 / 18 1.0 / 9 | Added VDI to Master QSEs Updated step 1 in Review Planned Outage Notes, QSGR & Log in Post-Contingency Overloads & PUN steps Updated section title & step 5, deleted step 3 Updated step 2 Updated step 1 & 2 Updated step 1 in RAP Deleted Note Updated Note & Step 1 in Voltage Issues Added Note, updated Market Notices Advisory & Watch Updated scripts | June 1, 2014 |
| 4.1 4.2 4.7 7.2 | 1.0 / 30 1.0 / 17 1.0 / 18 1.0 / 18 | Changed WGR to IRR & updated desktop reference Updated step 4 & 6 Updated 1st Note Added Media Appeal & updated step 1 script | August 1, 2014 |
| 4.1 5.1 6.1 7.1 | 1.0 / 31 1.0 / 10 1.0 / 21 1.0 / 19 | Updated desktop reference number & step 3 in Post-Contingency Overloads, added step 4 to PUN section Updated desktop reference number Updated step 1, 2 & 3 in Real-Time Voltage Issues, added Future Voltage Issues Updated Generic Script | October 1, 2014 |