- Power Operations Bulletin # 691

ERCOT has posted/revised the Reliability Unit Coommitment  manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 4.4.8 | 5.1 | 5.3(3) | 5.5.1 |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3 | 6.1(2) | 6.4.9.1.2 |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R1 & R11 |  |  |  |

| Version: 1 | Revision: 20 | Effective Date: December 15, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages - Monitor the HRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published. IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for HRUC are invalid, - Notify the Manager, - ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: - All load forecasts seem unreasonable; THEN: - Select the most reasonable forecast, AND - Call the Load Forecasting group for guidance on updating the weather or load forecast - Notify by e-mail the following distribution lists of the issue: - Load Forecasting & Analysis - 1 ERCOT Shift Supervisors |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS_DEV folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on WGR’s or Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue an electronic VDI - (priority should be given to WGRs and Resources that resolve congestion - Choose “DECOMMIT” as the Instruction Type from Resource tab - Enter “ERCOT requested decommit/capacity surplus” in Other Information. - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| A/S Infeasibility | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: - Undeliverable Ancillary Service are indicated; THEN: - Determine if the infeasibility is valid IF: - Valid; THEN: - Notify the affected QSE for the following information - the amount of A/S that must be reduced, and - the start and stop times of the reduction. - The QSE can substitute or ERCOT can open a SASM IF: - The QSE elects to substitute; THEN: - Determine the feasibility of the substitution. - If deemed infeasible, a SASM can be opened - Notify the Resource Operator of possible infeasibility issue. |
| A/S Insufficiency from SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - A/S Insufficiency; THEN - If deemed necessary, commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, - Refer to Desktop Guide RUC Section 2.18. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to transmission constraints; THEN: - Notify the Resource Operator. |
| STNET Study | Each hour run a STNET study for four hours out (example it is 0100, run study for 0500) to review voltage violations. IF: - Voltage contingencies or unsolved contingencies exist; THEN: - Check “Voltage Tracking Issues spreadsheet” on Sharepoint to ensure the contingency is not listed. - If not listed, convey the voltage violations to the Transmission and Security Operator - Create a savecase, use naming convention “SC_RUC(HE)_(DATE) - Make detailed log entry of what violations were passed to the Transmission and Security Operator. If it is the same violations from the previous hour, enter “no new voltage violations”. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually commit resources as needed Refer to Desktop Guide RUC Section 2.14. |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: - HRUC recommends the commitment of any unit; THEN: - Determine the validity, - Determine the temporal constraints for each of the units. IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason, IF: - There is a reliability reason requiring the resource commitment decision to be made immediately; - Resources returning from outages - Congestion or Capacity deficiencies that are creating HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, and uncommitting, otherwise a message window will pop up in DSP approval process. Examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Capacity - Constraint name (SLWSCRL5) * Do not use special characters Give a courtesy call to the QSE when commitments are made. |
| RMR Resources | QSEs will show a COP status of OFF when Resources are available. RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| RMR Commitment | WHEN: - HRUC recommends a RMR unit, AND - A capacity reserve shortage is projected and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; THEN: - Determine if an RMR Resource will need to be considered in HRUC Study Period; ISSUE: - Watch for projected reserve capacity shortage with no market solution; THEN: - Ensure COP status is “OFF” and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event; SELECT: - Commit Resource before HRUC is approved - Commit Resource, - List reason (RMR for Capacity). Call QSE with any modification to the Delivery Plan as a result of a commitment. |
| Hotline | Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Notify Transmission Operator to make Hotline call to TOs. |
| Post | Typical MIS posting: ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. |
| Cancel | WHEN: - Committed RMR Resources are off-line THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for a projected reserve capacity shortage with no market solution available. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: - Additional resources are needed to solve for transmission issues (such as for voltagesupport) and were not picked up in the HRUC run; THEN: - Commit unit before HRUC is approved - Change ‘blank’ to ‘Commit’, - List reason (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided. - Give courtesy call to QSE when commitments are made Note: Consider the need to commit Resources for preoperational warming in cases of extreme cold weather. |
| NOTE | - Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. - ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. - If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. - QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If HRUC recommends decommitments; Determine if: - Outage related, - Possible Network Model error/ Normal Breaker status variances, - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort, THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’), a message window will pop up in DSP approval process if no reason is provided - If Decommitment is error related: - No action is required |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |
| ### VSAT and RUC perform AC Analysis |  |
| NOTE | IF: - RUC cannot complete the process; THEN: - Notify the Transmission & Security Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The HRUC results are reasonable and after all necessary modifications have been made; THEN: - Approve the results (all RUC commitment, operator manual commitment/decommit/blank out must have a reason, otherwise a message window will pop up), OR IF: - The results are unacceptable; THEN: - Click on Disapprove button, AND - Follow the Manage HRUC Timeline Failure in the next section. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>HRUC> HRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>HRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue VDIs to cancel RUC instructions - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| Log | Log actions taken. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 4.4.8 | 5.1 (9) | 5.3(3) | 5.5.1(9) |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3(2) | 6.4.9.1(3) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 21 | Effective Date: December 15, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with Market Operations and Operations Support Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published, IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for DRUC are invalid, - Notify the Manager of System Operations and/or Control Room Operations Manager immediately, - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “Manage Capacity Insufficiency” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager Component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to Desktop Guide RUC Section 2.6, step 5. |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour, - Any under/over generation; THEN: - Be aware of these when running HRUC. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Notified from Market Operations of A/S Insufficiency from DAM; THEN - Issue a Watch to QSEs - Notify Transmission Operator to make Hotline call to TOs - Verify Market Operations has posted message on MIS Public - Refer to Desktop Guide RUC Section 2.1. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to A/S insufficiency in DAM for operating day [day]. The A/S insufficiencies will be procured in DRUC. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. WHEN: - A/S offers are committed in DRUC; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the Watch due to A/S insufficiency in DAM for operating day [day]. A/S insufficiencies were procured in DRUC. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required, - Valid; THEN - Locate the constraint on the DSP Constraint Summary display, - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, - Commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit; THEN - Determine the validity, - Determine the temporal constraints for each of the units, IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason. IF: - There is reliability reason requiring the resource commitment decision to be made immediately; - Resources with long start-up times - Resources returning from outages - Congestion or Capacity deficiencies that may create HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, uncommitting, examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Constraint name (SLWSCRL5) * Do not use special characters Give a courtesy call to the QSE when commitments are made. |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS_DEV folder: - “6 DRUC Capacity” which is based on the last ran DRUC VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision can be made in the future, THEN: - Issue OCN for Excess Reserve Capacity - Notify Transmission Operator to make Hotline call to TOs - Post message on MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting: ERCOT issued an OCN due to a projected excess reserve capacity for [HE XX – HE XX]. WHEN: - Projected excess reserve capacity; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| DRUC Committed For Capacity Shortage | IF: - DRUC recommends Resource(s) for capacity; THEN - Determine if start-up time allows enough time to re-evaluate, and - De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: - Issue an OCN for projected reserve capacity shortage - Notify Transmission Operator to make Hotline call to TOs - Post message on MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]. ERCOT will commit Resources as needed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting: ERCOT issued an OCN due to a projected capacity shortage for [HE XX – HE XX]. WHEN: - Projected reserve capacity shortage no longer exist; THEN: - Making hotline call to QSEs - Cancel MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the OCN for [date] due to a projected reserve capacity for [HE XX – HE XX]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Additional resources are needed to solve for transmission issues (such as voltage support) and were not picked up in the DRUC run, - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period, OR - A Resource was given a WRUC instruction and chose not to self-commit for all hours needed; THEN: - Change ‘blank’ to ‘Commit’ - List reason (capacity, constraint name or voltage issue). - Give courtesy call to QSE when commitments are made Note: Consider the need to commit Resources for preoperational warming in cases of extreme cold weather. |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments; DETERMINE IF: - Outage related’ - Possible Network Model error’ - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort; THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made; THEN: - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button - Follow the Manage DRUC Failure/Timeline Deviation procedure. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>DRUC> DRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>DRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue VDIs to cancel RUC instructions - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed and needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue VDI to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |

## 6.2	EEA

Procedure Purpose: To commit Resource that can be brought On-Line within the timeframe of the emergency.

| Protocol Reference | 3.9.1 | 6.5.9.4 | 6.5.9.4.1 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1 |  |  |  |
| NERC Standard | COM-002-2 R1, R1.1, R2 | EOP-001-2.1b R2.1, R2.3, R3.1, R3.2, R3.3, R4, R5 | EOP-002-3.1 R1, R2, R4, R6, R7 | EOP-003-2 R1, R5 |

| Version: 1 | Revision: 1 | Effective Date: December 15, 2014 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - A Generation Resource (without Non-Spin obligation) which has a unit status of OFF or EMR and can be brought On-line within the timeframe of the emergency; THEN: - Issue a VDI to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) - Enter “capacity” in “other information” - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| 2 | IF: - If Frontera can be switch from CFE into ERCOT within the timeframe needed; THEN: - Notify QSE for Frontera of the need to switch the generation from CFE into ERCOT - Issue RUC instruction |
| 3 | IF: - A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: - Issue a VDI to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) - Enter “capacity” in “other information” - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficiency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficiency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | - / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 - / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 - / 12 - / 7 - / 6 - / 14 - / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |
| 2.2 3.2 4.3 | 1.0 / 1 1.0 / 13 1.0 / 15 | Added Hotline Call Communication Updated Manual Commitment and Validate Updated Manual Commitment and Validate All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.3 4.3 4.6 | 1.0 / 9 1.0 / 16 1.0 / 5 | Added Blackstart Availability Updated Review Updated steps SASM not able to Procure all A/S Requested & Cancel Emergency Notice | March 1, 2013 |
| 3.1 3.2 3.3 3.5 3.7 4.3 4.4 4.5 4.6 5.2 6.1 | 1.0 / 6 1.0 / 14 1.0 / 8 1.0 / 4 1.0 / 1 1.0 / 17 1.0 / 9 1.0 / 4 1.0 / 6 1.0 / 5 1.0 / 11 | Updated step Deselect Contingencies Updated step Monitor, Excess Generation, Hotline, & Cancel Updated step Failure & Create Save Case Updated step REG/RRS Updated all steps Updated 1st Note, A/S Insufficiency from DAM, Excess Generation &DRUC Committed from Capacity Shortage Updated all steps Updated all steps Updated all steps Updated step Create Save Case Updated Notifications | June 1, 2013 |
| 3.5 4.3 4.4 4.6 6.1 | 1.0 / 5 1.0 / 18 1.0 / 10 1.0 / 7 1.0 / 12 | Correct typo in script Correct typo’s in scripts Updated Delay of DRUC steps Corrected reference in desktop guide Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.2 3.3 | 1.0 / 15 1.0 / 9 | Updated step HRUC Committed Units, Manual Commitment, HRUC Decommitted Resources & Approval Updated step Create Save Case | August 9, 2013 |
| 3.2 4.3 5.1 5.2 | 1.0 / 16 1.0 / 19 1.0 / 2 1.0 / 6 | Updated steps Violated Constraints, HRUC Committed Units, RMR Commitment & Manual Commitment Updated steps Violated Constraints, DRUC Committed Units & Manual Commitment Updated titles Updated Violated Constraints, Disapprove & Log. Deleted Long Lead Times, All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.3 4.4 4.6 6.1 | 1.0 / 10 1.0 / 11 1.0 / 8 1.0 / 13 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 and 529 | January 1, 2014 |
| 2.3 3.2 3.3 3.6 4.3 6.2 6.3 | 1.0 / 10 1.0 / 17 - / 11 1.0 / 1 1.0 / 20 1.0 / 0 1.0 / 2 | Updated Review and Select Load Forecast Updated step System Summary, HRUC Committed Units & VDI information Updated VDI information Added Manual Commit of a Resource & Canceling RUC Commitments Updated VDI information Updated DRUC Committed Units & VDI information Added new EEA procedure Change section number from 6.2 to 6.3 | April 4, 2014 |
| 2.2 2.3 2.4 2.5 3.2 3.6 4.5 4.6 5.2 6.1 | 1.0 / 2 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 18 1.0 / 2 1.0 / 5 1.0 / 9 1.0 / 7 1.0 / 14 | Added VDIs to Master QSEs Added Note to Increasing A/S before Publishing Added Note Updated Monthly MIS Posting step Updated step A/S Infeasibility Updated step 1 Updated step A/S Insufficiency Offers Updated DAM Failure Updated step Disapprove Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.2 6.1 | 1.0 / 19 1.0 / 15 | Updated Undeliverable A/S Capacity, added STNET Study and title change on VSAT and RUC perform AC Analysis Updated Generic Script | October 1, 2014 |
| 3.2 3.2 4.3 6.2 | 1.0 / 20 1.0 / 20 1.0 / 21 1.0 / 1 | Updated step STNET Study, HRUC Committed Units & Manual Commitment Updated STNET Study, HRUC Committed Units & Manual Commitment Updated step DRUC Committed Units & Manual Commitment Added step All procedures in this manual have been reviewed | December 15, 2014 |