- Power Operations Bulletin # 698

ERCOT has posted/revised the Real Time manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.2	Communication

Procedure Purpose:  To ensure that three part communication is used for all directives and ensuring all QSEs receive Hotline calls.

| Protocol Reference | 6.5.7.8(4) | 6.5.7.8(6) | 6.5.7.8(10) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Three-Part Communication |  |
| NERC | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall use three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any of the three parts is a NERC Reliability Standard Violation. |
| 2 | Many scripts have been placed throughout these procedures as a reminder of three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| ### Hotline Call Communication |  |
| 1 | When making Hotline calls, verify that every QSE has answered. IF: - Not every QSE answered the Hotline; THEN: - Contact them using their OPX line or LD line to provide them with the message - Inquire why they were not on the Hotline call - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
|  | Log all actions. |
| ### Dispatch |  |
| Definitions | - Dispatch is the act of issuing Dispatch Instructions. - A Dispatch Instruction is a specific command issued by ERCOT to a QSE or TO in the operation of the ERCOT System. When appropriate, an electronic dispatch instruction is issued. |
| ### Verbal Dispatch Instruction (VDI) |  |
| Definition | - A Dispatch Instruction issued orally. |
| ### Master QSE |  |
| 1 | Issue the VDI to the Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources as deemed necessary by ERCOT to effectuate actions for the total Generation Resource for instances when electronic Dispatch Instructions are not feasible. |
| LOG | Log all actions. |

## 3.1	Frequency Control Operating Procedure

Procedure Purpose: Frequency should be maintained within +/- 0.03 Hz of schedule in an attempt to maintain CPS1 scores over 100.

| Protocol Reference | 6.5.7.6.1 | 6.5.7.6.2.2(7) | 6.5.9.1(1)(b) |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4 | 2.2.8 |  |  |
| NERC Standard | BAL-002-1 R2.4, R6 | BAL-005-0.2b R8 | BAL-007 (Field Trial) | EOP-002-3.1 R5, R6.1 |
|  | NUC-001-1 |  |  |  |

| Version: 1 | Revision: 18 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Maintain System Frequency |  |
| Objective | - Frequency should be maintained within +/- 0.03 Hz of schedule - Attempt to maintain CPS1 scores over 100 - Frequency Bias set to 707MW/0.1Hz |
| CPS1 less than 100 | IF: - Performance drops below 100 for over three consecutive hours; THEN: - LOG the event and the possible cause of the poor performance. |
| BAAL | Corrective action shall be taken whenever the clock-minute average ACE is outside its clock-minute average Balancing Authority ACE Limit (BAAL). This is to ensure that the Balancing Authority ACE does not remain outside the BAAL for more than 30 consecutive clock-minutes. Performance under BAAL will be captured under the following: BAALHigh – effective when Actual Frequency is greater than 60 Hz. ERCOT ISO BAALHigh = 60.09 HZ = 636 MW BAALLow – effective when Actual Frequency is less than 60 Hz. ERCOT ISO BAALLow = 59.91 HZ = -636 MW |
| Criteria | Performance under the BAAL criteria for the yearly incentive plan will have the following levels of performance: - Level 1: Average of the 12 Monthly Maximum Durations not to exceed 25 minutes, - Level 2: Average of the 12 Monthly Maximum Durations not to exceed 17 minutes, - Level 3: Average of the 12 Monthly Maximum Durations not to exceed 14 minutes, - Exceeding the BAAL for 30 consecutive minutes is a NERC Reliability Standard Violation |
| Caution | NEVER (unless directed by EMMS Production or Support Engineer): - Change other tuning parameters (including QSE ramp rates, dead bands, thresholds, gains, time constraints) |
| Base Point Deviation | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Area Status>Related Displays>Expected Generation and Load Details Not-Tracking Units tab IF: - A QSE has a Resource with a large Base Point deviation (not tracking unit flag), AND - Their generation is not moving in the proper direction to correct their Base Point Deviation; THEN: - Notify the QSE of the issue. |
| Frequency Deviations | IF: - Frequency deviations are equal to or greater than +/- 0.10 Hz, OR - Sudden loss of generation greater than 450 MW; THEN: - Ensure frequency recovers to pre-disturbance within 15 minutes - Manually run SCED or use offset as needed. LOG: - Log the following information: - Possible reasons, if known (Base Point deviation, large schedule change, unit trip, etc.) - If unit trip: - Time of unit trip, - Name of unit, - Approximate net MW on unit, - Approximate lowest TrueTime frequency (use 3 decimals), - Amount of RRS deployed (if any), AND - Approximate ERCOT load. |
| Hydro Generation Operating in Synchronous Condenser Fast Response Mode | IF: - Hydro Resources operating in synchronous condenser fast-response mode who provide MW to the System in response to a frequency event without a Responsive Reserve deployment; THEN: - QSE will request VDI(s) - Choose Resource tab - Choose requesting QSE for Participant Name - Choose Resource name - Enter MW amount deployed in Current Operating Level - Choose Other For Resource for Instruction Type - State Hydro deployed in response to frequency in Other Information - Initiation Time, and - Completion Time - Confirm with Market Participant electronic VDI received. When issuing a VDI or when confirming the receipt of an Electronic VDI ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - A VDI will be needed for each Resource IF: - QSE contacts ERCOT to determine if it is allowed to recall and reset; THEN: - ERCOT grants approval to come off-line once the frequency recovers to pre-disturbance level or 60 Hz, whichever is lower, OR - Request QSE to remain On-line - May not exceed 30 minutes per deployment for each frequency deviation or event - Shall not exceed two hours per a 12-hour period in aggregate unless an EEA is declared |
| ### Response to High Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| Monitor | IF: - Frequency goes above 60.05 Hz and exceeds 60.05 Hz > 5 minutes AND - Regulation Down service remains and is deploying; THEN: - Manually run SCED IF: - Frequency goes above 60.05 Hz, AND - Out of Down Regulation; THEN: - CHECK the GEN-LDL or Cap to decrease BP on the EMS to ensure there is adequate down room, - Enter manual offset (the offset will continue until removed). IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Request RUC Operator to issue electronic VDI |
| 10 MINUTES | REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Enter manual offset, - Manually run SCED (do not run SCED more than once between SCED runs). |
| Notify | If it is recognized that Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE above BAALHigh (60.09 Hz); THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to decrease Base Points GEN-LDL, - Re-adjust manual offset, - Manually run SCED, - Log the event and notify Operations Support Engineer to send an event notification to BAALfieldtrials@ercot.com. IF: - There is no generation left for SCED to lower; THEN: - Coordinate with the Shift Supervisor and Transmission Operator to select a Resource to decommit, - Request RUC Operator to issue electronic VDI |
| 20 Minutes | IF: - 20 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources that have positive Base Point deviations and instruct them to bring their Base Point deviations to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Request RUC Operator to issue electronic VDI |
| 25 Minutes | IF: - 25 consecutive minutes of ACE above BAALHigh (60.09 Hz) and Frequency is above 60.10 Hz; THEN: - Call QSEs with Resources with positive Base Point deviations and instruct them to bring their Base Point deviation to zero, - Coordinate with Shift Supervisor, Transmission Operator to select an additional Resource to decommit, - Request RUC Operator to issue electronic VDI |
| Stable | IF: - A manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Response to Low Frequency |  |
| BAAL Sheet | Located on realtime on ‘prwp056c’/_Operations Official Spreadsheets/BAL 007 ERCOT Interconnection and select Control T simultaneously. |
| NOTE | UFRs will deploy as follows: - Hydro RRS - 59.80 Hz - Load Resource providing RRS – 59.70 Hz |
| Monitor/ Deploy | IF: - Frequency drops below 59.95 Hz, AND - Regulation Up service remains and is deploying; THEN: - Manually run SCED (do not run SCED more than once between SCED runs) IF: - Frequency drops below 59.95 Hz, AND - Out of Up Regulation; THEN: - Check the GTBD2[HDL] on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS and enter appropriate manual offset - If using OpsMon Dashboard, do not enter an offset > than GTBD2[HDL] - If using EMS, do not enter an offset > than Cap to increase BP or HDL-Gen IF: - Frequency is below 59.95 Hz and out of Up Regulation, AND - GTBD2[HDL] on the OpsMon SCED GEN ONLINE Dashboard or Cap to increase BP or HDL-Gen on the EMS does not have adequate up room; THEN: - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. |
| 10 Minutes | REFERENCE DISPLAY: EMP Applications>Generation Unit Status>Related Displays>Expected Generation and Load Details>Top Ten button AND Market Operation>Real-Time Market>SCED Displays>DSI Displays>DSI Data Processes>DSI Generation Requirement Manual Adjustment IF: - 10 consecutive minutes of ACE is less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources with negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Confirm Responsive Reserve has been deployed, - Verify SCEDs capacity to increase Base Points, - Enter manual offset - If room is available - Manually run SCED IF: - There is no generation left for SCED to increase; THEN: - Confirm with the Resource Operator that Non-Spin has been deployed, - Manually deploy Responsive Reserve using the ERCOT Nodal Summary display on the EMS - Check the box labeled “Activate Manual Responsive Reserve” to activate, - Enter the “Desired RRS MW”, - Select Enter, - Select Commit. - QSE’s have one minute to update schedule to free up the capacity, SCED will automatically run after one minute. - Remember to remove the manual RRS amount when frequency has recovered. - Notify the Shift Supervisor of the need to possibly commit additional Resources. |
| Notify | If it is recognized that the Frequency is or expected to be outside +/- 0.1 Hz for a non-transient event and will not recover within 15 minutes, notify the Nuclear Power Plants QSEs. |
| 15 Minutes | IF: - 15 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available - Manually run SCED, - Log the event and notify Operations Support Engineer to send notification of the event to BAALfieldtrials@ercot.com. |
| 20 Minutes | IF: - 20 consecutive minutes of ACE less than BAALLow (59.91 Hz); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points (HDL-GEN), - Re-adjust manual offset, - If room is available, manually run SCED. |
| 25 Minutes | IF: - 25 consecutive minutes of ACE less than BAALLow (59.91 Hz ); THEN: - Call QSEs with Resources that have negative Base Point deviations and instruct them to bring their Base Point deviations to zero, - Verify SCEDs capacity to increase Base Points, - Re-adjusted manual offset, - Do Not enter an offset > than (HDL-GEN) - Manually run SCED. |
| Stable | IF: - RRS was manually deployed; THEN: - Uncheck the Activate Manual Responsive Reserve, IF: - An manual offset was used; THEN: - Ensure that it has been removed. |
| Log | Log all actions. |
| ### Monitor Frequency for the Loss of EMS or Site Failover |  |
|  | The ability to view an adequate Frequency source may be limited during a site-failover, database load, or if AGC is temporarily unavailable. To view the System Frequency during these conditions you may monitor the following sources. - ERCOT Control Room digital wall frequency displays - PI ProcessBook → ERCOT → TrueTime Frequency (Taylor) and/or - PI ProcessBook → ERCOT → TrueTime Frequency (Bastrop) It may be necessary to reload the PI ProcessBook “ERCOT Main Summary” display to show the historical data. |
| ### Actions When Frequency Telemetry is Incorrect |  |
|  | REVIEW REFERENCE DISPLAY: EMP Applications>Generation Control>Generation Area Status>Current Frequency Deviation from Nominal IF: - Frequency is believed to be incorrect; THEN: - Check the current Frequency and switch to a different source, - Select Skip on the incorrect Frequency device, - Contact the Help Desk. |

## 3.2	Monitor Large Ramp Events

Procedure Purpose:  The ERCOT Large Ramp Alert System (ELRAS) is designed to monitor the probability of large wind output ramps in the ERCOT region and provide ERCOT Operators with further situational awareness.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 5 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT Large Ramp Alert System (ELRAS) link: AWS primary web server site: http://products.meso.com/elras_dev AWS backup web server site: http://products-db.meso.com/elras_html The potential for a large ramp can be identified using the “Graphical Forecast” page of ELRAS forecast Real-Time Mode. An example of the page is in figure 1 below. The “Graphical Forecast” page plots the probability of a ramp rate event starting at a given time during the next 6 hours. The graphical displays are broken up into three timeframes; 15-minute probabilities, 60-minute probabilities, and 180-minute probabilities, and Up and Down ramp rate events are split up for each time frame. These displays are interpreted by first looking at a particular interval on a given display. The value for that interval on that display is characterized as the probability of a given MW change occurring over a specified amount of time starting at the specified interval. For example, looking again at figure 1, the “Graphical Forecast” is showing a 50% probability of at least a 2,000 MW increase occurring over 180 minutes starting at 18:00. In other words, between 18:00 and 21:00 there is a 50% chance that the aggregate wind output will increase by at least 2,000 MW. For the purpose of this procedure, the forecasted ramp rates to be considered significant are those that are indicated in Red; 1,000 MW in 15-minutes, 2,000 MW in 60-minutes, and 4,000 MW in 180-minutes. In the event that one of these ramp rates is forecasted to have at least a 30% probability of occurring, determine if the system has the ramp rate to keep up with the wind ramp. |
| 1 | IF: - The ELRAS tool does not forecast a ramp that you believe it should have; THEN: - Send an e-mail to “Operations Analysis” and “shiftsupv” |
| ### Down Ramp Event |  |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| 2 | IF: - There is a 30% probability of a projected system wide down-ramp of 4,000 MW within the next 180 minutes, OR - There is a 30% probability of a projected system wide down-ramp of 2,000 MW within the next 60 minutes; THEN: - Refer to the “180 min. HASL(COP) - LF or 60 min. HASL(COP) - LF” on the 60 to 180 minute OpsMon Dashboard to determine if system ramp rate capability is sufficient, AND - Make a Hotline call to provide situational awareness about a possible down-ramp event of 2,000 MW or greater within the next 60 minutes or 4,000 MW or greater within the next 180 minutes. IF: - System ramp rate is not sufficient; THEN: - Notify RUC Operator to procure Resources as needed. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN due to the forecasted probability of a [4,000 MW down-ramp in the next 180 minutes] [2,000 MW down-ramp in the next 60 minutes]. ERCOT is forecasting that the system ramp rate capability is [sufficient] [not sufficient]. [QSE] please repeat that back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | IF: - There is a 30% probability of a projected system wide down-ramp of 1,000 MW within the next 15 minutes; THEN: - Refer to the “HDL-Gen” on the 15 minute OpsMon Dashboard and the available Regulation UP Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Deploy Non-Spin as needed, and - Continue to monitor frequency and “HDL-Gen” |
| ### Up Ramp Event |  |
| NOTE | Up ramps should be self-mitigating since a majority of the wind generators have governor response capabilities. |
| 1 | PERIODICALLY REVIEW: - EMS Applications>Frequency>Frequency Dashboard - OpsMon Dashboard Viewer under the MOS folder: - “Monitor Large Ramp Events” |
| - 2 | IF: - There is a 50% probability of a projected system wide up-ramp of 2,000 MW within the next 15 minutes; THEN: - Refer to the “Gen - LASL” on the 15 minute OpsMon Dashboard and the available Regulation DOWN Service in the EMS Display, IF: - The margin is less than available to adequately maintain the potential system ramp rate; THEN: - Monitor frequency, Reg-Down and run SCED as often as required. |
| Log | Log all actions. |

## 3.5	Monitor Capacity and Reserves and Respond to Shortages or Surplus

Procedure Purpose:  Monitoring sufficient operating reserves.  Deploying and recalling Non-Spin and dealing with capacity surplus.

| Protocol Reference | 6.5.7.6.2.3 | 6.5.9.4.1 (c) | 6.5.9.4.1(d) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | BAL-002-1 R2.4 | IRO-005-3.1a R1.4, R1.5, R4 |  |  |

| Version: 1 | Revision: 11 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The Day-Ahead process, the Adjustment Period process, and the Real-Time process must be utilized before ordering Resources to specific output levels with Emergency Base Point instructions. |
| ## Insufficient Generation |  |
| RMR | Prior to declaring EEA, start RMR Units available in the time frame of the emergency. RMR Units should be loaded to full capability. |
| Deploying Non-Spin | Triggers to deploy Non-Spin MONITOR: - The OpsMon Dashboard - 01 SCED GEN ONLINE and scroll down to Lookahead Load Ramping from MTLF - Avail CAP 30Min represents (HASL – Gen) – (30 minute load ramp) IF: - Avail_CAP_30Min < 0 THEN: - Coordinate with the Resource Operator to deploy half of available Non-Spin. IF: - Avail_CAP_30Min < -300, OR - PRC is < 2500 MW; THEN: - Coordinate with the Resource Operator to deploy all of available Non-Spin. |
| Recalling Non-Spin | WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 2800 MW; THEN: - Coordinate with the Resource Operator to recall half of the deployed Non-Spin. WHEN: - Avail_CAP_30Min > 1000, AND - PRC is > 3000 MW; THEN: - Coordinate with the Resource Operator to recall all of the deployed Non-Spin. |
| HASL Release | Triggers to manually deploy RRS MONITOR: - “HASL – Load Ramp” value on the Generation Area Status display, this is HASL – (Gen + 5 minute load ramp) IF: - HASL – Load Ramp < = 200 MW; THEN: - Manually deploy 500 MW of RRS. - Ensure all Non-Spin has been deployed first before manually deploying the RRS. IF: - After Resources have responded to the previous deployment (if it has been at least 10 minutes), AND - HASL – Load Ramp < = 200 MW; THEN: - Manually deploy another 500 MW (it is incremental, enter 1,000). IF: - PRC < = 2000 MW; THEN: - Manually deploy all remaining RRS. |
| HASL Recall | WHEN: - HASL – Load Ramp > 1600 MW AND/OR - PRC > = 3300 MW, AND - Frequency is 59.970 HZ or above; THEN: - Manually recall the RRS, which can be done in 500 MW steps. |
| ## Surplus Generation |  |
| SCED Surplus | MONITOR: - The Generation Area Status Page IF: - (GEN-LDL) < 200 MW; THEN: - Consult with RUC Operator to ensure HRUC is seeing the situation and is decommitting Resources, - If needed, request the RUC Operator to issue VDI to decommit a Resource to help alleviate the surplus |
| Log | Log all actions. |
| ## Valley Generation |  |
| Monitor | Market Operations>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>Generator Outputs>Generation Schedule |
| 1 | WHEN: - Two or more Generation plants (DUKE, FRONTERA, NEDIN and/or SILASRAY) are scheduled to go Off-Line at the same time; THEN: - Discuss with Transmission and Security Operator AND Shift Supervisor - Ensure AEP TO is notified with the shut down time and with at least an hours’ notice, they need to pre-posture reactive devices. |
| Log | Log all actions. |

# 3.9	Unannounced Constant Frequency Control Testing

Procedure Purpose: This procedure provides direction and guidelines for conducting unannounced testing to verify a QSE’s capability to operate in CFC mode.  Only QSEs with at least 350 MW of spinning reserve room will be tested.  QSEs shall be tested at least every three years.

| Protocol Reference | 6.6.9 |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.4.3 |  |  |  |
| NERC Standard |  |  |  |  |

| Version: 1 | Revision: 0 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Testing will be coordinated with staff from Operations Analysis, they will select the QSE to test - EMMS Production personnel will be in the Control Room to take the EMS off AGC - The frequency bias can be found on the Generation Area Status display |
| START CFC Test | Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT is conducting an unannounced test to test your ability to operate on constant frequency control mode. The frequency bias to enter into your control system is [bias]. You have five minutes to switch to CFC mode then hold for 15 minutes. I will give another call when you can return to normal operation. [QSE] please repeat this back to me. That is correct, thank you.” |
| END CFC Test | Typical Script: “This is ERCOT operator [first and last name]. At [time], ERCOT is ending the unannounced constant frequency control test; please change your control mode back to normal. I will send you an electronic Dispatch Instruction that you will need to acknowledge. [QSE] please repeat this back to me. That is correct, thank you.” |
| ISSUE Electronic Dispatch Instruction | Issue electronic Dispatch Instruction: - QSE Level - Instruction Type: Operate at Constant Frequency - Confirm with Market Participant electronic Dispatch Instruction received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| LOG | Make log entry |

## 6.2	Extreme Cold Weather

Procedure Purpose: To ensure ERCOT and Market Participants are prepared for extreme cold weather operations.

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3(2)&(3) | 6.5.9.3.1(4) | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3 (6) | 6.5.9.3.4 (1) |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 10 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Extreme cold weather notifications will be issued when temperatures or wind chill is forecasted to be below freezing for sustained periods and may abnormally impact load levels or generation availability - For such events, additional reserves may be necessary |
| OCN | When approaching extreme cold weather is approximately 5 days away, using the Hotline issue an OCN to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for an extreme cold weather system approaching [time frame] with temperatures anticipated to remain 32°F or below. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance or returning from outage early, - Review and implement winterization procedures. Notify ERCOT of any changes or conditions that could affect system reliability. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Advisory | When approaching extreme cold weather is approximately 3 days away, using the Hotline issue an Advisory to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing an Advisory for the extreme cold weather system approaching [time frame] with temperatures anticipated to remain 32°F or below. QSEs are instructed to: - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Review Planned Resource outages and consider delaying maintenance or returning from outage early, - Review and implement winterization procedures. Notify ERCOT of any changes or conditions that could affect system reliability. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Watch | When approaching extreme cold weather is approximately 1 day away and concerns exists to escalate the notice, using the Hotline issue a Watch to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for the extreme cold weather system approaching [time frame]. Temperatures are expected to remain 32°F or below. QSEs are instructed to : - Make available, any Resources that can be returned to service and keep COPs and HSLs updated, - Review fuel supplies and notify ERCOT of any known or anticipated fuel restrictions, - Prepare for higher than usual loads and the possible need for additional Ancillary Services, - Review and implement winterization and emergency operating procedures, including utilization of Resource pre-warming techniques. Notify ERCOT of any changes or conditions that could affect system reliability. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Emergency Notice | When extreme cold weather has arrived and is beginning to have an adverse impact on the system, using the Hotline issue an Emergency Notice to all QSEs: Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an Emergency Notice, the extreme cold weather system is beginning to have an adverse impact on the system such as [state what the adverse impacts are]. QSEs are instructed to: - Make Resources available that can be returned to service and keep COPs and HSLs updated, - Keep ERCOT informed of known or anticipated fuel restrictions, - Notify ERCOT of any changes or conditions that could affect system reliability. ERCOT will continue to monitor the extreme cold weather system. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Post | Coordinate with the Transmission & Security Operator for the posting of the notices on MIS Public. |
| Cancel Posting | Coordinate with the Transmission & Security Operator for the cancelation of the postings on MIS Public. |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Prepares | November 10 , 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch, Foster and Hartmann | Procedure writers and editors | January 3, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 1, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy, Hartmann and Solis | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Drummond, Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.4 3.1 3.2 3.4 3.5 3.6 4.2 5.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated Categories and Priorities Updated Response to High Frequency steps 15, 20 and 25 minutes and Response to Low Frequency step 15 Updated steps Failure Indication/Issues and QSE Capacity Issues Updated steps AGC/RLC Issues, System Wide Capacity Issue and AGC/RLC Issues Resolved Updated step 1 Updated step Capacity Surplus Updated step 2, 3, 4 and 5 Updated all steps of “Implement Level 2B” | December 1, 2010 |
| 4.1 4.2 5.2 | 1.0 / 1 1.0 / 2 1.0 / 1 | Updated step “MP unable to Override” Updated step 1 & 2 Updated step 1 in sections WATCH and Advisory | December 15, 2010 |
| 3.1 3.2 3.3 3.4 4.1 5.1 5.4 | 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 | Updated step “BAAL” Updated step “AGC Issues Resolved” Updated step “Hotline” Updated step “Failure Indications, AGC/RLC Issues, System Wide Capacity Issue, AGC/RLC Issues Resolved” Updated step 2 in “Workflow Controller Messages”, added new procedure “Exceeding West – North Stability Limit”, updated Note in “Generation Resource Shut-down/Start-up Process” Updated step 1 in “Watch” and step Hotline in “Scripts” Updated step 1 in “Move from EEA level 3 to EEA lever 2B” | January 5, 2011 |
| 2.4 2.5 2.6 2.7 3.1 3.2 3.3 3.4 3.5 4.1 4.2 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 | 1.0 / 0 1.0 / 2 1.0 / 0 1.0 / 0 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure Changed procedure number Added new procedure Added new procedure Updated sections “Maintain System Frequency”, “Response to High Frequency”, “Response to Low Frequency” and “Actions when Frequency Telemetry in Incorrect. Combined sections 3.3, 3.4 & 4.2 into 3.2 Changed 3.5 “Potential DCS Event” to 3.3 & updated whole procedure Changed 3.6 “Monitor Capacity Reserves & Respond to Capacity Issues to 3.4 Changed 3.7 “Monitor and Control Time Error Correction to 3.5 & updated script Deleted Exceeding West-North Stability Limit Deleted Procedure Updated script Updated step 1 in “Advisory” and “Watch” Updated all steps Updated all steps Updated all steps Updated all steps Updated all steps Updated OCN | January 31, 2011 |
| 2.6 3.2 3.3 3.4 3.6 5.1 5.2 | 1.0 / 1 1.0 / 4 1.0 / 3 - / 3 1.0 / 0 1.0 / 3 1.0 / 3 | Updated step Site Failovers Updated step 3 in SCED Failure, step 4 in RLC Failure, Note in LFC (AGC) Failure and step 2 in EMS (LFC and RLC/SCED Failure Updated step 3 Updated step Capacity Shortage Added new procedure Updated Watch and Emergency Notice All step 1’s | March 25, 2011 |
| 2.6 3.1 3.2 3.3 3.6 5.1 5.4 5.5 | 1.0 / 2 1.0 / 4 1.0 / 5 1.0 / 4 1.0 / 1 - / 4 1.0 / 3 1.0 / 2 | Added steps and updated whole procedure Added new step to Maintain System Frequency and updated Response to High Frequency & Response to Low Frequency Updated steps 2, 3, 5 in SCED Failure; steps 2, 3, 4, 6 in RLC Failure; steps 1, 3 in LFC (AGC) Failure; steps 2, 5 in EMS (LFC and RLC/SCED) Failure Updated NERC Recovery Criteria, step 1 & 4 Updated 1st script Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B Updated step 3 | April 22, 2011 |
| 3.3 5.1 5.3 5.4 6.1 6.2 6.3 6.4 | 1.0 / 5 1.0 / 5 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 0 1.0 / 2 1.0 / 2 | Updated step NERC Recovery Criteria Updated all step 1’s Updated step 1 in Implement EEA Level 1, step 1 in Implement EEA Level 2A, added note and updated step 2 in Implement EEA Level 2B, step 1 in Implement EEA Level 3 Updated all step 1’s Updated all steps Added new procedure Updated section number and all steps Updated section number and all steps | June 8, 2011 |
| 2.6 3.1 5.1 5.2 5.3 5.4 8.1 | 1.0 / 3 1.0 / 5 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 5 1.0 / 1 | Added step If EBPs are needed”, updated step IF EBPs are needed and W-N was Active before site failover started Added step Hydro, updated step Frequency Deviations Updated step Watch Updated all steps Updated 1st note, step 1 in EEA level 1 & 2A Updated step 1 in Move for EEA level 1 to 0 Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.1 3.2 3.4 4.1 6.4 6.5 | 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 4 1.0 / 0 1.0 / 3 | Updated step Monitor, 15 minutes, 20 minutes and 25 minutes in Response to High Frequency Updated step 2 in LFC Failure, step 4 & 5in EMS Failure Updated step Capacity Surplus Updated step 2 in Workflow Controller Messages Added new procedure “Extreme Hot Weather” Changed section number | August 3, 2011 |
| 2.7 3.1 5.1 5.2 5.3 5.4 6.4 7.1 | 1.0 / 1 1.0/ 7 1.0 / 7 1.0 / 5 1.0 / 5 1.0 / 6 1.0 / 1 1.0 / 1 | Updated step Hotline Call Updated NERC Standard reference table Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated step 1 in Advisory & Watch Updated 2nd Note, step 1 in Implement EEA 1, step Media Appeal & 1 in Implement EEA 2A, 1st Note & step 2 in Implement EEA 2B Added Note to Move From EEA 3 to EEA 2B and Move From EEA 2A to EEA 1 Updated temperature from 102 to 103 Updated 4th note and step 1 | September 1, 2011 |
| 3.2 5.3 5.4 | 1.0 / 7 1.0 / 6 1.0 / 7 | Updated SCED Failure step 2 and 3, RLC Failure step 3 and LFC (AGC) Failure step 3 Combined EEA 2A & B per NPRR 379 Combined EEA 2 A & B per NPRR 379 | October 1, 2011 |
| 3.2 | 1.0 / 8 | Updated script for LFC and EMS Failure | November 1, 2011 |
| 2.4 2.6 4.1 5.1 6.3 | 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 8 1.0 / 3 | Added step Review, Updated “Site Failover with W-N Active” Added Note to Large Resource Trips or Runbacks Updated Post in “Scripts” Updated “OCN” and “Advisory” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 4.1 8.1 | 1.0 / 1 1.0 / 7 1.0 / 6 - / 2 | Updated Scope Updated Response to High Frequency & Response to Low Frequency Updated Large Resource Trips or Runbacks, Quick Start Generation Resource Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.1 5.1 5.3 7.1 8.1 | 1.0 / 1 1.0 / 8 1.0 / 7 1.0 / 9 1.0 / 7 1.0 / 2 1.0 / 3 | Updated paragraph 4 Updated BAAL Updated Desktop Guide reference & step QSE Override & QSE unable to Override Updated step 1 in Watch Updated Step 1 in Implement EEA Level 1 Updated Desktop Guide references Changed title names, updated steps 1 & 3 & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.2 3.3 3.5 4.1 5.1 6.2 6.3 6.4 8.1 | 1.0 / 2 1.0 / 9 1.0 / 9 1.0 / 6 1.0 / 2 1.0 / 8 1.0 / 10 1.0 / 4 1.0 / 2 1.0 / 4 1.0 / 4 | Changed TSO, DSP to TO Changed Shift Engineer to Operations Support Engineer, removed Automatic SCED Runs & Hydro Generation in Fast Response Mode, updated Note, Monitor/Deploy, 15 minutes, 20 minutes in Response to Low Frequency Updated step 2, 4 & 5, added SCED Data Input Failure, updated RLC Failure, LFC Failure, & EMMS Failure sections Updated Nerc Recovery Criteria step & step 3 Updated Requirements and Notes Changed Shift Engineer to Operations Support Engineer, deleted Large Resource Trips or Runbacks section Updated OCN, Advisory, Watch, Emergency Notice sections Deleted Cold Weather, replaced with Extreme Cold Weather Section changed to Extreme Hot Weather, added OCN and Emergency Notice steps Section number changed Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 3.1 3.4 5.2 | 1.0 / 10 1.0 / 5 1.0 / 6 | Added back step Hydro Generation Operating in Synchronous Condenser Fast Response Mode Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 2.6 5.3 5.4 6.3 | 1.0 / 5 1.0 / 8 1.0 / 8 1.0 / 3 | Updated Site Failover step Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 2.6 5.1 5.3 5.4 6.2 6.3 7.1 | 1.0 / 1 1.0 / 6 1.0 / 11 1.0 / 9 1.0 / 9 1.0 / 5 1.0 / 4 1.0 / 3 | Removed ERCOT Shift Supervisor paragraph Updated all steps Updated all step 1’s Updated 2nd note, added TCEQ, & XML for ERS Clarified LR and ERS recalls Updated script for Emergency Notice Updated script for Emergency Notice Updated 4th note | July 16, 2012 |
| 2.6 3.1 4.1 5.3 | 1.0 / 7 1.0 / 11 1.0 / 9 1.0 / 10 | Added note to step Database Load Updated Frequency Deviations and Monitor Frequency for the Loss of EMS or Site Failover Incorporated NPRR348 Added 30 MIN ERS and updated steps 1, 2 & 3 on Implement EEA Level 1 | August 29, 2012 |
| 2.2 2.5 3.5 4.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 10 1.0 / 11 | Added Hotline Call Communication Updated step 3 Updated per NOGRR100 Added Note to Shut-down/Start-up Process and new Combine Cycle Generation Resources section Updated ERS scripts All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.5 3.1 3.2 3.3 3.4 3.5 3.6 3.7 5.4 | 1.0 / 4 1.0 / 12 1.0 / 0 1.0 / 10 1.0 / 7 1.0 / 6 1.0 / 4 1.0 / 2 1.0 / 10 | Updated step 3 Updated BAAL New procedure, Monitor Large Ramp Events Updated section # & SCED failure step 2 Updated section # Updated section # Updated section # Updated section # Updated Cancel Watch All procedures in this manual have been reviewed. | March 1, 2013 |
| 2.6 2.7 3.1 3.2 3.3 3.4 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 | 1.0 / 8 1.0 / 2 1.0 / 13 1.0 / 1 1.0 / 11 1.0 / 8 1.0 / 3 1.0 / 11 1.0 / 12 1.0 / 8 1.0 / 12 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 6 1.0 / 5 1.0 /5 | Updated scripts Updated scripts Updated Monitor Frequency for the Loss of EMS or Site Failover & Actions when Frequency Telemetry is Incorrect Updated scripts Updated scripts Updated script Updated scripts Added QSGR Decommitment step to QSGR Added Generic and Specific scripts Updated Note and scripts Updated TCEQ section and scripts Updated scripts Updated scripts Updated scripts Updated scripts Updated scripts Correct spelling and updated script | June 1, 2013 |
| 2.6 3.1 3.2 3.8 5.1 5.3 5.4 | 1.0 / 9 1.0 / 14 1.0 / 2 1.0 / 0 1.0 / 13 1.0 / 13 1.0 / 12 | Changed title name & updated step EMS Changes & added MMS Changes Updated steps Base Point Deviation & 10 Minutes Updated 1st note Moved procedures from Resource desk Updated step 1 in Watch & Emergency Notice Updated step Pilot Project WS ERS Updated step Reserves | July 15, 2013 |
| 2.6 3.2 3.8 4.1 | 1.0 / 10 1.0 / 3 1.0 / 1 1.0 / 12 | Updated MMS Changes Updated 1st Note Updated Unit & Load RRS Shortage & Not Dispatchable to SCED Updated Shutdown/Startup | August 9, 2013 |
| 3.8 | 1.0 / 2 | Updated Unit RRS Shortage, Load RRS Shortage, REG Shortage, & added Real-Time Non-Spin Shortage | September 27, 2013 |
| 2.4 3.1 3.2 3.3 3.4 3.5 3.7 4.1 5.1 5.2 5.3 5.4 5.5 6.1 6.2 6.3 6.4 7.1 8.1 | 1.0 / 2 1.0 / 15 1.0 / 4 1.0 / 12 1.0 / 9 1.0 / 7 1.0 / 4 1.0 / 13 1.0 / 14 1.0 / 9 1.0 / 14 1.0 / 13 1.0 / 4 1.0 / 4 1.0 / 7 1.0 / 6 1.0 / 6 1.0 / 4 1.0 / 5 | Updated step Log Updated step Frequency Deviations & step Log Updated step Log Updated step Log Updated step Log Added step RMR & updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated step Log Updated note and step Log Updated step Log Added & updated step Log All procedures in this manual have been reviewed | December 13, 2013 |
| 2.6 3.3 5.1 | 1.0 / 11 1.0 / 13 1.0 / 15 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542, deleted West to North GTL and updated procedure for North to Houston to a new GTL | January 1, 2014 |
| 2.6 3.1 3.3 3.5 3.6 4.1 5.3 5.4 6.4 8.1 | 1.0 / 12 1.0 / 16 1.0 / 14 1.0 / 8 1.0 / 5 1.0 / 14 1.0 / 15 1.0 / 14 1.0 / 7 1.0 / 6 | Updated Site Failover Complete Updated VDI information, step Monitor/Deploy & step 10 Minutes in Response to Low Frequency Updated VDI information Updated VDI information Updated step Terminating Time Error Correction Updated VDI information Updated ERS, Media appeal, TCEQ and VDI information Updated steps Reserves and 1 in Restore firm load and step 2 in Move From EEA Level 2 to EEA Level 1 Updated Note Updated Requests to Decommit Self-committed Resource in Operating Period | April 4, 2014 |
| 2.2 3.1 3.3 4.1 5.1 5.2 6.2 6.3 | 1.0 / 2 1.0 / 17 1.0 / 15 1.0 / 15 1.0 / 16 1.0 / 10 1.0 / 8 1.0 / 7 | Added VDIs to Master QSEs Updated step BAAL Updated SCED Failure & SCED Data Input Failure steps Updated QSGR in Quick Start Generation Resource Added Note, updated Market Notices Advisory & Watch Updated Watch steps Updated Emergency Notice step Updated Emergency Notice step | June 1, 2014 |
| 3.5 5.3 | 1.0 /9 1.0 / 16 | Updated Deploying Non-Spin, added HASL Release & Recall Added Media Appeal | August 1, 2014 |
| 4.1 5.1 5.3 | 1.0 / 16 1.0 / 17 1.0 / 17 | Updated Reference section step 2 Updated Generic Script Added HASL Release step | October 1, 2014 |
| 2.3 2.4 2.6 3.3 3.5 5.1 5.3 | 1.0 / 1 1.0 / 3 1.0 / 13 1.0 / 16 1.0 / 10 1.0 / 18 1.0 / 18 | Updated all steps Updated step Send E-mail Deleted Site Failover with W-N Active & updated step If EBPs are Needed Updated 1st note & updated scripts Added new procedure, “Valley Generation” Updated GMD scripts Updated scripts to consolidate All procedures in this manual have been reviewed | December 15, 2014 |
| 6.2 | 1.0 / 9 | Updated Note and scripts | December 22, 2014 |
| 2.2 3.1 3.2 3.5 3.9 6.2 | 1.0 / 3 1.0 / 18 1.0 / 5 1.0 / 11 1.0 / 0 1.0 / 10 | Added Dispatch and VDI definitions Updated Objective and BAAL Updated procedure Updated step 1 and added Log on Valley Generation Added new procedure for NOGRR136 Updated scripts | March 1, 2015 |