- Power Operations Bulletin # 699

ERCOT has posted/revised the Reliability Unit Commitment manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.2	Communication

Procedure Purpose:  To ensure that three part communication is used for all directives and ensuring all QSEs receive Hotline calls.

| Protocol Reference | 6.5.7.8(4) | 6.5.7.8(6) | 6.5.7.8(10) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## Three-Part Communication |  |
| NERC | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall use three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been placed throughout the procedures as a reminder of three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| ## Hotline Call Communication |  |
| 1 | When making Hotline calls, verify that every QSE has answered. IF: - Not every QSE answered the Hotline; THEN: - Contact them using their OPX line or LD line to provide them with the message - Inquire why they were not on the Hotline call - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| ### Dispatch |  |
| Definitions | - Dispatch is the act of issuing Dispatch Instructions. - A Dispatch Instruction is a specific command issued by ERCOT to a QSE or TO in the operation of the ERCOT System. When appropriate, an electronic dispatch instruction is issued. |
| ### Verbal Dispatch Instruction (VDI) |  |
| Definition | - A Dispatch Instruction issued orally. |
| ### VDI to Master QSE |  |
| 1 | Issue the VDI to the Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources as deemed necessary by ERCOT to effectuate actions for the total Generation Resource for instances when electronic Dispatch Instructions are not feasible. |
| LOG | Log all actions. |

## 2.3	Publish A/S Requirements and Review System Conditions

Procedure Purpose:  To publish and verify daily Ancillary Service requirements are posted to the market.

| Protocol Reference | 4.2.1.1 | 4.2.1.2(2) | 4.3(2) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R5 | TOP-006-2 R6 |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Review and update A/S Requirements must be completed prior to 0500. - The Shift Supervisor must verify the posted ancillary service requirements for the 1st day of the month. |
| ### Review Weather Data Information |  |
| 1 | REVIEW the Weather Data for the next operating day in the EMS. |
| 2 | REVIEW REFERENCE DISPLAY: EMS Applications>Weather Details>Real Time Displays>Weather Forecast Directory IF: - The Last Weather Source Update or Last Weather Read is less than one (1) hour old; THEN: - Using the usual sources, review the weather forecast for at least two days out. IF: - The data update or read is more than one (1) hour old; THEN: - Notify the Shift Supervisor and the Help Desk. |
| 3 | Evaluating the weather forecast for several days ahead is needed to help determine if there is a potential for fuel supply problems. The trigger will usually be an extreme weather event which will cause temperatures to be below freezing for an extended period of time, though there could be other reasons. It may be necessary to consider fuel switching and optimize fuel supply if a reliability issue exists. |
| Fuel Switching | IF: - Notified of fuel limitations; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider fuel switching options (gas to oil) if capability exists. |
| Optimize Fuel Supply | IF: - A particular fuel supply is at risk; THEN: - Consult with Supervisor and determine if reliability concerns exits - Identify potential transmission issues - Identify potential capacity issues IF: - Reliability concerns exists; THEN: - Consider committing Resources with fuel that is not at risk. |
| ### Review and Select Load Forecast |  |
| 1 | - Review and Select load forecast for next day (Refer to Desktop Guide RUC Section 2.17. |
| 2 | IF: - There is a large difference between the load forecasts, AND - There is uncertainty on which load forecast is correct; THEN: - Call the Load Forecasting group for guidance on updating the weather or load forecast. |
| 3 | Notify by e-mail the following distribution lists of the issue: - Load Forecasting & Analysis - 1 ERCOT Shift Supervisors |
| ### Publish A/S Requirements |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, verify the hourly ERCOT system total A/S requirements for each of the following, for each hour of the operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| ### Increasing A/S Requirements before A/S Obligations Publish |  |
| NOTE | This procedure would be performed when it has been determined that additional A/S is needed, such as to support a weather event. |
| NOTE | If an Emergency Condition may exist that would adversely affect system reliability, ERCOT may change the percentage of Load Resources that are allowed to provide RRS from the monthly amounts determined previously. |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > AS Market > AS Plan Before 04:00, increase the hourly ERCOT system total A/S requirements for each requirement needed for each hour of the next operating day: - Reg-Up; - RRS. - Reg-Down; - Non-Spin. |
| 2 | REFERENCE DISPLAY: Market Participation > Monitoring > Event Manager > Events Search / Filter for AS_OBLIGATION_CALC Before 06:00, verify the hourly ERCOT system total A/S requirements have been automatically published at 04:55: IF: - Status indicates complete, no further action is necessary, OR - Status indicates anything else; THEN: - Change status to start now and select submit to database poke point. |
| 3 | IF: - The A/S requirements were increased, THEN: - The next day will copy the new A/S requirements unless you return the A/S requirements to the A/S Plan requirements for the month. REFERENCE DISPLAY: - Market Participation > Physical Market > AS Market > AS Plan Before 04:00 update the A/S requirements. |
| NOTE | Refer to the A/S requirements for the current month’s A/S Plan if no changes are required. |
| ### Priority Outages |  |
| 1 | A Priority Outage is one that affects generation. Prior to 1200: - Review the Outage Notes for the next Operating Day, make lists of Priority Outages, sorted by the affected TOs, - The file is located in P:\DAY AHEAD – TDSP PRIORITY OUTAGE NOTIFICATION, - Print copies, - Fax the lists to the respective TOs using the Priority Outage Fax sheet which states to notify ERCOT within 30 minutes of the Actual Start and Actual End times for the Priority Outages, - Place in Daily Log File. |
| ### Blackstart Availability |  |
| 1 | REFERENCE DISPLAY: Market Participation > Physical Market > Market Participant Submissions > Availability Plan ERCOT SharePoint > System Operations – Control Center > Documents > Blackstart Availability REVIEW: - Blackstart Availability Plan for next operating day (OD+1 tab) IF: - Blackstart Availability Plan for next operating day is missing THEN: - Call the QSE and request them to submit their Blackstart Availability Plan for next operating day - Update the Blackstart Availability spreadsheet located on SharePoint |
| Log | LOG when completed and any additional actions taken. |
| ### Verification of Published A/S Requirements |  |
| NOTE | This step may be completed after 0600. |
| 1 | VERIFY by spot-checking the following information posted to the ERCOT Market Information System (MIS) for the next operating day (or two days if two-day Ahead market is in effect) is posted. - Planned Transmission line and equipment outages for the operating day. - MIS; Grid; Transmission; Transmission Outages; Approved and Accepted Transmission Outages - Weather assumptions used to provide the system conditions forecast. - MIS; Markets; Day-Ahead Market; Day-Ahead Public Information; Weather assumptions - The hourly ERCOT System total Ancillary Service requirements for Regulation Down – REGDN, Regulation Up – REGUP, Responsive Reserve – RRS, and Non-spinning Reserve – NSPIN. - MIS; Markets; Day-Ahead Market; Ancillary Service Plans; DAM Ancillary Service Plan. |
| Log | LOG any significant problems including any action taken. |

## 3.2	Review, Approve and Post HRUC Results

Procedure Purpose:  Monitor RUC applications to determine if systems are functioning properly.  Verify results and correct for any warning or error messages.  Review and approve final results for market posting.

| Protocol Reference | 4.4.8 | 5.1 | 5.3(3) | 5.5.1 |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3 | 6.1(2) | 6.4.9.1.2 |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R1 & R11 |  |  |  |

| Version: 1 | Revision: 21 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Market Operation>Reliability Unit Commitment>HRUC Displays>Workflow>HRUC Workflow Messages - Monitor the HRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published. IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for HRUC are invalid, - Notify the Manager, - ERCOT may use information from the DAM processes as decision support during the HRUC processes. |
| System Summary | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary IF: - All load forecasts seem unreasonable; THEN: - Select the most reasonable forecast, AND - Call the Load Forecasting group for guidance on updating the weather or load forecast - Notify by e-mail the following distribution lists of the issue: - Load Forecasting & Analysis - 1 ERCOT Shift Supervisors |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS_DEV folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on WGR’s or Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Issue an electronic Dispatch Instruction - (priority should be given to WGRs and Resources that resolve congestion - Choose “DECOMMIT” as the Instruction Type from Resource tab - Enter “ERCOT requested decommit/capacity surplus” in Other Information. - Confirm with QSE, the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| A/S Infeasibility | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary Market Participation>Physical Market>SASM Market>AS Infeasibility Market Participation>Physical Market>SASM Market>AS Replacement IF: - Undeliverable Ancillary Service are indicated; THEN: - Determine if the infeasibility is valid IF: - Valid; THEN: - Notify the affected QSE for the following information - the amount of A/S that must be reduced, and - the start and stop times of the reduction. - The QSE can substitute or ERCOT can open a SASM IF: - The QSE elects to substitute; THEN: - Determine the feasibility of the substitution. - If deemed infeasible, a SASM can be opened - Notify the Resource Operator of possible infeasibility issue. |
| A/S Insufficiency from SASM | If a SASM market has been previously run, the following display will indicate if additional A/S Insufficiencies exist: REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment IF: - A/S Insufficiency; THEN - If deemed necessary, commit the necessary Resources that are qualified to provide the service that is deficient while honoring temporal constraints, - Refer to Desktop Guide RUC Section 2.18. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to transmission constraints; THEN: - Notify the Resource Operator. |
| STNET Study | Each hour run a STNET study for four hours out (example it is 0100, run study for 0500) to review voltage violations. IF: - Voltage contingencies or unsolved contingencies exist; THEN: - Check “Voltage Tracking Issues spreadsheet” on Sharepoint to ensure the contingency is not listed. - If not listed, convey the voltage violations to the Transmission and Security Operator - Create a savecase, use naming convention “SC_RUC(HE)_(DATE) - Make at least one detailed log entry per shift that that the studies are being executed. If any new voltage violations are identified that do not have a solution, log the information and notify the Transmission and Security Operator of the new violation(s). |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required; IF: - Valid; AND - Related to a phase shifter tap settings, THEN: - Notify Operations Support Engineer to determine and determine if adjusting a Phase Shifter would reduce the flow, - Create Suggestion Plan for Constraint, - Manually commit resources as needed Refer to Desktop Guide RUC Section 2.14. |
| HRUC Committed Units | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>External Input Data>MF Generator Parameter IF: - HRUC recommends the commitment of any unit; THEN: - Determine the validity, - Determine the temporal constraints for each of the units. IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Periods, and - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the HRUC study by changing ‘Commit’ to ‘blank’ and list reason, IF: - There is a reliability reason requiring the resource commitment decision to be made immediately; - Resources returning from outages - Congestion or Capacity deficiencies that are creating HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, and uncommitting, otherwise a message window will pop up in DSP approval process. Examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Capacity - Constraint name (SLWSCRL5) * Do not use special characters Give a courtesy call to the QSE when commitments are made. |
| RMR Resources | QSEs will show a COP status of OFF when Resources are available. RMR Resources will only be dispatched from the Hourly Reliability Unit Commitment (HRUC). |
| RMR Commitment | WHEN: - HRUC recommends a RMR unit, AND - A capacity reserve shortage is projected and no market Resources are available to meet the projected system demand, and there is a risk of an EEA event; THEN: - Determine if an RMR Resource will need to be considered in HRUC Study Period; ISSUE: - Watch for projected reserve capacity shortage with no market solution; THEN: - Ensure COP status is “OFF” and the resource start-up time allows enough time to procure the RMR for the hours showing to be deficient with risk of an EEA event; SELECT: - Commit Resource before HRUC is approved - Commit Resource, - List reason (RMR for Capacity). Call QSE with any modification to the Delivery Plan as a result of a commitment. |
| Hotline | Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Notify Transmission Operator to make Hotline call to TOs. |
| Post | Typical MIS posting: ERCOT issued a Watch for a projected reserve capacity shortage with no market solution available. HRUC recommended RMR Resources have been committed. |
| Cancel | WHEN: - Committed RMR Resources are off-line THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is canceling the Watch for a projected reserve capacity shortage with no market solution available. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Manual Commitment | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays> External Input Data>MF Generator Parameters IF: - Additional resources are needed to solve for transmission issues (such as for voltage support) and were not picked up in the HRUC run; THEN: - Commit unit before HRUC is approved - Change ‘blank’ to ‘Commit’, - List reason (constraint name, valley import or voltage support), a message window will pop up in DSP approval process if no reason is provided. - Give courtesy call to QSE when commitments are made |
| NOTE | - Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. - ERCOT may only decommit a Resource to resolve transmission constraints that are otherwise unsolvable or to maintain the reliability of the ERCOT System. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. - If ERCOT communicates HRUC commitments and decommitments verbally to a QSE, then the same Resource attributes communicated programmatically must be communicated when ERCOT gives a verbal Resource commitment or decommitment. - QSE’s shall acknowledge the notice of commit or decommit by updating their COP. |
| HRUC Decommitted Resources | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If HRUC recommends decommitments; Determine if: - Outage related, - Possible Network Model error/ Normal Breaker status variances, - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort, THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’), a message window will pop up in DSP approval process if no reason is provided - If Decommitment is error related: - No action is required |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Confirm with QSE that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |
| ### VSAT and RUC perform AC Analysis |  |
| NOTE | IF: - RUC cannot complete the process; THEN: - Notify the Transmission & Security Operator and additional personnel as required. |
| Validate | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | HRUC must be approved by XX:50 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The HRUC results are reasonable and after all necessary modifications have been made; THEN: - Approve the results (all RUC commitment, operator manual commitment/decommit/blank out must have a reason, otherwise a message window will pop up), OR IF: - The results are unacceptable; THEN: - Click on Disapprove button, AND - Follow the Manage HRUC Timeline Failure in the next section. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>HRUC> HRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>HRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue electronic Dispatch Instructions to cancel RUC instructions - Confirm with QSE that the electronic Dispatch Instruction received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| Log | Log actions taken. |

## 3.3	HRUC Failure/Timeline Deviation

Procedure Purpose:  To address situations in which the HRUC process has failed.  Failures can be identified by software failure, results not approved in a timely manner or certain conditions.

| Protocol Reference | 6.5.9.1(2) | 6.5.9.3.3(2)(e) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R5, R7, R11 | IRO-001-1.1 R9 |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### HRUC Failure/Timeline Deviation |  |
| Failure | IF: - HRUC solved with invalid solution, - Time does not allow for full review of results, OR - HRUC software fails without expectation of timely repair; THEN: - Notify Help Desk and Control Room Staff, - Issue a Watch by making a Hotline call to QSEs - Make posting on MIS Public. - Notify Transmission Operator to make Hotline call to TOs Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing a Watch due to HRUC not completing for [state HE] due to [failure or timeline deviation]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. WHEN: - HRUC is operating properly; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At, [xx:xx], ERCOT is canceling the Watch for HRUC not completing for [state HE]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Create Save Case | IF: - HRUC is aborted or shut down; THEN: - Go to display System Administration > Savecase Management. - Choose File Type as HRUC. - Fill in File Name (no spaces allowed) - Fill in Description. - Push Create Button. - The message will show up in the Text field. - Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Also refer to Desktop Guide Common to Multiple Desks Section 2.16, if needed. - Contact Helpdesk to notify EMMS Production Support that HRUC was aborted or shut down and a Savecase was created. |
| NOTE | IF: - HRUC is having trouble solving in the required timeline due to transmission/capacity violations in the study; THEN: - Have Operations Support Engineer check validity of violation AND if correct, - Consider committing Resource(s) sooner instead of waiting to evaluate later. |
| Commit/ De-Commit Resources By VDI | IF Needed: - Commit/De-Commit Resources by issuing electronic Dispatch Instructions for the following: - Choose COMMIT or DECOMMIT as the Instruction Type from the RES Level, - Enter reason (capacity, capacity surplus or contingency name) in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |

## 3.6	Manual Dispatch of Resources

Procedure Purpose:  Manually Dispatch Resources as necessary to ensure system security when HRUC can not be used.

| Protocol Reference | 5.1(12) | 5.5.3(3) | 6.5.9 (3) |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R5, R6 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | ERCOT shall honor all Resource operating parameters in Dispatch Instruction under normal conditions and Emergency Condition. During Emergency Conditions, ERCOT may verbally request QSE’s to operate its Resources outside normal operating parameters. If such request is received by a QSE, the QSE shall discuss the request with ERCOT in good faith and may choose to comply with the request. |
| ### Manual Commit of a Resource |  |
| 1 | IF: - It has been determined that a Resource is needed in real-time for a transmission condition; THEN: - Issue an electronic Dispatch Instruction to commit the Resource, - Choose “COMMIT” as the Instruction Type from Resource level - Enter reason, such as contingency name or capacity in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received - The same Resource attributes communicated programmatically must be communicated when giving a VDI. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement See Desktop Guide Common to Multiple Desks Section 2.3 for additional information to submit a correct electronic Dispatch Instruction. |
| LOG | Log all actions. |
| ### Manual Dispatch to take a Unit Off-Line |  |
| 1 | IF: - A manual dispatch instruction will result in the unit being dispatched off-line (i.e., less than the minimum operating limit for that Resource); THEN: - Issue an electronic Dispatch Instruction taking the Resource to zero until it can be released, - Choose “DECOMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Ensure QSE updates telemetry. |
| ### Manual Dispatch to take a Unit of a Combined Cycle Off-line |  |
| 1 | IF: - System conditions require one unit of a Combined Cycle Plant to be manually dispatched off-line; THEN: - Contact the QSE and request which unit the QSE would like to shutdown, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue an electronic Dispatch Instruction to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Manual Dispatch to bring a Unit of a Combined Cycle On-line |  |
| 1 | IF: - System conditions require a unit of a Combined Cycle Plant to be manually dispatched on-line; THEN: - Contact the QSE and notify which unit will be committed, - Request the planned/current CC configuration and then the CC configuration that the Resource will need to be operating, - Issue an electronic Dispatch Instruction to “COMMIT” the QSE to their CC configuration. All data must be entered but pay attention to the following details. - Choose the proper QSE from the Participant name - Select the CC configuration that you are instructing the Resource to operate in from the Resource name - Choose “COMMIT” as the Instruction Type from Resource level - Enter contingency name in “other information” - Confirm with QSE that the electronic VDI was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Log the above information. |
| ### Canceling RUC Commitments |  |
| 1 | IF: - A Resource is RUC committed that needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue an electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information |
| LOG | Log all actions. |

## 4.3	Review, Approve and Post DRUC Results

Procedure Purpose:  To work collaboratively with Market Operations Support Personnel in reviewing, and if necessary, modifying DRUC data, to approve and post the final DRUC results.

| Protocol Reference | 4.4.8 | 5.1 (9) | 5.3(3) | 5.5.1(9) |
| --- | --- | --- | --- | --- |
|  | 5.5.2 | 5.5.3(2) | 6.4.9.1(3) |  |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R5, R7, R11 |  |  |  |

| Version: 1 | Revision: 22 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | See Desktop Guide Common to Multiple Desks Section 2.16 if the savecase function fails when running RUC |
| Monitor | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow Messages |
| Review | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary When DRUC has completed. If necessary, work with Market Operations and Operations Support Engineer to review the results. - Monitor the DRUC Workflow display to determine when it is complete, ENSURE: - The workflow has completed before the study is approved and published, IF: - The study is approved before it completes, - Incorrect RUC deployments are sent to QSE’s THEN: - Make hotline call to notify QSE’s that deployments for DRUC are invalid, - Notify the Manager of System Operations and/or Control Room Operations Manager immediately, - Abnormal system condition in the summary display after IUC (Initial Unit Commitment component of MMS) and NCUC (Network Constrained Unit Commitment component of MMS). - For Under Generation, prepare for following “Manage Capacity Insufficiency” section of this procedure - For Over generation, check for COP or Load Forecast errors - For System Lambda greater than $10, check intermediate NSM (Network Security Manager Component of MMS) results for constraint violation. For abnormal constraints in the NSM outputs and abnormal commitments in IUC and NCUC outputs, refer to Desktop Guide RUC Section 2.6, step 5. |
| NOTE | - Resources with NO Current Operating Plan (COP) entry are considered as “Unavailable” in RUC. - Resources with “EMR” Resource status can only be committed during Emergency conditions. |
| System Summary | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary Line Flow DETERMINE IF: - The load forecast is reasonable for each hour, - Any under/over generation; THEN: - Be aware of these when running HRUC. |
| A/S Insufficiency from DAM | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Decision Support for Ancillary Service Deployment Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Notified from Market Operations of A/S Insufficiency from DAM; THEN - Issue a Watch to QSEs - Notify Transmission Operator to make Hotline call to TOs - Verify Market Operations has posted message on MIS Public - Refer to Desktop Guide RUC Section 2.1. Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name], at [xx:xx] ERCOT is issuing a Watch due to A/S insufficiency in DAM for operating day [day]. The A/S insufficiencies will be procured in DRUC. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. WHEN: - A/S offers are committed in DRUC; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the Watch due to A/S insufficiency in DAM for operating day [day]. A/S insufficiencies were procured in DRUC. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Undeliverable A/S Capacity | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Undeliverable Ancillary Service Capacity Summary IF: - Undeliverable A/S due to Transmission Constraints and Reliability issues exist; THEN: - Notify the QSEs and provide the following information: - The amount of its Resource capacity that does not qualify to provide A/S - The projected hours - Notify the Resource Desk Operator. |
| Violated Constraints | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Binding Constraint Summary Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Constraint Summary REVIEW: - Violated constraints. If needed, notify Operations Support Engineer to determine the validity; IF: - Invalid, no further action is required, - Valid; THEN - Locate the constraint on the DSP Constraint Summary display, - Create a Suggestion Plan for the identified violated constraint - Review the temporal constraints of the suggested resources - If resource start-up time allows enough time to re-evaluate the need for its commitment, be aware of these conditions when running HRUC, - Commit resources as needed prior to DRUC approval if needed due to temporal constraints. |
| NOTE | RUC Operators can decide to postpone a commitment if the startup time is well into the future. It will be left up to future HRUC solutions to actually commit the unit. |
| DRUC Committed Units | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSI Displays>External Input Data>MF Generator Parameter Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays>DSP RUC Commitment/Decommitment Summary IF: - DRUC recommends the commitment of any unit; THEN - Determine the validity, - Determine the temporal constraints for each of the units, IF: - The resource start-up time allows enough time to re-evaluate the need for its commitment in future HRUC Study Period, AND - There is no reliability reason requiring the resource commitment decision to be made immediately; THEN: - De-select the resource prior to approving the DRUC study by changing ‘Commit’ to ‘blank’ and list reason. IF: - There is reliability reason requiring the resource commitment decision to be made immediately; - Resources with long start-up times - Resources returning from outages - Congestion or Capacity deficiencies that may create HRUC performance issues THEN: - Log the reason for not de-selecting the resource. NOTE: A reason must be entered for commit, decommit, uncommitting, examples below: - Evaluate later (should be used when waiting until the last possible hour to commit) - Short start (should be used for units that can start within 1 hour) - Voltage support - Valley import - Constraint name (SLWSCRL5) * Do not use special characters Give a courtesy call to the QSE when commitments are made. |
| Excess Generation | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS_DEV folder: - “6 DRUC Capacity” which is based on the last ran DRUC VERIFY: - TOTAL_LOAD is less than SS_LASL, IF: - Load forecast is reasonable AND the decision can be made in the future, THEN: - Issue OCN for Excess Reserve Capacity - Notify Transmission Operator to make Hotline call to TOs - Post message on MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is issuing an OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting: ERCOT issued an OCN due to a projected excess reserve capacity for [HE XX – HE XX]. WHEN: - Projected excess reserve capacity; THEN: - Making hotline call to QSEs - Cancelling MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the OCN for [date] due to a projected excess reserve capacity for [HE XX – HE XX]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| DRUC Committed For Capacity Shortage | IF: - DRUC recommends Resource(s) for capacity; THEN - Determine if start-up time allows enough time to re-evaluate, and - De-select the Resource(s) prior to approving the DRUC, After DRUC is approved: - Issue an OCN for projected reserve capacity shortage - Notify Transmission Operator to make Hotline call to TOs - Post message on MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an OCN for [date] for a projected Reserve Capacity Shortage for [HE XX to HE XX]. ERCOT will commit Resources as needed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting: ERCOT issued an OCN due to a projected capacity shortage for [HE XX – HE XX]. WHEN: - Projected reserve capacity shortage no longer exist; THEN: - Making hotline call to QSEs - Cancel MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the OCN for [date] due to a projected reserve capacity for [HE XX – HE XX]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| Manual Commitment | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - Additional resources are needed to solve for transmission issues (such as voltage support) and were not picked up in the DRUC run, - The resource start-up time doesn’t allow enough time to re-evaluate the need for its commitment in the HRUC Study Period, OR - A Resource was given a WRUC instruction and chose not to self-commit for all hours needed; THEN: - Change ‘blank’ to ‘Commit’ - List reason (capacity, constraint name or voltage issue). - Give courtesy call to QSE when commitments are made |
| NOTE | Resources cannot be decommitted for just a portion of a DAM-Committed Interval, which is a one-hour interval. ERCOT may only decommit a Resource to resolve transmission constraints that otherwise cannot be resolved. Qualifying Facilities (QFs) may be decommitted only after all other types of Resources have been assessed for decommitment. |
| DRUC Decommitted Resources | REVIEW REFERENCE DISPLAYS: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP RUC Commitment/Decommitment Summary IF: - If RUC recommends commitments/decommitments; DETERMINE IF: - Outage related’ - Possible Network Model error’ - COP error for Combine Cycle configurations / JOU, - Qualifying Facilities should be de-committed ONLY as a last resort; THEN: - If this is a true decommitment: - Confirm Decommitment - List reason (most likely reason is ‘transmission outage’) - If Decommitment is error related: - No action is required |
| NOTE | Once you have completed your review of DRUC, consult with Market Operations to ensure they see no issues before approving. |
| Validate | REVIEW REFERENCE DISPLAY: Market Participation>Physical Market>SASM Market>AS Responsibility - QSE Market Operation>Reliability Unit Commitment>DRUC Displays>UC Displays>Output Display Menu>System Outputs>Summary VERIFY: - Input data - Updated Time - Results are reasonable |
| Approval | DRUC must be approved by 1600 REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>DSP Displays> DSP Execution Control Parameters IF: - The DRUC results are reasonable after all necessary modifications have been made; THEN: - Approve the results, OR IF: - The results are unacceptable; THEN: - Click on Disapprove button - Follow the Manage DRUC Failure/Timeline Deviation procedure. IF: - Disapprove button was selected in error; THEN: - Contact Helpdesk to open ticket for EMMS Production Support to correct it. |
| NOTE | If the Operator disapproves the results, the results will be saved in the database for future analysis and will not be published to the MPs. |
| After Approval | AFTER: - Approval button is pushed; THEN: - Double check display Market Participation>Physical Market>Market Results>DRUC> DRUC Results, - Make sure the records in this display matches data in display Market Operation>Reliability Unit Commitment>DRUC Displays >DSP Displays>DSP RUC Commitment/Decommitment Summary. IF: - Displays are different, the RUC commitments thought to be blanked out were sent out; THEN: - Notify the Helpdesk to call the On-Call EMMS Production support, and - Issue VDIs to cancel RUC instructions - Confirm with QSE that the electronic Dispatch Instruction received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| Canceling RUC Commitments | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>HRUC Displays>DSI Displays>DSI Data Processes>DSI Operator Manual Commitment IF: - A Resource is RUC committed and needs to be canceled; - Only cancel RUC commits if the ERCOT Operator Resource commitment was unintended. THEN: - Issue an electronic Dispatch Instruction to cancel the RUC instruction - Choose “CANCEL RUC COMMIT” as the Instruction Type - Enter “unintended commitment” in other information - Confirm with QSE that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement - Remove unintended RUC commit from DSI Operator Commitment by changing (AUTO) to (OFF) for the hours in question. |

## 4.4	DAM/DRUC Timeline Deviation

Procedure Purpose: To address situations in which the DAM/DRUC process has deviated from its timeline.

| Protocol Reference | 4.1.2 | 5.2.2.1 |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | TOP-002-2.1b R5, R7, R11 | IRO-001-1.1 R9 |  |  |

| Version: 1 | Revision: 12 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| Logs | Document decisions made and actions taken within this procedure in the Operator Logs. |
| ### DAM Timeline Deviation |  |
| DAM Timeline Deviation | IF: - Notified by Market Operations that the DAM Market timeline is deviated; THEN: - Issue an Advisory for DAM timeline deviation - Notify Transmission Operator to make Hotline call to TOs - Market Operations will post message on the MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Advisory for the timeline deviation of the Day Ahead Market; the start of DRUC will be delayed, until further notice. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. WHEN: - DAM completes; THEN: - Make Hotline call to QSE’s and give one hour notice to update COPs - Post message on MIS Public Typical Hotline Script for cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. At [xx:xx], ERCOT is canceling the Advisory for the delay of DAM. DAM is now complete; DRUC will begin at [time]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting: DAM is complete, DRUC will begin at [xx:xx]. |
| ### Delay of DRUC |  |
| DRUC Delay | Note: This step is for any reason than DAM being delayed. DAM completed on time however there is an issue with DRUC By 16:00 IF: - DRUC is delayed for any reason other than DAM timeline deviation; THEN: - Notify Shift Supervisor and Helpdesk, - Issue an Advisory by making a Hotline call to QSEs - Notify Transmission Operator to make Hotline call to TOs - Post message on the MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing an Advisory for the timeline deviation of DRUC for [effected date] due to [state issue]. ERCOT will continue to try to complete DRUC by 18:00. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. Typical MIS Posting: ERCOT issued an Advisory for DRUC timeline deviation. ERCOT will continue to try to complete DRUC by 18:00. |
| DRUC Completes By 18:00 | By 18:00 IF: - DRUC has completed by 18:00; THEN: - Notify Shift Supervisor, - Cancel the Advisory by making a Hotline call to QSEs - Notify Transmission Operator to make Hotline call to TOs - Cancel message on the MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is canceling the Advisory for the timeline deviation of DRUC. DRUC completed at [time]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| DRUC Not Complete By 18:00 | REVIEW REFERENCE DISPLAY: Market Operation>Reliability Unit Commitment>DRUC Displays>Workflow>DRUC Workflow By 18:00 IF: - DRUC completed and the results cannot be approved; THEN: - No need to abort DRUC Process, just don’t approve. IF: - DRUC has not completed (i.e. software issues); THEN: - Abort DRUC Process. |
| 1 | IF: - DRUC has not completed by 18:00; THEN: - Notify the Help Desk and control room staff, - Issue a Watch by making a Hotline call to QSEs - Notify Transmission Operator to make Hotline call to TOs - Posting message on the MIS Public Typical Hotline Script: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT Operator [first and last name]. ERCOT is issuing a Watch due to DRUC not completing by 1800 due to [state reason]. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 2 | AFTER: - HRUC has been approved for 18:00; THEN: - Cancel the Watch by making hotline call to QSEs - Cancel MIS posting - Notify Transmission Operator to make hotline call to TOs. Typical Hotline Script Cancellation: “This call requires everyone to remain on the line until it is complete. [QSE] I will be asking you for the repeat back. This is ERCOT operator [first and last name]. At [xx:xx], ERCOT is cancelling the Watch due to DRUC not completing by 1800. ERCOT will procure in HRUC if needed. [QSE] please repeat this back to me.” If repeat back is CORRECT, “That is correct, thank you.” If INCORRECT, repeat the process until the repeat back is correct. |
| 3 | IF: - DRUC is aborted or shut down; THEN: - Go to display System Administration > Savecase Management. - Choose File Type as DRUC. - Fill in File Name (no spaces allowed) - Fill in Description. - Push Create Button. - The message will show up in the Text field. - Refresh the display (F5), make sure the savecase name will show up in the File Name Field. Also refer to Desktop Guide Common to Multiple Desks Section 2.16, if needed. |
| NOTE | After 1800, HRUC will run for the rest of the current day and the next day even if DRUC has not run successfully. |

## 6.2	EEA

Procedure Purpose: To commit Resource that can be brought On-Line within the timeframe of the emergency.

| Protocol Reference | 3.9.1 | 6.5.9.4 | 6.5.9.4.1 | 6.5.9.4.2 |
| --- | --- | --- | --- | --- |
| Guide Reference | 4.5.3.1 |  |  |  |
| NERC Standard | COM-002-2 R1, R1.1, R2 | EOP-001-2.1b R2.1, R2.3, R3.1, R3.2, R3.3, R4, R5 | EOP-002-3.1 R1, R2, R4, R6, R7 | EOP-003-2 R1, R5 |

| Version: 1 | Revision: 2 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| 1 | IF: - A Generation Resource (without Non-Spin obligation) which has a unit status of OFF or EMR and can be brought On-line within the timeframe of the emergency; THEN: - Issue an electronic Dispatch Instruction to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) - Enter “capacity” in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| 2 | IF: - If Frontera can be switch from CFE into ERCOT within the timeframe needed; THEN: - Notify QSE for Frontera of the need to switch the generation from CFE into ERCOT - Issue RUC instruction |
| 3 | IF: - A Generation Resource was scheduled to come Off-line before the start of the emergency and requests to come Off-line; THEN: - Issue an electronic Dispatch Instruction to commit the Resource - Choose “Commit” as the Instruction Type from Resource level - VDIs need a start/stop time (issue one hour at a time) - Enter “capacity” in “other information” - Confirm with QSE that the electronic Dispatch Instruction was received. When issuing a VDI or when confirming the receipt of an electronic Dispatch Instruction ensure the use of three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Barcalow, Lowrie, and Stone | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 22, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 20, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 2.3 2.4 3.2 3.3 4.3 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Added new procedure “Phase Shifter Tap Settings” Updated Note Updated step “Monitor” Updated steps “Commit/De-Commit”, “Violated Constraints” and “HRUC Committed” Updated step “Review”, “A/S Insufficiency from DAM” and “DRUC Committed” | December 1, 2010 |
| 2.3 4.2 4.3 4.4 | 1.0 / 2 1.0 / 1 1.0 / 2 1.0 / 1 | Updated “Review Weather Data Information” step 2 Added steps “DRUC Committed for Capacity Shortage” and “Projected Reserve Capacity Shortage” Updated steps “DAM Timeline Deviation, DAM Failure, DRUC Delay & Software Failure” change to step 1 | December 15, 2010 |
| 3.2 4.3 4.1 4.4 6.1 | 1.0 / 2 1.0 / 3 1.0 / 2 - / 2 1.0 / 1 | Updated step “HRUC Committed Units”, “Manual Commitment”, added steps “Excess Generation” and “Canceling RUC commitments” Updated step DRUC Committed Units”, “Manual Commitment, added steps “Excess Generation” and “Canceling RUC commitments” Updated step “DAM Timeline Deviation”, DAM Failure”, DRUC Delay” Updated scripts Updated script | January 31, 2011 |
| 3.2 3.3 3.5 4.3 4.4 6.1 | 1.0 / 3 1.0 / 2 - / 0 - /4 - / 3 1.0 / 2 | Updated step Canceling RUC Commitments Deleted HRUC Timeline Deviation and updated HRUC Failure/Timeline Deviation Added new section Updated step Canceling RUC Commitments Updated step DAM Timeline Deviation in DAM Timeline Deviation/Failure Timeline not Met in section DRUC Timeline Deviation/Failure Updated Watch and Emergency Notice | March 25, 2011 |
| 2.5 3.2 3.3 4.3 6.1 6.2 | 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 1 | Updated Monthly MIS Posting Updated step Canceling RUC Commitments Updated step Failure Updated step Canceling RUC Commitments Updated step 1 in Watch and Emergency Notice Updated step & removed step Market Notification | April 22, 2011 |
| 3.2 3.5 4.3 4.4 5.2 6.1 | 1.0 / 5 1.0 / 1 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 4 | Updated steps HRUC Committed Units and Approval Updated all steps Updated step Approval Updated step DAM Timeline Deviation Updated step Long Lead Times Updated all steps | June 8, 2011 |
| 2.3 3.1 3.2 3.5 4.2 4.3 4.4 4.5 | 1.0 / 3 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 2 1.0 / 7 1.0 / 5 1.0 / 1 | Added steps for Publish A/S Requirements Updated Load Forecast step Updated steps Excess Generation, A/S Insufficiency from SASM, Violated Constraints and Approval Corrected title to match TOC and updated 1st note Updated Load Forecast step Updated Approval step Added subtitles, step DRUC Delay & step 1 Moved section 2.6 to 4.5 | July 20, 2011 |
| 2.3 2.4 3.2 3.3 4.3 6.1 7.1 | 1.0 / 4 - / 1 1.0 / 7 1.0 / 4 1.0 / 8 1.0 / 5 1.0 / 1 | Added Note to Increasing A/S Requirements before A/S Obligations Publish Added information on RMR Resource Commitment Updated step Excess Generation, added RMR Resources, RMR Commitment and Canceling RUC Commitments Updated step Commit/Decommit Resources by VDI Updated step Canceling RUC Commitments Added Projected Reserve Capacity Shortage to Watch Updated 4th note | August 24, 2011 |
| 3.2 4.2 4.3 6.1 7.1 | 1.0 / 8 1.0 / 3 1.0 / 9 1.0 / 6 1.0 / 2 | Added Note, updated step Hotline, Post and added step Cancel Deleted step RMR, updated Manual Commitment, deleted Note Updated Note Added Extreme Hot Weather in Watch Updated 3rd note and step 1 | September 1, 2011 |
| 2.3 2.4 3.1 3.2 4.3 4.4 4.5 4.6 4.5 Original | 1.0 / 5 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 10 1.0 / 6 1.0/ 0 1.0 / 0 1.0 / 2 | Deleted Phase Shifter Tap Settings Deleted step Resources Updated step Manual Commitment in Tasks prior to execution of HRUC Updated step RMR Resources and Canceling RUC Commitments Updated step for Canceling RUC Commitments Moved A/S Insufficiency in DAM to section 4.5 & DAM Failure to section 4.6 Moved A/S Insufficiency in DAM to section 4.5 & deleted Increase A/S Capacity needs about Day-Ahead Requirements Moved from section 4.5 Deleted procedure (was section 4.5), duplicate | November 1, 2011 |
| 2.3 6.1 | - / 6 1.0 / 7 | Removed Invalid SPS/RAP due to Outage Updated Post in “Notifications” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.5 4.3 4.6 | 1.0 / 1 1.0 / 3 1.0 / 11 1.0 / 3 | Updated Scope Updated all steps Updated A/S Insufficiency from DAM Updated desktop guide section | January 19, 2012 |
| 2.1 2.3 2.5 3.1 3.2 3.3 3.7 4.2 4.3 4.4 4.5 4.6 5.2 6.1 7.1 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 10 1.0 / 5 1.0 / 0 1.0 / 4 1.0 / 12 - / 7 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 8 1.0 / 3 | Updated 4th Paragraph Updated Desktop Guide reference Updated Monthly MIS Posting Updated Desktop Guide reference Updated Desktop Guide references and step After Approval Added step Create Save Case Added new procedure Projected Capacity Reserve Shortage with no Market Solution Updated Desktop Guide references Updated Desktop Guide references and added step After Approval Added step 2 Updated Desktop Guide reference Updated Desktop Guide reference Added step Create Save Case Updated step 1 of Watch Updated Desktop Guide references | March 1, 2012 |
| 1.1 2.1 3.1 3.2 3.3 4.2 4.3 5.1 5.2 6.1 8.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 11 1.0 / 6 1.0 / 5 1.0 / 13 1.0 / 1 1.0 / 3 1.0 / 9 1.0 / 1 | Changed Shift Engineer to Operations Support Engineer Changed TSP,DSP to TO Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and added WRUC Changed Shift Engineer to Operations Support Engineer and Manual Commitment Changed Shift Engineer to Operations Support Engineer Changed Shift Engineer to Operations Support Engineer and updated step Long Lead Times for NPRR402 Updated OCN, Advisory, Watch, Emergency Notice sections Changed Shift Engineer to Operations Support Engineer | May 1, 2012 |
| 1.1 1.3 2.3 3.1 3.2 3.3 4.2 4.3 4.4 5.2 6.1 7.1 | 1.0 / 2 1.0 / 1 1.0 / 8 1.0 / 5 - / 12 - / 7 - / 6 - / 14 - / 8 1.0 / 4 1.0 / 10 1.0 / 4 | Updated last paragraph, HRUC Removed ERCOT Shift Supervisor paragraph Updated step 3, added Fuel Switching and Optimize Fuel Supply & 2nd note Changed Shift Engineer to Operations Support Engineer Updated HRUC Committed Units Updated Create Save Case Updated Manual Commitment on 14:30 each day Updated DRUC Committed Units Updated step 2 in Delay of DRUC Updated Create Save Case Updated all step 1’s Updated 4th note | July 16, 2012 |
| 2.2 3.2 4.3 | 1.0 / 1 1.0 / 13 1.0 / 15 | Added Hotline Call Communication Updated Manual Commitment and Validate Updated Manual Commitment and Validate All procedures in this manual have been reviewed. | November 1, 2012 |
| 2.3 4.3 4.6 | 1.0 / 9 1.0 / 16 1.0 / 5 | Added Blackstart Availability Updated Review Updated steps SASM not able to Procure all A/S Requested & Cancel Emergency Notice | March 1, 2013 |
| 3.1 3.2 3.3 3.5 3.7 4.3 4.4 4.5 4.6 5.2 6.1 | 1.0 / 6 1.0 / 14 1.0 / 8 1.0 / 4 1.0 / 1 1.0 / 17 1.0 / 9 1.0 / 4 1.0 / 6 1.0 / 5 1.0 / 11 | Updated step Deselect Contingencies Updated step Monitor, Excess Generation, Hotline, & Cancel Updated step Failure & Create Save Case Updated step REG/RRS Updated all steps Updated 1st Note, A/S Insufficiency from DAM, Excess Generation &DRUC Committed from Capacity Shortage Updated all steps Updated all steps Updated all steps Updated step Create Save Case Updated Notifications | June 1, 2013 |
| 3.5 4.3 4.4 4.6 6.1 | 1.0 / 5 1.0 / 18 1.0 / 10 1.0 / 7 1.0 / 12 | Correct typo in script Correct typo’s in scripts Updated Delay of DRUC steps Corrected reference in desktop guide Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 3.2 3.3 | 1.0 / 15 1.0 / 9 | Updated step HRUC Committed Units, Manual Commitment, HRUC Decommitted Resources & Approval Updated step Create Save Case | August 9, 2013 |
| 3.2 4.3 5.1 5.2 | 1.0 / 16 1.0 / 19 1.0 / 2 1.0 / 6 | Updated steps Violated Constraints, HRUC Committed Units, RMR Commitment & Manual Commitment Updated steps Violated Constraints, DRUC Committed Units & Manual Commitment Updated titles Updated Violated Constraints, Disapprove & Log. Deleted Long Lead Times, All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.3 4.4 4.6 6.1 | 1.0 / 10 1.0 / 11 1.0 / 8 1.0 / 13 | Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 Updated for NPRR542 and 529 | January 1, 2014 |
| 2.3 3.2 3.3 3.6 4.3 6.2 6.3 | 1.0 / 10 1.0 / 17 - / 11 1.0 / 1 1.0 / 20 1.0 / 0 1.0 / 2 | Updated Review and Select Load Forecast Updated step System Summary, HRUC Committed Units & VDI information Updated VDI information Added Manual Commit of a Resource & Canceling RUC Commitments Updated VDI information Updated DRUC Committed Units & VDI information Added new EEA procedure Change section number from 6.2 to 6.3 | April 4, 2014 |
| 2.2 2.3 2.4 2.5 3.2 3.6 4.5 4.6 5.2 6.1 | 1.0 / 2 1.0 / 11 1.0 / 3 1.0 / 3 1.0 / 18 1.0 / 2 1.0 / 5 1.0 / 9 1.0 / 7 1.0 / 14 | Added VDIs to Master QSEs Added Note to Increasing A/S before Publishing Added Note Updated Monthly MIS Posting step Updated step A/S Infeasibility Updated step 1 Updated step A/S Insufficiency Offers Updated DAM Failure Updated step Disapprove Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.2 6.1 | 1.0 / 19 1.0 / 15 | Updated Undeliverable A/S Capacity, added STNET Study and title change on VSAT and RUC perform AC Analysis Updated Generic Script | October 1, 2014 |
| 3.2 3.2 4.3 6.2 | 1.0 / 20 1.0 / 20 1.0 / 21 1.0 / 1 | Updated step STNET Study, HRUC Committed Units & Manual Commitment Updated STNET Study, HRUC Committed Units & Manual Commitment Updated step DRUC Committed Units & Manual Commitment Added step All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 2.3 3.2 3.3 3.6 4.3 4.4 6.2 | 1.0 / 3 1.0 / 12 1.0 / 21 1.0 / 12 1.0 / 3 1.0 / 22 1.0 / 12 1.0 / 2 | Added Dispatch & Verbal Dispatch Instruction Deleted Meterlogix number. Updated Priority Outages Corrected VDI vs. Dispatch Instruction and Manual Commitment Corrected VDI vs. Dispatch Instruction Corrected VDI vs. Dispatch Instruction Updated step Manual Commitment & corrected VDI vs. Dispatch Instruction Updated DAM Timeline Deviation Corrected VDI vs. Dispatch Instruction | March 1, 2015 |