- Power Operations Bulletin # 701

ERCOT has posted/revised the Shift Supervisor manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

http://www.ercot.com/mktrules/guides/procedures/index.html

## 2.2	Communication

Procedure Purpose:  To ensure that three part communication is used for all directives and ensuring all entities receive Hotline calls.

| Protocol Reference | 6.5.7.8(4) | 6.5.7.8(6) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 3 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## Three-Part Communication |  |
| NERC | Each Reliability Coordinator, Transmission Operator, and Balancing Authority shall issue directives in a clear, concise, and definitive manner, shall ensure the recipient of the directive repeats the information back correctly; and shall acknowledge the response as correct or repeat the original statement to resolve any misunderstandings. |
| NOTE | A directive is an authoritative instruction or direction; specific order. |
| 1 | ERCOT ISO is the Reliability Coordinator, Transmission Operator, and Balancing Authority. When issuing a directive you shall follow the three-part communication: - Issue the directive - Receive a correct repeat back - Give an acknowledgement Failing to do any of the three parts is a NERC Reliability Standard violation. |
| 2 | Many scripts have been placed throughout the procedures as a reminder for the three-part communication. However, a script cannot be provided for every scenario. Effective three-part communication skills are mandatory. |
| ## Hotline Call Communication |  |
| 1 | When making Hotline calls, verify that every entity has answered. IF: - Not every entity answered the Hotline; THEN: - Contact them using their OPX line or LD line to provide them with the message - Inquire why they were not on the Hotline call - Open a Help ticket if ERCOT’s Telecommunications department is needed to investigate. |
| ### Dispatch |  |
| Definitions | - Dispatch is the act of issuing Dispatch Instructions. - A Dispatch Instruction is a specific command issued by ERCOT to a QSE or TO in the operation of the ERCOT System. When appropriate, an electronic dispatch instruction is issued. |
| ### Verbal Dispatch Instruction (VDI) |  |
| Definition | - A Dispatch Instruction issued orally. |
| ## Master QSE |  |
| 1 | Issue the VDI to the Master QSE of a Generation Resource that has been split to function as two or more Split Generation Resources as deemed necessary by ERCOT to effectuate actions for the total Generation Resource for instances when electronic Dispatch Instructions are not feasible. |
| LOG | Log all actions. |

## 3.2	Capacity and Reserve Monitoring

Procedure Purpose:  To monitor capacity for SCED dispatch and total system capacity for providing Ancillary Services.

| Protocol Reference | 6.3.2(2) | 6.5.9.1(1)(a) | 6.5.7.6.2.3(1) |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 2.2.1(3)(a) |  |  |  |
| NERC Standard | EOP-002-3.1 R2, R4 | IRO-002-2 R5 | IRO-005-3.1a R2 |  |

| Version: 1 | Revision: 6 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Capacity Monitoring |  |
| 1 | Monitor the Excel MAI: IF: - Load forecast is reasonable AND “Adj. Max Capacity Room” shows insufficient capacity; THEN: - Verify that HRUC has identified the insufficient capacity situation. |
| 2 | IF: - HRUC has not identified the insufficient capacity; THEN: - Have RUC Operator verify that HRUC is using a reasonable forecast AND update if necessary, - Ensure Resource commitments are being made, if needed. |
| 3 | Triggers to deploy Non-Spin MONITOR: The Generation Area Status Page and the OpsMon Dashboard IF: - Avail_CAP_30Min < 0; THEN: - Verify that the Resource Desk Operator has deployed half of available Non-Spin. IF: - Avail_CAP_30Min < -300, OR - PRC is < 2500 MW; THEN: - Verify that the Resource Operator has deployed all of available Non-Spin, IF: - Additional capacity is required, THEN: - Verify the RUC Operator is aware of the requirement to commit additional Resources for the next hour. |
| 4 | During periods of low load and excess generation: PERIODICALLY REVIEW: - OpsMon Dashboard Viewer under the MOS_Dev folder: - “Last Approved HRUC Capacity” which is based on the last ran HRUC solution IF: - Load forecast is reasonable AND the decision needs to be made in the near future, THEN: - Decommit generation from the HRUC next study, - Priority should be on Resources that resolve congestion; IF: - The decision needs to be made immediately, THEN: - Request RUC Operator to issue electronic Dispatch Instruction. |

## 3.3	Disseminating Information to System Security Response Group (SSRG)

Procedure Purpose: To communicate information concerning disturbances or unusual occurrences to appropriate parties in the Interconnection.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.8(4) |  |  |  |
| NERC Standard | EOP-004-2 |  |  |  |

| Version: 1 | Revision: 11 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | Threat alerts can be viewed at either of the following links: http://www.esisac.com/SitePages/Home.aspx, OR http://www.dhs.gov/files/programs/ntas.shtm The definitions for the threat alert levels are listed in the Security Alert Plan which can be found in the Operating Procedure Manual. |
| NOTE | - The SSRG e-mail exploder list is used to disseminate information to the SSRG members of the ERCOT Region when an SSRG conference call is not necessary. - This information is intended for use within the industry and not for public release. - At the beginning of each e-mail state the follow “This information is intended for use within the industry and not for public release” - At the bottom of each e-mail, be sure to include a Confidentiality Notice and your signature. - The Reliability Coordinator Information System (RCIS) is used to disseminate information to other RCs in other Interconnections. - Do not list the entity name on the SSRG e-mails or on the RCIS. |
| ### Events not Considered an Act of Suspected Sabotage |  |
| 1 | IF: - A TO or QSE reports an event that is not considered an act of suspected sabotage, such as the following: - Copper thefts - Substation break-in - Vandalism - Malicious mischief - Suspicious photos THEN: - Disseminate this information using the ‘SSRG’ distribution list: - State in the e-mail that the event is “currently not considered as an act of suspected sabotage”. - State the county of the event |
| 2 | MONITOR: - The RCIS (CIP Free Form) for ERCOT events which meet the criteria in step 1 that should be disseminated to SSRG; THEN: - Follow instructions in step 1 to disseminate the information |
| LOG | Log all actions. |
| ### Suspected Sabotage or Sabotage Events |  |
| Physical | For suspected physical sabotage at the ERCOT facilities, refer to ERCOT Guideline GL7.8.1 located under the “Sabotage Event Recognition” tab in each procedure manual. - RCIS posting and SSRG email will also be required. |
| Cyber | When notified by Cyber Security of a reportable event at ERCOT, collect the information to post under “CIP Free Form” on the RCIS. |
| 1 | IF: - A TO or QSE reports an act of suspected sabotage or a sabotage event; THEN: - Verify that the FBI has been notified, - Disseminate the information using the ‘SSRG’ distribution list: - State in the e-mail that the event is considered “an act of suspected sabotage OR further investigation/information is needed to determine if event is an act of suspected sabotage,” - State the county the event occurred ONCE: - Enough information has been received; NOTIFY: - TOs and QSEs via Hotline with information you have, - Post on the RCIS using “CIP Free Form”, - Coordinate with the Manager, System Operations and/or Control Room Operations Manager to determine if procedure 3.4 SSRG Conference Calls is necessary and for any NERC and DOE reporting requirements. Typical Hotline Script: “This is ERCOT operator [first and last name], at [xx:xx], ERCOT notified the System Security Response Group (SSRG) of a suspected sabotage event [give information]. Please notify your SSRG representative.” |
| 2 | WHEN: - Updates are received; THEN: - Send an updated e-mail to the ‘SSRG’ distribution list, - Update RCIS posting as needed |
| LOG | Log all actions. |

## 5.3	Notification of Protective Relay or Equipment Failures and Updates

Procedure Purpose:  Be aware and respond if needed to protective relay system failures when notified by a QSE or TO.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 6.2.3 | 6.2.4 |  |  |
| NERC Standard | PRC-001-1 R2, R2.2 |  |  |  |

| Version: 1 | Revision: 7 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ### Protective Relay or Equipment Failure |  |
| NERC | “If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible.” |
| NOTE | Protective relay systems include: relays, associated communications systems, voltage and current sensing devices, station batteries, and DC control circuitry |
| 1 | When notified by a QSE or TO that a protective relay or equipment failure reduces system reliability: - Ask the QSE or TO how it reduces ERCOT Grid system reliability and if any corrective actions have been taken, - Ask the QSE or TO if notifications have been made to any other affected TOs, - Notify the Operations Support Engineer to verify that system reliability has been affected. If so, a corrective action must be taken within 30 minutes, - Determine if other TOs are affected by this failure and make notification by phone. |
| 2 | - After notification from a TO or QSE, NOTIFY by e-mail: - OPS Support Engineering - Operations Analysis - Shift Supervisors - The subject line of the e-mail should read “Protective Relay or Equipment Failure.” - Include in the e-mail: - Entity Name - Brief description - Contact information - Any significant information |
| 3 | If a TO or QSE e-mails a – “Mis-Operation Relay report that has occurred in the past, forward to the above identified e-mail address. |
| 4 | Log all actions. |
| ### Protective Relay Outages |  |
| NOTE | Protective relay maintenance that ERCOT ISO has been made aware of can be found on the Outage Calendar located on the System Operations SharePoint. |
| Planned Outage | IF: - Notified that a relay is going to be removed from service (Planned); THEN: - Verify information is on the Outage Calendar located on the System Operations SharePoint Site; IF: - Notification is posted; THEN: - Notify the Market Participant they can proceed with work; IF: - Notification is NOT posted; THEN: - The relay can’t be removed from service unless there are secondary/back up relays that will be functional and no system degradation will occur; |
| Forced Outage | IF: - Notified that a primary relay has been removed from service (forced); THEN: - Ask if the secondary/back up relay is functional; IF: - There is no secondary/back up relay; THEN: - The equipment will need to be removed from service since it is no longer protected. |
| Log | Log all actions. |
| ### Protection System Setting Notifications |  |
|  | - WHEN: - Protection system setting notifications are received - FORWARD TO: - OPS Support Engineering - Operations Analysis - Shift Supervisors |

## 5.5	Supervise Coordination with SPP, MISO and CFE

Procedure Purpose:  To ensure proper notification and coordination takes place.

| Protocol Reference |  |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | IRO-014-1 R1 | TOP-001 R6 |  |  |

| Version: 1 | Revision: 5 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | The ERCOT ISO is only connected to another RC through asynchronous ties. The coordination and communication that must take place with SPP, MISO and CFE is outlined below. It is the responsibility of the Shift Supervisor to ensure this coordination takes place. - DC-Tie Tagging Activities - EEA Levels - Outages on DC-Ties - BLT’s - Arming of the Monticello SPS - Switchable Generation - ERCOT System Blackout Communications with CFE will be coordinated through AEP Corpus for the Eagle Pass and Laredo DC-Tie and Sharyland for the Railroad DC-Tie. |
| DC-Ties | Confirm that the DC Tie schedules and E-Tags were properly verified. Ensure that the “after-the-fact checkout” is performed each night and e-mailed to the appropriate entities as outlined in the DC-Tie Procedures. |
| EEA | ERCOT’s EEA status must be communicated to the SPP Reliability Coordinator (Turret phone button labeled SPP RC) as outlined in the DC-Tie procedures. |
| Outages | All planned and forced outages that affect the DC-Ties shall be coordinated with the Tie Operator(s) and SPP (if SPP DC-Ties affected). A message must also be posted on the MIS Public using Notice Builder for planned outages on any commercial DC-Ties. |
| BLT | Notify the SPP or MISO Reliability Coordinator when a BLT is initiated between ERCOT and SPP or MISO, as outlined in the Transmission & Security procedures. |
| SPS | Notify the SPP Reliability Coordinator when the Monticello SPS arms. If the SPS activates, the DC-E will trip. |
| ### Switchable Generation Resource |  |
| NOTE | Switchable Generation Resource (SGR) can be connected to either the ERCOT grid or MISO or SPP. ERCOT has coordination agreements with both SPP and MISO, if any entity enters or foresees entering into an emergency, the RC with the emergency can request help to mitigate the emergency. This help will consist of requesting one or more SGRs to switch into the grid with the emergency. |
| 1 | IF: - MISO or SPP call to request one or more SGR be switched into them; THEN: - Within one hour, determine that by releasing the SGRs it does not cause an Adverse Reliability Impact for ERCOT. IF: - No Adverse Reliability Impacts; THEN: - Notify the RC and the QSE for the SGR, it is up to the QSE as to whether they want to switch. Follow the same process if ERCOT requests a SGR be switched into ERCOT. |

## 6.1	Reports

Procedure Purpose: Provide reporting criteria and instructions for the daily reports sent to the PUC, the process to report certain events to the Texas Reliability Entity, posting EEA notices to RCIS and the process for reporting system disturbances to NERC and DOE.

| Protocol Reference | 22 (B) | 6.5.1.2 (5) |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference | 3.2.3 | 4.7 |  |  |
| NERC Standard | OE-417 | EOP-004-2 | EOP-010-1 |  |

| Version: 1 | Revision: 22 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |  |
| --- | --- | --- |
| ### PUCT Daily Report |  |  |
| Initial Report | Complete the PUCT Daily Report template between 0300 – 0400 and again between 1400 – 1500 each day. |  |
| E-Mail Report | E-mail the report to the distribution list entitled “PUC-Available Generating Resources.” |  |
| Update Report | Update and resend report when system conditions change that cause concern. Some examples are below: - The probability of an EEA event increases. Give reason(s) for concerns - When Off-Line Non-Spin is deployed for capacity (provide times) - A special update is not needed; provide information next time report is updated. - Conditions change that required new notices to be issued or cancelled - OCN, Advisory, Watch, or Emergency Notice (excluding GMD Advisory’s) - Clarify whether Transmission Watch/Emergency is due to a planned or forced outage (state the area of the state) noting the date and time - A special update is not needed for DAM/DRUC delays; provide information on the 1500 update - Do NOT update report for tool outages. - The Gibbons Creek Bryan East/Green Prairie 138 kV double circuit transmission line trips, or if unplanned outages of generation units cause security problems in the Bryan-College Station area - Localized gas curtailments, not expected to cause reliability issues (be specific, how much is derated) - A DCS event - Deployment of Load Resources - Any Nuclear Resource issues (including trips, coming off-line, high risk activities, de-ratings, etc.) Do Not use abbreviations, spell words out. Send updated report when conditions have returned to normal. |  |
| Weather Information | The temperatures are automatically pulled from the EMS, however please verify temperatures from a National or Local Weather Service for each city listed and adjust as necessary. |  |
| Guidelines for Determining EEA Potential | Use the following guidelines to determine the potential for EEA when completing the PUCT Daily Report: Potential for EEA Level 1 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability. - Medium - A Watch is in effect for Physical Responsive Capability. - Loss or delay of generation availability during peak demand that may diminish Physical Responsive Reserves - Excel MAI shows multiple hours of insufficient reserves and there is belief it is a significant threat - High - A Watch is in effect for Physical Responsive Capability and trending downward after procuring quick-start capacity - Excel MAI shows multiple hours of insufficient reserves AND ERCOT has been unable to correct the capacity insufficiency over several hours AND ERCOT believes it is a significant threat - Critical - EEA Level 1 in effect Potential for EEA Level 2 - Low - Sufficient capacity to cover peak demand - An Advisory is in effect for Physical Responsive Capability - Medium - EEA Level 1 in effect - High - Physical Responsive Reserve ≤ 1750 MW and trending downward - Critical - Physical Responsive Reserve ≤ 1375 MW and trending downward Potential for EEA Level 3 - Low - Sufficient capacity to cover peak demand - High - EEA Level 2 in effect - Physical Responsive Reserve < 1000 MW and trending downward, OR - Unable to maintain frequency ≥ 59.8 Hz - Critical - EEA Level 3 in effect |  |
| ### 7-Day Outlook |  |  |
| Report | Complete the 7-Day Outlook Report between 1500 – 1530 each day. |  |
| Open | The 7 Day Forecast file is located: P:\SYSTEM OPERATIONS drive in the “7-Day Outlook” Folder. |  |
| Verify | Data looks to be correct. |  |
| E-Mail Report | E-mail the report to the 7-Day Load and Capacity Outlook distribution list by selecting “Report” and confirming. |  |
| Unit Trip Posting |  |  |
| Report | Complete the Unit Trip posting for the previous day between 0000 – 0800 each day of the week. |  |
| Analyze | Review: - Any unit trips from the previous day, - Post an Operational Information message, low priority, on MIS Public |  |
| <450 MW | IF: - No trips are greater than 450 MW, - Post the following message example on MIS Public |  |
| Post | No sudden loss of generation greater than 450 MW occurred on <Date>. |  |
| ≥450 MW | IF: - A trip was 450 MW or more, - Post the following message example on MIS Public |  |
| Post | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| Multiple Trip Example | On <Date>, a sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. Another sudden loss of generation occurred at <Time> totaling *** MW. Frequency declined to **.*** Hz, ERCOT load was **,*** MW. |  |
| ### Event Analysis Reporting |  |  |
| 1 | WHEN an event occurs that is listed on the “event list” below, before shift is over: - E-mail information to Manager, System Operations and Control Room Operations Manager - The subject line of the e-mail should read “TRE Event.” |  |
| Event List | For purposes of the event analysis program, brief reports must be completed with 5 days. Most events listed are either OE-417 or EOP-004 reportable, those timelines and forms will be used in place of the EA brief report. Category 1 Events: - An unexpected outage, contrary to design, of three or more elements caused by a common disturbance. For example: - The sustained outage of a combination of three or more facilities - The outage of an entire generation station of three or more generators (aggregate generation of 500 MW to 1,999 MW); each combined cycle unit is counted as one generator - Intended and controlled system separation by the proper operation of a SPS - Failure or misoperation of BPS SPS - System-wide voltage reduction of 3% or more that lasts more than 15 continuous minutes due to a BPS emergency - Unintended BPS system separation that results in an island of 100 MW to 999 MW. Excludes BPS radial connection, and non-BPS (distribution) level islanding - Unplanned evacuation from a control center facility with BPS SCADA functionality for 30 minutes or more - The loss of generation of 1,000 MW – 1,399 MW - Loss of monitoring or control, at a control center, such that it significantly affects the entity’s ability to make operating decisions for 30 continuous minutes or more. Examples include, but are not limited to the following: - Loss of operator ability to remotely monitor, control Bulk Electric System (BES) elements, or both. - Loss of communications from SCADA RTUs - Unavailability of ICCP links reducing BES visibility - Loss of the ability to remotely monitor and control generating units via AGC - Unacceptable State Estimator or Contingency Analysis solutions Category 2 Events: - Complete loss of all BPS control center voice communication system for 30 minutes or more - Complete loss of SCADA, control or monitoring functionally for 30 minutes or more - Voltage excursions equal to or greater than 10% lasting more than 15 continuous minutes due to a BPS emergency - Loss of off-site power (LOOP) to a nuclear generating station per the Nuclear Plant Interface Requirement - Unintended system separation that results in an island of 1,000 MW to 4,999 MW - Unintended loss of 300 MW or more of firm load for more than 15 minutes - Interconnection Reliability Operating Limit (IROL) Violation for time greater than Tv. Category 3 Events: - Unintended loss of load or generation of 1,400 MW or more - Unintended system separation that results in an island of 5,000 MW to 10,000 MW Category 4 Events: - Unintended loss of load or generation from 5,001 MW to 9,999 MW - Unintended system separation that results in an island of more than 10,000 MW Category 5 Events: - Unintended loss of load of 10,000 MW or more - Loss of generation of 10,000 MW or more |  |
| ### NERC and DOE Reporting |  |  |
| NOTE | - Contact the Manager, System Operations and/or Control Room Operations Manager when a NERC or DOE reporting event occurs. If available, they will be responsible to complete the required form - In the body of the e-mail, type the following: - "Contains Privileged Information and/or Critical Energy Infrastructure Information - Do Not Release.". - NERC 24-hour Emergency Hotline (404) 446-9780), |  |
| OE-417 Reporting Events | DOE OE-417 forms can be downloaded at: http://www.eia.gov/survey/form/oe_417/form.pdf. The items in bold/grey must be reported within 1 hour of the incident. The others must be reported within 6 hours. All final reports must be submitted within 48 hours. OE-417 reports are required for the following events: - Actual physical attack that causes major interruptions or impacts to critical infrastructure facilities or to operations - Actual cyber or communications attack that causes major interruptions of electrical system operations - Complete operation failure or shut-down of the transmission and/or distribution electrical system - Electrical System separation (Islanding) where part or parts of a power grid remain(s) operational in an otherwise blacked out area or within the partial failure of an integrated electrical system - Uncontrolled loss of 300 MW or more of firm system loads for more than 15 minutes from a single incident - Load shedding of 100 MW or more implemented under emergency operational policy - System-wide voltage reduction of 3 % or more - Public appeal to reduce the use of electricity for purpose of maintaining the continuity of the electric power system (ERCOT process each EEA) - Suspected physical attacks that could impact electric power system adequacy or reliability; or vandalism which target components of any security systems - Suspected cyber or communications attacks that could impact electric power system adequacy or vulnerability - Loss of electric service to more than 50,000 customers for 1 hour or more - Fuel supply emergencies that could impact system adequacy or reliability |  |
| Event Reporting EOP-004-2 | NERC Preliminary Disturbance reports are to be completed within 24 hours of recognition of meeting an event type threshold for reporting or by the end of the next business day if the event occurs on a weekend (which is recognized to be 4 PM local time on Friday to 8 AM Monday local time).. Events that are also DOE reportable, the OE-417 form should be used. For the other events, use the EOP-004 – Attachment 2 Event Reporting Form: - Damage or destruction of a Facility that results in actions to avoid a BES Emergency - Damage or destruction of a Facility that results from actual or suspected intentional human action - Physical threats to a Facility excluding weather or natural disaster related threats, which has the potential to degrade the normal operation of the Facility or suspicious device or activity at a Facility. Do not report theft unless it degrades normal operation of a Facility - Physical threats to a BES control center - Public appeal for load reduction event (ERCOT process each EEA) - System wide voltage reduction of 3% or more - Manual firm load shedding 100 MW or more - Automatic firm load shedding 100 MW or more (via automatic undervoltage or underfrequency load shedding schemes or SPS - Voltage deviation of 10% or more of nominal voltage sustained for 15 or more continuous minutes - IROL violation - Loss of firm load for 15 minutes or more: - 300 MW or more for entities with a previous year’s demand of 3,000 MW or more - 200 MW or more for all other entities - Each system separation resulting in an island 100 MW or more - Loss of generation of 1,000 MW or more - Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement - Unexpected loss within its area, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing - Unplanned evacuation from BES control center facility for 30 continuous minutes or more - Complete loss of voice communication capability affecting a BES control center for 30 continuous minutes or more - Complete loss of monitoring capability affecting a BES control center for 30 continuous minutes or more such that analysis capability (i.e., State Estimator or Contingency Analysis) is rendered inoperable |  |
| 1 | When required to file or forward a report, the Manager, of System Operations or the Control Room Operations Manager will be responsible. File or forward disturbance report to entities that have not received: - NERC System Awareness (systemawareness@nerc.net) - NERC (esisac@nerc.com), courtesy copy only - Fax (404) 446-9770, if internet down - Phone (404) 446-9780 - DOE when required above (doehqeoc@oem.doe.gov) - Fax (202) 586-8485, if internet down - Phone (202) 586-8100 - NERC and DOE Disturbance Reporting e-mail list |  |
| NOTE | Please be aware that for phone calls to NERC, you will be prompted by a computerized auto-attendant to press 1 for operational issues or 2 for cyber-security issues. |  |
| ### RCIS Reporting |  |  |
| EEA Postings | There are four levels of Emergency Energy Alert (EEA). As ERCOT enters each level, postings must be made on the RCIS under “Energy Emergency Alert”: - “ERCOT is declaring EEA 1” - “ERCOT is declaring EEA 2” - “ERCOT is declaring EEA 3” - “ERCOT is in EEA 0 and back to normal operations.” |  |
| ### NXT Notification Requirements |  |  |
| Beginning of each Shift |  | Log into the NXT Communicator at the beginning of each shift in order to make the required notification quickly. - If issues arise and you are unable to log into the NXT Communicator with your user name, notify the helpdesk and request immediate assistance. |
| NOTE |  | NXT notification should be coordinated with the Shift Engineer. |
| Watch |  | IF: - A Watch for Physical Responsive Capability is initiated, THEN: - Select the “SO Watch PRC below 2500” Scenario and activate notification, WHEN: - A Watch for Physical Responsive Capability has been cancelled, THEN: - Select the “SO Watch for PRC Cancelled” Scenario and activate notification. |
| EEA Implementation Levels |  | IF: - ERCOT initiates EEA Level 1, THEN: - Select the “SO EEA Level 1” Scenario and activate notification, IF: - ERCOT initiates EEA Level 2, THEN: - Select the “SO EEA Level 2” Scenario and activate notification, IF: - ERCOT initiates EEA Level 3, THEN: - Select the “SO EEA Level 3” Scenario and activate notification. |
| EEA Termination Levels |  | WHEN: - EEA Level 3 is terminated, THEN: - Select the “SO EEA Level 3 to EEA Level 2” Scenario and activate notification, WHEN: - EEA Level 2 is terminated, THEN: - Select the “SO EEA Level 2 to EEA Level 1” Scenario and activate notification, WHEN: - EEA Level 1 is terminated, THEN: - Select the “SO EEA Level 1 Cancellation” Scenario and activate notification. |
| Loss of Firm Load |  | IF: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≤ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately. WHEN: - An Operator (ERCOT or TO) has issued a request for firm load shed of ≥ 100 MW, THEN: - Notify the Manager, System Operations and/or Control Room Operations Manager immediately, - Select the “SO Request Firm Load Shed” Scenario and activate notification. |
| NXT Testing |  | WHEN: - Performing Shift Supervisor Procedure 9.2 Monthly Testing of Non-Routinely used Telecommunications Facilities, THEN: - Select the “SO ENS Test” Scenario and activate notification. |
| ### ERCOT Morning Report |  |  |
| NOTE | - This report is currently only required Monday – Friday. - The Morning Report form is located on the _Operations Official Spreadsheets folder |  |
| 1 | Weather Information: - Enter temperatures from a National or a Local Weather Service for each city listed. - Enter the current day forecast conditions for each city listed. |  |
| 2 | Load Data: - The All-Time Peak MW and Seasonal Peak MW will be provided as needed. - Verify the Projected Peak MW and peak hour for the current day. Use the most reasonable forecast, which may not be the highest. - Verify the Previous Day Actual MW. |  |
| 3 | Interchange: - Verify the net flow across the DC-Ties for the peak hour. This can be obtained from the MOI under “DC Tie Scheduling” or from the Excel MAI. |  |
| 4 | Transmission Line Outages: - Verify the number of 345 kV line segment outages for the peak hour. |  |
| 5 | Generation MW Totals: - Verify the Generation scheduled outage MW total. - Verify the Generation forced outage MW total. |  |
| 6 | Projected MW Reserves: - Verify the Responsive Reserve requirement at the Project Peak. - Verify the anticipated operating reserves available at time of peak. - The anticipated operating reserves can be found by adding the “Max Cap. Room” and Responsive Reserve requirement. |  |
| 7 | Recent ERCOT Congestion Activity: - No action needed |  |
| 8 | Comments: - List any active OCNs, Advisories, Watches or Emergency notices. |  |
| 9 | Select: Create Report |  |
| EMAIL | The file is transferred to P:\SYSTEM OPERATIONS drive in the NERC Morning Report Folder. This report should be sent as an attachment by 0700 using the e-mail distribution list entitled “ERCOT Morning Report.” The subject line of the e-mail should read “ERCOT Morning Report for <date>” |  |
| ### RMR Unexcused Misconduct Events |  |  |
| NOTE | - For a RMR unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not; deliver the energy at a level of at least 98% on each hour of the level shown in the Availability Plan. - For a Synchronous Condenser Unit, a “Misconduct Event” means any hour or hours during which Participant is requested to, but does not, synchronize the Unit to the ERCOT Transmission Grid during any hour in which the Unit is shown in the Availability Plan |  |
| 1 | IF: - An RMR or Synchronous Condenser fail to deliver the energy when requested to; THEN: - Notify the Manager of System Operations and/or Control Room Operations Manager. - The manager will gather the detailed information and send an e-mail to “Nodal Settlements and Billing” with the subject line “Action Required – RMR Unexcused Misconduct Event”. |  |
| ### Shift Schedule |  |  |
| NOTE | - Shift Schedules will be posted to the MIS under GRID on the Transmission Page in the Transmission Supporting Information section. - The posting of the schedule will be current at all time to be compliant with the Protocols. |  |
| ### GEO-Magnetic Disturbance (GMD) |  |  |
| NOTE | Solar storms or Geo magnetic disturbances (GMDs) are caused by the interaction of coronal mass ejections (solar flares) with the Earth’s Ionosphere. This interaction produces ionospheric currents in the magnitude of millions of amperes which disturb Earth’s magnetic field. This disturbance induces voltage potential at Earth’s surface which results in geomagnetically induced currents (GICs) in conducting paths such as long transmission lines, pipelines, cables etc. GICs are low frequency or quasi-DC currents which enter and exit the power system at transformer groundings and grounded transmission lines. GICs of 100’s of amperes in magnitude have been recorded. Hence the GICs have the potential to disrupt the normal operation of power system and may damage transformers. GICs may also lead to the loss of reactive power support and hence may cause voltage instabilities. |  |
| Monitor | Monitor: - Reliability Coordinator Information System (RCIS) at https://rcis.nerc.net - NOAA’s Space Weather Prediction Center |  |
| Warning | WHEN: - A Warning for a GMD is issued for K-7 and greater or G3 and greater; THEN: - Post message on MIS Public - Notice Type: Operational Information - Notice Priority: Low Typical MIS Posting: The Space Weather Prediction Center has issued a GMD Warning of [state level] until [date and time]. |  |
| Extend | IF: - The Warning is extended; THEN: - Post new message on MIS Public and - Cancel the older message Typical MIS Posting: The Space Weather Prediction Center has extended the GMD Warning of [state level] until [date and time]. |  |
| Cancel | WHEN: - The Warning is no longer valid; THEN: - Cancel the MIS posting. |  |
| Alert | WHEN: - An Alert for a GMD is issued for K-7 and greater or G3 and greater; THEN: - Instruct the Transmission & Security and Real-Time Operators to implement their GMD procedures. |  |
| Extend | IF: - The Alert is extended; THEN: - Instruct the Operators to extend the Alert. |  |
| Cancel | WHEN: - The Alert is no longer valid; THEN: - Instruct the Operators to cancel the Advisory for the Alert. |  |
| Issues | IF: - Any TO reports an issue due to the GMD event; THEN: - Send e-mail to the following with the details - Operations Analysis - Shiftsupv |  |
| ### Gas Restrictions |  |  |
| 1 | Once notified by a QSE of gas restrictions - Send an e-mail to “Gas Company Notifications”. This will notify all appropriate ERCOT staff. |  |
| 2 | Determine: - If the gas restriction could impact electric power system adequacy or reliability, THEN: - Proceed to “Reports” procedure for NERC/DOE reporting requirements, AND - Consider fuel switching for the generation that has this capability This data can be viewed at ERCOT SharePoint > System Operations – Control Center > Quick Links > Fuel Oil Capability |  |
| ### Special Protection Systems (SPSs) |  |  |
|  | IF: - A Monthly SPSs report is received by e-mail; THEN: - Forward reports to: - OPS Support Engineering - Shift Supervisors |  |

## 7.2	EEA Implementation Checklist

shift Supervisor – EEA IMPLEMENTATION Check List

| Time | Action | Comment |
| --- | --- | --- |
|  | Administrative tasks applicable to each step: |  |
|  | - Hotline calls made |  |
|  | - NXT System activated |  |
|  | - MIS message posted |  |
|  | - SPP RC Notified |  |
|  | - RCIS Posting |  |
|  | - PUCT Report updated |  |
|  | - Ensure 3-part communication is used |  |
|  | EEA Level 1 Implementation | PRC <2300 MW |
|  | - Non-Spin deployed |  |
|  | - 30 MIN ERS deployed, if deploying in Level 1. This includes Weather-Sensitive if June – September and business hours 2 & 3 |  |
|  | - Resource testing suspended |  |
|  | - Online RMRs loaded to full output |  |
|  | - Emergency Energy procedures implemented across CFE DC-Ties |  |
|  | - EEA 1 Schedule requested across SPP DC-Ties |  |
|  | - RUC VDI/electronic Dispatch Instruction, as appropriate/including EMR |  |
|  | - TOs load management program deployed if deemed necessary if June - September |  |
|  | - OE-417 for public appeals |  |
|  | EEA Level 2 Implementation | PRC <1750MW |
|  | - Load Resources deployed and/or ERS Resources - Block 1 (<1750MW) - Block 2 (as needed) - Both (<1375MW) |  |
|  | - 30 MIN ERS deployed, if not deployed in Level 1. This includes Weather-Sensitive if June – September and business hours 2 & 3 |  |
|  | - 10 MIN ERS deployed, if deemed necessary |  |
|  | - TOs load management program deployed if June - September |  |
|  | - Emergency Energy Procedures implemented across SPP DC-Ties |  |
|  | - TOs notified of Load Resource deployment |  |
|  | - Distribution voltage reduction, as appropriate |  |
|  | - RUC VDI/electronic Dispatch Instruction, as appropriate/including EMR |  |
|  | EEA Level 3 Implemention | Unable to maintain Freq at 59.8 Hz. |
|  | - Firm Load shed ordered (100 MW blocks) |  |
|  | - QSEs notified of Firm Load shed |  |
|  | - Load shed achieved |  |

## 7.5	Extreme Cold Weather

Procedure Purpose: To ensure ERCOT is prepared for Severe Cold Weather Operations

| Protocol Reference | 6.3.2(3)(a)(ii) | 6.5.9.3(2)&(3) | 6.5.9.3.1(4) | 6.5.9.3.2(4) |
| --- | --- | --- | --- | --- |
|  | 6.5.9.3.3(6) | 6.5.9.3.4(1) |  |  |
| Guide Reference | 4.2.1 | 4.2.2 | 4.2.3 | 4.2.4 |
| NERC Standard | COM-002-2 R2 |  |  |  |

| Version: 1 | Revision: 4 | Effective Date: March 1, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| NOTE | - Extreme cold weather notifications will be issued when temperatures or wind chill is forecasted to be below freezing for sustained periods and may abnormally impact load levels or generation availability - For such events, additional reserves may be necessary |
| Reporting | As system conditions warrant, complete the following tasks: - Refer to the “Abnormal Events” procedure (7.1) and take appropriate actions for “Gas Restrictions” - Refer to the “Reports” procedure (6.1) and complete the appropriate reporting forms for the conditions that exist. |
| OCN | When approaching extreme cold weather is approximately 5 days away: - Ensure OCN is issued - Continue to monitor the expected path of the approaching extreme cold front - Coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored - Coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market allows - Review emergency operating procedures |
| Advisory | When approaching extreme cold weather is 3 days away: - Ensure Advisory is issued - Continue to monitor the expected path of extreme cold front - Continue to coordinate with Outage Coordination for the review of planned and existing transmission outages to be withdrawn, rejected, or restored - Continue to coordinate with Outage Coordination for the review of planned and existing Resource outages that could be asked to be delayed or returned early - Contact Operations Support to run studies to determine the impact of current and future outages - Review system conditions and determine if more lead-time is needed than the normal Day Ahead market or if additional Ancillary Services will be needed - Review emergency operating procedures |
| Watch | When approaching extreme cold weather is 1 day away: - Ensure Watch is issued - Continue to monitor the expected path of extreme cold front - Review emergency operating procedures - Determine the need for additional support staff - Determine if additional Ancillary Services will be needed - Ensure maximizing generator availability is complete - Determine if Resources need to be committed early before freezing temperatures arrive - Consider if fuel switching is needed. |
| Emergency Notice | When extreme cold weather has arrived and is beginning to have an adverse impact on the ERCOT System: - Ensure Emergency Notice is issued - Implement emergency procedures as needed |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch, Hartmann, and Moore | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 10, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | August 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch and Hartmann | Procedure writers and editors | January 27, 2014 |
| Frosch, Gaddy, and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Updated steps 1 and 5, deleted steps 6, 7 and 8 Updated VDI, Testing Rules and Retest Updated PUCT Daily Report step “Update Report”. Updated all steps of Texas RE Event Reporting. Updated Title (Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms), 1st Note and Monitor | December 1, 2010 |
| 3.2 3.3 3.7 4.2 6.1 10.2 | 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 2 1.0 / 2 - / 2 | Updated step 1,3 and added step 4 in “Capacity Monitoring” Updated step 4 Updated step No SCED Solution Updated VDI, Retest, and Notify, added Completion Updated step OE-417 Reporting Events in NERC, DOE Reporting and step 2 on GEO-Magnetic Disturbance (GMD) Updated step Monitor on “Dynamic Rating, SCED Status, EMBP, SE, RTCA or RLC Alarms” | January 31, 2011 |
| 3.2 5.3 5.5 6.1 7.2 7.3 9.2 | 1.0 / 2 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated step 3 “Capacity Monitoring” Updated step 1 & 3 Updated 1st note & step 2 Updated PUCT Daily Report, Texas RE Event Reporting & NXT Notification Updated EEA Checklist Updated EEA Restoration Checklist Added new steps “SAT modem testing” & updated NXT Tests | March 25, 2011 |
| 4.2 5.1 7.1 7.3 | 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 1 | Updated “Unannounced Resource Testing” 1st note Updated 2nd & 6th paragraphs Updated “System Disturbance” NERC, step 2 and “Degraded Weather” step 3 Updated Table | April 22, 2011 |
| 5.3 5.7 6.1 7.1 7.4 7.5 7.6 8.3 | 1.0 / 2 1.0 / 1 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 0 1.0 / 1 1.0 / 1 | Updated step 2 Updated all steps Updated all steps in Texas RE Event Reporting and NERC and DOE Reporting Updated steps in Degraded Weather Updated all steps Added new procedure Updated all steps Updated step 2 and deleted step 3 | June 8, 2011 |
| 3.6 4.1 4.2 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 1 1.0 / 4 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 2 | Updated step 3 Removed Initial Synchronization of New Resource Updated Testing Rules Updated step Event List Updated EEA Implementation Checklist Updated EEA Restoration Checklist Added Notice Builder test in Primary Control Center section | July 20, 2011 |
| 4.2 5.5 6.1 7.2 7.3 7.7 9.2 10.1 | 1.0 / 5 1.0 / 2 1.0 / 6 1.0 / 2 1.0 / 3 1.0 / 0 1.0 / 3 1.0 / 1 | Updated step Caution Updated 1st Note Updated step 1 in Texas RE Event Reporting and NXT Testing in NXT Notification Requirements Updated EEA Implementation checklist Updated EEA Restoration checklist Added Extreme Hot Weather Updated NXT Test in Alternate Control Center Updated step 3 | September 1, 2011 |
| 3.4 6.1 7.2 7.3 9.2 | 1.0 / 1 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 4 | Grammar changes Combined EEA 2A & B per NPRR 379 Updated to implement NPRR 379 Updated to implement NPRR 379 Updated Phone Test in Alternate Control Center | October 1, 2011 |
| 3.7 7.2 10.2 | 1.0 / 2 1.0 / 3 1.0 / 3 | Changed title & all steps Updated EEA checklist Updated 1st Note | November 1, 2011 |
| 3.3 6.2 6.3 | 1.0 / 2 1.0 / 1 1.0 / 1 | Updated all steps Updated step 2 Updated step 1 & 2 All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 4.2 5.7 | - / 1 - / 6 - / 2 | Updated Scope Updated all steps of procedure Updated Market Participant Backup Control Center Transfer | January 19, 2012 |
| 2.1 3.3 3.4 3.7 3.8 4.1 4.2 5.3 5.6 5.8 6.1 7.1 9.1 9.2 10.2 | 1.0 / 1 1.0 / 3 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 7 1.0 / 3 1.0 / 1 1.0 / 1 1.0 / 8 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 4 | Updated paragraph 4 Updated Step 3 Updated Threat & Emergency Classifications & Desktop Guide reference Changed Shift Engineer to Operations Support Corrected grammar on step 1 Changed Shift Engineer to Operations Support Updated procedure Changed Shift Engineer to Operations Support Corrected grammar on step 2 Updated step 2 Updated Texas RE Event Reporting, OE-417 reporting & Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Updated Desktop Guide reference Changed Shift Engineer to Operations Support and updated Desktop Guide reference | March 1, 2012 |
| 2.1 3.3 3.6 5.6 6.1 7.1 7.4 7.5 7.6 | 1.0 / 2 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 9 1.0 / 4 1.0 / 2 1.0 / 2 1.0 / 2 | Changed TSP/DSP to TO Updated 3rd Note Updated purpose Changed TSP to TO and Transmission Facility Updated step Update Report & changed ARR to PRC and ERCOT Morning Report Updated step NERC and Degraded Weather Updated OCN, Advisory, & Watch steps Deleted Cold Weather, not Extreme Cold Weather Section number changed, Added OCN, Advisory and Emergency Notice | May 1, 2012 |
| 3.2 | 1.0 / 3 | Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 3 1.0 / 4 | Updated EILS to ERS per NPRR 451 & added TO load management program Updated EILS to ERS per NPRR 451 & added TO load management program | June 1, 2012 |
| 3.3 4.2 6.1 | 1.0 / 5 1.0 / 8 1.0 / 10 | Updated step 3 Added Desktop Guide to VDI reference Updated PUCT Daily Report, NERC and DOE Reporting and RCIS Posting | July 16, 2012 |
| 3.4 4.2 5.9 6.1 7.2 | 1.0 / 3 1.0 / 9 1.0 / 1 1.0 / 11 1.0 / 4 | Added CPT to procedure and Typical Subject line for e-mail Added Log to procedure Deleted Procedure Updated NERC and DOE Reporting Added 30 MIN ERS deployed to EEA 1 | August 29, 2012 |
| 2.2 3.1 5.3 6.1 7.6 9.1 | 1.0 / 1 1.0 / 2 1.0 / 4 1.0 / 12 1.0 / 3 1.0 / 2 | Added Hotline Call Communication Updated step 5 Updated and added Planned and Forced Outage sections. Added Weather Information section to PUCT Daily Report. Updated step 1 in NERC and DOE Reporting and ERCOT Morning Report section. Updated OCN, Advisory, & Watch Updated step E-mail All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.2 3.3 3.4 3.5 3.6 3.7 3.8 4.1 5.2 5.3 5.5 5.6 5.8 6.1 6.2 6.3 7.4 7.5 7.6 8.3 8.6 9.2 10.1 10.2 11.0 | 1.0 / 4 1.0 / 6 1.0 / 4 1.0 / 1 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 3 1.0 / 1 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 2 1.0 / 13 1.0 / 2 1.0 / 2 1.0 / 3 1.0 / 3 1.0 / 4 1.0 / 2 1.0 / 1 1.0 / 6 1.0 / 2 1.0 / 5 1.0 / 1 | Updated step 1, Capacity Monitoring and deleted Reserve Monitoring Updated step 3 Updated notes and Management Notifications Updated purpose and step 1 Updated step 2 Updated step TCM & renamed LMP Map Delete procedure for large wind ramp events Updated step 1 Grammatical correction Updated step 3 Protective Relay or Equipment Failure Added MISO Reliability Coordinator Updated step 2 TO Temporary Equipment Limitation Notifications Updated purpose Updated step 1 Texas RE Event Reporting, Note and step 1 NERC and DOE Reporting, Loss of Firm Load NXT Notification Requirements, step 1 Weather Information section to ERCOT Morning Report, step 1 RMR Unexcused Misconduct Events, GMD, step 2 Gas Restrictions and added Special Protection Systems (SPSs) Deleted procedure Renamed to 6.2 and updated procedure Updated step Reporting Updated step Reporting Updated Log Updated step 2 Updated procedure Deleted Notice Builder Updated step 3 Updated step monitor, step 4 Building Security and Fire Alarms and step 3 Failure of the Emergency Generator Updated procedure Review New Communications from Manager and/or Control Room Operations Manager and step 4 Implement ERCOT Personnel and Company Standards | March 1, 2013 |
| 3.3 3.4 6.1 | 1.0 / 7 1.0 / 5 1.0 / 14 | Updated all steps Added 1st Note, deleted 2nd & 3rd Notes, Management Notification, updated QSE Notification, TO Notification Updated step Update Report | June 1, 2013 |
| 4.1 5.1 6.1 10.2 | 1.0 / 4 1.0 / 2 1.0 / 15 1.0 / 6 | Updated Ancillary Service Testing Coordination and added Coordinated Reactive Tests Added MISO Updated PUCT Daily Report & step 1 on NERC and DOE Reporting and added Note to NXT Notification Requirements Updated 1st Note and step #3 on Building Security and Fire Alarms | July 15, 2013 |
| 3.4 4.1 6.1 7.3 | 1.0 / 6 1.0 / 5 1.0 / 16 1.0 / 5 | Updated QSE Notification, TO Notification & Send E-mail Updated Coordinated Reactive Tests Added 7-Day Outlook, updated Event List on Texas RE Event Reporting & step 2 on GEO-Magnetic Disturbance (GMD) Updated table | August 9, 2013 |
| 3.3 | 1.0 / 8 | Removed HHGT TO reference | August 30, 2013 |
| 3.3 3.4 4.1 4.2 5.3 5.4 5.6 5.7 6.1 7.6 8.1 8.2 8.3 9.1 9.2 10.2 | 1.0 / 9 1.0 / 7 1.0 / 6 1.0 / 10 1.0 / 6 1.0 / 1 1.0 / 4 1.0 / 3 1.0 / 17 1.0 / 5 1.0 / 1 1.0 / 1 1.0 / 3 1.0 / 3 1.0 / 7 1.0 / 7 | Updated step 1 and Log Updated step Log Updated step Log Updated step Log Updated step 4, Planned Outage, Forced Outage and added Log Updated step Log Updated step Log Updated step 1 and added Log Updated step Update Report, TRE Event Reporting changed to Event Analysis Report and event list updated, and NERC and DOE Reporting updated Added step Issues and updated Log Updated step 3 and added Log Updated step 3, 5 and added Log Updated step 3 Updated step Log Updated steps Log Added step 4 and updated Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 4.1 6.1 7.2 7.3 | 1.0 / 7 1.0 / 18 1.0 / 5 1.0 / 6 | Updated for NOGRR125 & OK to test on Coordinated Reactive Tests Updated NERC and DOE Reporting Updated EEA Implementation Checklist Updated EEA Restoration Checklist | January 29, 2014 |
| 3.2 4.2 5.5 6.1 6.2 | 1.0 / 5 1.0 / 11 1.0 / 4 1.0 / 19 1.0 / 3 | Updated VDI information Updated VDI information Updated Note Updated Update Report on PUCT Daily Report and step 1 on NERC and DOE Reporting Updated step 1 | April 4, 2014 |
| 2.2 7.1 | 1.0 / 2 1.0 / 5 | Added VDIs to Master QSEs Updated step 1 | June 1, 2014 |
| 4.2 6.1 6.2 7.2 | 1.0 / 12 1.0 / 20 1.0 / 4 1.0 / 6 | Updated 1st Note, Retest and added Demonstration Test Updated step Update Report Updated steps 1 & 4 Updated checklist | August 1, 2014 |
| 3.3 3.4 4.1 4.2 9.2 | 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 13 1.0 / 8 | Added step 2 Corrected spelling on Send E-mail Updated script for Unit Testing Added new reference Updated new section on Phone Tests | October 1, 2014 |
| 3.6 3.7 4.2 6.1 | 1.0 / 4 1.0 / 5 1.0 / 14 1.0 / 21 | Changed title and removed references to W-N Added step RTMONI Updated Testing Rules and Scripts Added 2nd note to NERC and DOE Reporting & updated GMD procedure All procedures in this manual have been reviewed | December 15, 2014 |
| 2.2 3.2 3.3 4.2 5.3 5.5 6.1 7.2 7.5 | 1.0 / 3 1.0 / 6 1.0 / 11 1.0 / 14 1.0 / 7 1.0 / 5 1.0 / 22 1.0 / 7 1.0 / 4 | Added Dispatch and VDI definitions Updated step 4 Updated step 1 in Suspected Sabotage or Sabotage Events Moved procedure to Resource desk Updated title and added Protection System Setting Notifications Added Switchable Generation Resource Added Unit Trip Posting Updated checklist Updated Note | March 1, 2015 |