- Power Operations Bulletin # 724

ERCOT has posted/revised the Resource manual.

The Various Changes are shown below.

A copy of the procedure can be found at:

## http://www.ercot.com/mktrules/guides/procedures/index.html

## 3.5	Responding to GTCs

Procedure Purpose:  Deployment/Termination of Non-Spin Reserve Service and/or Load Resources for Congestion Management as requested by the Transmission Operator.

| Protocol Reference | 6.5.7.6.2.3(10) |  |  |  |
| --- | --- | --- | --- | --- |
| Guide Reference |  |  |  |  |
| NERC Standard | EOP-001-2.1b R2.2, R3.2, R4 | TOP-004-2 R1 | TOP-007-0 R3 | TOP-008-1 R1 |

| Version: 1 | Revision: 15 | Effective Date: October 30, 2015 |
| --- | --- | --- |

| Step | Action |
| --- | --- |
| ## North to Houston Interface |  |
| Deploy Non-Spin | WHEN: - Notified by the Transmission Operator to deploy Non-Spin in the Houston area for the North-Houston Interface; THEN: - Deploy Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) (Refer to Desktop Guide Resource Desk Section 2.1.3) |
| NOTE | To the extent that ERCOT deploys a Load Resource that has chosen a block deployment option, ERCOT shall either deploy the entire offer or, if only partial deployment is possible, skip the offer by the Load Resource with the block deployment option and proceed to deploy the next available Resource. |
| NOTE | If Non-Spin is deployed from one operating day to the next operating day, new deployments will need to be sent for the new day. |
| Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Houston area for the North-Houston Interface; THEN: - Deploy Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by XML (Refer to Desktop Guide Resource Desk Section 2.2.2), - Call appropriate QSE to notify them their LR was deployed. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Houston area for the North-Houston Interface; THEN: - Recall Load Resources in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML (Refer to Desktop Guide Resource Desk Section 2.2.4), - Call appropriate QSE to notify them their LR was recalled. |
| Recall Non-Spin | WHEN: - Notified by the Transmission Operator to recall Non-Spin in the Houston area for the North-Houston Interface; THEN: - Recall Non-Spin in the Houston area (Coast Weather Zone WZ_COAST) by sending a Zero MW XML, (Refer to Desktop Guide Resource Desk Section 2.1.4). |
| ## Rio Grande Valley Interface |  |
| Deploy Load Resources | WHEN: - Notified by the Transmission Operator to deploy Load Resources in the Rio Grande Valley; THEN: - Deploy Load Resources (Refer to Desktop Guide Resource Desk Section 2.2.3), - Call appropriate QSE to notify them their LR was deployed. |
| Recall Load Resources | WHEN: - Notified by the Transmission Operator to recall Load Resources in the Rio Grande Valley; THEN: - Recall Load Resources in the Rio Grande Valley (Refer to Desktop Guide Resource Desk Section 2.2.4), - Call appropriate QSE to notify them their LR was recalled. |
| Log | Log all actions. |

Document Control

Preparation

| Prepared by | Role | Date Completed |
| --- | --- | --- |
| Frosch, Hartmann, Stone, and Barcalow | Preparers | November 10, 2010 |
| Frosch and Hartmann | Procedure writers and editors | November 29, 2010 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2010 |
| Frosch and Hartmann | Procedure writers and editors | January 26, 2011 |
| Frosch and Hartmann | Procedure writers and editors | March 23, 2011 |
| Frosch and Hartmann | Procedure writers and editors | April 20, 2011 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2011 |
| Frosch and Hartmann | Procedure writers and editors | June 6, 2011 |
| Frosch and Hartmann | Procedure writers and editors | July 18, 2011 |
| Frosch and Hartmann | Procedure writers and editors | August 30, 2011 |
| Frosch and Hartmann | Procedure writers and editors | September 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | October 28, 2011 |
| Frosch and Hartmann | Procedure writers and editors | December 13, 2011 |
| Frosch and Hartmann | Procedure writers and editors | January 16, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | April 25, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | May 30, 2012 |
| Barcalow, Frosch and Hartmann | Procedure writers and editors | July 10, 2012 |
| Frosch and Hartmann | Procedure writers and editors | August 27, 2012 |
| Frosch and Hartmann | Procedure writers and editors | October 26, 2012 |
| Frosch and Hartmann | Procedure writers and editors | February 26, 2013 |
| Frosch and Hartmann | Procedure writers and editors | May 28, 2013 |
| Frosch and Hartmann | Procedure writers and editors | July 8, 2013 |
| Cheng, Frosch and Hartmann | Procedure writers and editors | August 7, 2013 |
| Frosch and Hartmann | Procedure writers and editors | September 25, 2013 |
| Frosch and Hartmann | Procedure writers and editors | December 11, 2013 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | April 1, 2014 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | May 27, 2014 |
| Frosch and Hartmann | Procedure writers and editors | July 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | September 29, 2014 |
| Frosch and Hartmann | Procedure writers and editors | December 10, 2014 |
| Frosch and Thompson | Procedure writers and editors | December 19, 2014 |
| Frosch and Hartmann | Procedure writers and editors | February 25, 2015 |
| Frosch and Hartmann | Procedure writers and editors | April 29, 2015 |
| Frosch and Hartmann | Procedure writers and editors | July 13, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 4, 2015 |
| Hartmann and Gaddy | Procedure writers and editors | September 25, 2015 |
| Frosch, Gaddy and Hartmann | Procedure writers and editors | October 27, 2015 |

Manual Change History

| Procedure | Ver/Rev | Reason for Issue | Effective Date |
| --- | --- | --- | --- |
| All Sections | 1.0 / 0 | New procedures for all sections for Nodal implementation | November 28, 2010 |
| 3.1 3.4 3.5 3.7 4.1 5.1 5.1 5.2 6.1 7.2 | 1.0 / 1 1.0 / 1 - / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 1.0 / 1 | Deleted WGR section, in section “Monitor QSE Ancillary Services Obligation”, updated step Infeasible A/S Capacity from RUC & A/S Difference in COP Updated Note Updated step 3 Updated whole procedure Updated step 2 In section “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide”, “Replacement of Ancillary Services in Real Time”, Updated step 1 Updated whole procedure In section “Timeline Deviations”, Updated 2nd Note In section “Returning from Planned Outage Early”, Updated Deny In section “Implement EEA Level 1”, Updated step 1 | December 1, 2010 |
| 3.1 3.7 3.8 5.1 | 1.0 / 2 1.0 / 2 1.0 / 0 1.0 / 2 | Deleted “Monitor Base Point Deviations” and updated “A/S Difference in COP” Deleted step Note, Deployment, & Termination New Procedure Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services” and “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and 4 | December 15, 2010 |
| 3.1 3.2 3.4 3.3 3.5 3.7 4.1 5.1 5.2 7.1 7.2 7.3 8.2 | 1.0 / 3 1.0 / 1 1.0 / 2 1.0 / 1 1.0/ 2 1.0 / 3 1.0 / 2 1.0 / 3 - / 2 - / 1 - / 2 1.0 / 1 1.0 / 1 | Updated step Telemetered Status, step 1 in Manual Override Checks and removed workaround step “Real Time A/S shortage” in Monitor QSE Ancillary Services Obligation Updated all steps Updated steps “Deployment” and “Termination” Updated step 1 on “Cancelation” Updated all steps and added note Updated all steps Updated and deleted Notes and step 1 Updated “Procurement of Ancillary Services due to DAM Failure”, “ERCOT Increases the Amount of Ancillary Services”, “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide“ step 3 and added note on Replacement of Ancillary Services in Real Time Updated Second Note on “Timeline Deviations” Updated Hotline on “Scripts” Updated Step 1 on ” Implement EEA Level 1” and “Implement EEA Level 2A” Updated Steps 1 on “Move from EEA Level 3 to EEA Level 2B” and “Cancel Watch” Deleted Site Failover Notification procedure & changed 8.3 to 8.2 | January 31, 2011 |
| 3.3 3.4 3.7 5.1 7.1 | 1.0 / 2 1.0 / 3 1.0 / 4 1.0 / 4 1.0 / 2 | Updated step 1 in “Watch” & step 1 in “Cancelation” Updated “Deployment” and “Termination” Updated “Issue Watch & Deploy Non-Spin” and “Recall Non-Spin” Updated step 2 in “Replacement of Ancillary Service Due to Infeasibility/Failure to Provide” Updated “Watch” and “Emergency Notice” | March 25, 2011 |
| 3.5 7.1 7.3 | 1.0 / 3 1.0 / 3 1.0 / 2 | Updated NERC Recovery Criteria Updated step 1 in Watch and Emergency Notice and step Post Updated 1st and 2nd script in Restore Firm Load, Updated 1st in Move From EEA Level 3 to EEA Level 2B | April 22, 2011 |
| 3.8 3.9 5.1 8.1 | 1.0 / 0 1.0 / 1 1.0 / 5 1.0 / 1 | Added new procedure Changed section number from 3.8 to 3.9 Updated steps 3-5 in Replacement of A/S due to Infeasibility/Failure to Provide, deleted Replacement of A/S in Real-Time Change section name, updated step 2 & 3 | May 11, 2011 |
| 3.3 3.4 3.6 3.7 3.8 7.1 | 1.0 / 3 1.0 / 4 1.0 / 1 1.0 / 5 1.0 / 1 1.0 / 4 | Updated step 1 in Advisory and Watch Updated step Deployment Updated step 1 Updated step Deploy Non-Spin & Post & Deploy Load Resources & Post Updated step Post Updated all steps | June 8, 2011 |
| 3.3 3.4 3.5 3.8 4.1 5.2 7.1 7.2 7.3 9.1 | 1.0 / 4 1.0 / 5 1.0 / 4 - / 2 1.0 / 3 1.0 / 3 1.0 / 5 1.0 / 3 1.0 / 3 1.0 / 1 | Updated step 1 in Advisory and Watch Updated step on Deployment Updated step on PRC Below 2300 Added step Termination, updated steps on Post and Cancel Posting Updated step 2 in Approve/Reject Decommitment QSE Requests in Operating Period Updated step 1 and deleted 2nd note in Timeline Deviations Updated step Watch Updated all steps Updated all steps Added Market Participant Backup Control Center Transfer procedure | July 20, 2011 |
| 3.3 3.4 5.1 7.1 7.2 7.3 8.2 | 1.0 / 5 1.0 / 6 1.0 / 6 1.0 / 6 - / 4 1.0 / 4 1.0 / 2 | Updated step 1 in Cancelation Updated Note, added steps Additional Deployment & Commit, updated steps Note & Deployment Updated 1st Note Added projected reserve capacity shortage and Extreme Hot Weather in Watch Updated 2nd Note, step 1 & 2 in EEA Level 1, step 1 in EEA Level 2A, added note in EEA Level 2B Updated step 1 in Cancel Watch Updated 4th Note and step 1 | September 1, 2011 |
| 7.2 7.3 8.1 | 1.0 / 5 1.0 / 5 1.0 / 2 | Combined EEA 2A & B per NPRR 379 Combined EEA 2A & B per NPRR 379 Updated step 2 | October 1, 2011 |
| 3.1 3.4 3.6 3.8 3.9 4.1 5.1 8.1 | 1.0 / 4 1.0 / 7 1.0 / 2 1.0 / 3 1.0 / 2 1.0 / 4 1.0 / 7 1.0 / 3 | Changed desktop guide reference in Monitor QSE Ancillary Services Obligation Updated step Commit Updated procedure title and all steps Updated steps 1 & Termination, added step 2 Deleted procedure due to protocol change Added 2nd Note Updated steps 1 – 3 in Procurement of A/S due to DAM Failure, steps 1 -2 in ERCOT Increased the Amount of A/S, steps 1 & 4 in Replacement of A/S Due to Infeasibility/Failure to Provide Added Note 2 & 3 | November 1, 2011 |
| 3.3 3.4 3.7 3.8 7.1 | 1.0 / 6 1.0 / 8 1.0 / 6 1.0 / 4 1.0 / 7 | Add Note in Watch Added second Note Added second Note Added Note Updated Post in “Scripts” All procedures in this manual have been reviewed. | December 15, 2011 |
| 1.2 3.1 3.4 4.1 5.1 | 1.0 / 1 1.0 / 5 1.0 / 9 1.0 / 5 1.0 / 8 | Updated Scope Updated Monitor QSE A/S Obligation procedure Updated 1st Note Updated steps 1 & 2 Updated step 2, 3 & 4 | January 19, 2012 |
| 2.1 3.1 3.3 3.4 3.5 3.7 3.8 4.1 5.1 7.1 7.2 7.3 8.2 9.1 | 1.0 / 1 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 5 1.0 / 7 1.0 / 5 1.0 / 6 1.0 / 9 1.0 / 8 1.0 / 6 1.0 / 6 1.0 / 3 1.0 / 2 | Updated paragraph 4 Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated 1st Note & step 1 Updated Desktop Guide references, step 3s & 4 Updated step 1 of Watch Updated Desktop Guide references Updated Desktop Guide references Updated Desktop Guide references Updated QSE Override, QSE unable to Override, Backup/Alternate Control Center Transfer, QSE Issues & step Power System Stabilizers (PSS) & Automatic Voltage Regulators (AVR) | March 1, 2012 |
| 2.1 3.1 3.5 3.6 3.7 4.1 5.1 7.1 9.1 | 1.0 / 2 1.0 / 7 1.0 / 6 1.0 / 3 1.0 / 6 1.0 / 7 1.0 / 10 1.0 / 9 1.0 / 3 | Changed TSP/DP to TO Updated step Not Dispatchable to SCED Deleted Potential DCS Event, changed section number for System Failures Changed section number Changed section number & added step 3 Updated step 1 Updated information needed in e-mail Updated all step 1’s Changed Shift Engineer to Ops Support Engineer | May 1, 2012 |
| 3.3 3.4 | 1.0 / 8 1.0 / 11 | Updated to reflect changes in the TAC approved Non-Spin document Updated to reflect changes in the TAC approved Non-Spin document | May 14, 2012 |
| 7.2 7.3 | 1.0 / 7 1.0 / 7 | Updated EILS to ERS per NPRR 451 Updated EILS to ERS per NPRR 451 | June 1, 2012 |
| 1.3 4.1 6.1 7.1 7.2 7.3 8.2 | 1.0 / 1 1.0 / 8 1.0 / 2 1.0 / 10 1.0 / 8 1.0 / 8 1.0 / 4 | Removed ERCOT Shift Supervisor paragraph Added Desktop Guide to VDI reference Added Desktop Guide to VDI reference and updated Maintenance Level 2 and 3 outages Updated all step 1’s Added Desktop Guide to VDI reference, updated step 1 Implement EEA Level 2 and added ERS Updated step 1 Move from EEA Level 3 to EEA Level 2 Updated 4th note | July 16, 2012 |
| 3.1 7.2 | 1.0 / 8 1.0 / 9 | Updated step ONTEST Updated step 1 of Implement EEA Level 1 | August 29, 2012 |
| 2.2 7.2 8.1 | 1.0 / 1 1.0 / 10 1.0 / 4 | Added Hotline Call Communication Updated Implement EEA Level 1 step 2, Implement EEA Level 2 step 1 and ERS Business Hour Changes Updated 1st Note, step 1, 2 & 3. Added step 4 and Log All procedures in this manual have been reviewed. | November 1, 2012 |
| 3.3 3.4 3.6 3.7 4.1 5.1 7.3 | 1.0 / 9 1.0 /12 1.0 / 9 1.0 / 7 1.0 / 8 1.0 / 11 1.0 / 9 | Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Non-Spin deployment messages are now automated Updated steps 1 & 2 Updated steps Note, Procurement Timeline & 1. Added new procedure, Daily Reconfiguration SASM Updated step 1 of Cancel Watch | March 1, 2013 |
| 3.3 3.5 5.1 5.2 7.1 7.2 7.3 8.1 9.1 | 1.0 / 10 1.0 / 4 1.0 / 12 1.0 / 4 1.0 / 11 1.0 / 11 1.0 / 10 1.0 / 5 1.0 / 4 | Removed notice builder reference Removed notice builder reference Updated steps 1 & 5 in ERCOT Increased the amount of A/S & steps in Daily Reconfiguration SASM Updated step 1 Updated Scripts Removed notice builder reference & Updated Scripts Removed notice builder reference Updated Script Updated Script | June 1, 2013 |
| 3.1 7.1 | 1.0 / 9 1.0 / 12 | Deleted 1st Note, added step Log, moved Not Dispatchable to SCED, Control Block Up/Down, & Real-Time RRS A/S Shortages to Real-Time procedure, deleted Manual Override Checks Updated step 1 in Watch & Emergency Notice | July 15, 2013 |
| 5.1 5.2 | 1.0 / 13 1.0 / 5 | Updated 1st Note for R4 changes, Daily SASM Timeline Updated 1st Note for R4 changes | August 9, 2013 |
| 5.1 6.1 | 1.0 / 14 1.0 / 3 | Updated 1st Note, Daily SASM Timeline Updated to reflect SCR770 changes | September 27, 2013 |
| 3.1 3.2 3.3 3.5 3.6 3.7 4.1 5.1 6.1 6.2 7.1 7.2 7.4 8.2 9.1 | 1.0 / 10 1.0 / 2 1.0 / 11 1.0 / 5 1.0 / 10 1.0 / 8 1.0 / 10 1.0 / 15 1.0 / 4 1.0 / 1 1.0 / 13 1.0 / 12 1.0 / 1 1.0 / 5 1.0 / 5 | Added Monitor QSE A/S Obligation Title Updated Evaluate Request Updated step Log Updated step Log Updated step Log Updated step Log Updated step 3 Updated step Log Updated Accept Maintenance Outage, Coordinate Maintenance Outage, Coordinate Maintenance Level 2 and 3 and Log Updated step Log Updated step Log Updated last step and added Log Updated step Log Updated step Log Updated and added step Log All procedures in this manual have been reviewed. | December 13, 2013 |
| 3.4 3.5 3.74.1 6.1 7.1 7.2 7.3 8.1 | 1.0 / 13 1.0 / 7 1.0 / 9 1.0 / 11 1.0 / 5 1.0 / 14 1.0 / 13 1.0 / 11 1.0 / 6 | Updated VDI information Updated for NPRR542 Updated VDI information Updated VDI information Updated VDI information Updated to incorporate NPRR542 Updated ERS, Media appeal, TCEQ, VDI language, and moved steps to RUC desk Updated Reserves and step 1 Updated step 1 & 3, added step 5 | April 4, 2014 |
| 2.2 3.1 3.3 3.4 4.1 5.1 5.2 7.1 | 1.0 / 2 1.0 / 11 1.0 / 12 1.0 / 14 1.0 / 12 1.0 / 16 1.0 / 6 1.0 / 15 | Added VDIs to Master QSEs Updated Monitor QSE AS Obligations steps Updated steps in Watch Updated title, step Deployment & Termination Updated step 1 & 2 Updated section titles & steps Updated Timeline Deviations Added Note, updated Advisory & Watch | June 1, 2014 |
| 3.1 3.4 3.6 3.7 4.1 5.1 6.1 7.2 7.3 | 1.0 / 12 1.0 / 15 1.0 / 11 1.0 / 10 1.0 / 13 1.0 / 17 1.0 / 6 1.0 / 14 1.0 / 12 | Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop references Updated Desktop reference Updated steps 1, 4-6 in Replacement of A/S due to infeasibility or failure to provide, & Desktop references Updated Forced Derate Updated Desktop references Updated Desktop references | August 1, 2014 |
| 7.1 | 1.0 / 16 | Updated Scripts | October 1, 2014 |
| 3.4 3.6 4.1 6.2 | 1.0 / 16 1.0 / 12 1.0 / 14 1.0 / 2 | Deleted Note & added Log Changed title & added Rio Grande Valley Re-worded procedure Added step 2 All procedures in this manual have been reviewed | December 15, 2014 |
| 5.1 | 1.0 / 18 | Added new procedure “Increasing A/S for Extreme Cold Weather and changed title for “Increasing A/S for other reasons and updated timeline | December 22, 2014 |
| 2.2 3.3 3.4 3.5 3.6 3.7 5.1 5.2 6.1 | 1.0 / 3 1.0 / 13 1.0 / 8 1.0 / 13 1.0 / 11 1.0 / 0 1.0 / 19 1.0 / 7 1.0 / 7 | Added Dispatch and VDI definitions Combined section 3.3 & 3.4 into one procedure Updated section number Updated section number Updated section number and Corrected VDI vs. Dispatch Instruction New, moved procedure from Shift Supervisor desk Added SASM Failure and reformatted Deleted procedure Corrected VDI vs. Dispatch Instruction | March 1, 2015 |
| 3.2 3.3 3.5 3.6 5.1 7.1 8.1 9.1 | 1.0 / 3 1.0 / 14 1.0 / 14 1.0 / 12 1.0 / 20 1.0 / 17 1.0 / 7 1.0 / 6 | Updated step Evaluate Request Combined step in Watch Updated GTL to GTC Updated step 2 Moved scripts to script procedure Moved scripts to script procedure Combined Note steps & moved scripts to script procedure Moved script to script procedure | May 1, 2015 |
| 5.1 | 1.0 / 21 | Added a “Q” for QSE scripts Updated per NPRR 682 | July 15, 2015 |
| 5.1 | 1.0 / 22 | Updated per NPRR 701 | September 9, 2015 |
| 5.1 | 1.0 / 23 | Updated Reconfiguration Supplemental Ancillary Service Market (RSASM) | October 1, 2015 |
| 3.5 | 1.0 / 15 | Updated to include calls for deployment and recalls of Load Resources. | October 30, 2015 |